## Prva stran
variable | 2306 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_ST2 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 14 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 118 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
ST2 | INT | 26 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 1490 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 7 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 18 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
| ULONG | 0 | ULONG | ULONG | 8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 118 | DIGITAL | 118 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 40 | INT | 40 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 1490 | REAL | 2980 (word)
| STRING | 7 | STRING | 105 (word)
| UINT | 18 | UINT | 18 (word)
| ULONG | 0 | ULONG | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 7001 |  | STRING
| UINT | 8001 |  | UINT
| ULONG | 9001 |  | ULONG
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_ST2_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
ST2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada1 | [5 empty] | 6157 | 0
ST2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada2 | [5 empty] | 6157 | 0
ST2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada1 | [5 empty] | 6157 | 0
ST2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada2 | [5 empty] | 6157 | 0
ST2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada1 | [5 empty] | 6157 | 0
ST2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada2 | [5 empty] | 6157 | 0
ST2ComError | DIGITAL | IOD_ST2 | ST2:.ComError | [5 empty] | 6157 | 0
ST2ComSCADA | DIGITAL | IOD_ST2 | ST2:.ComSCADA | [5 empty] | 6157 | 0
ST2ComSCADA1 | DIGITAL | IOD_ST2 | ST2:.ComSCADA1 | [5 empty] | 6157 | 0
ST2ComSCADA2 | DIGITAL | IOD_ST2 | ST2:.ComSCADA2 | [5 empty] | 6157 | 0
ST2ComSCADA3 | DIGITAL | IOD_ST2 | ST2:.ComSCADA3 | [5 empty] | 6157 | 0
ST2Date_Time0 | STRING | IOD_ST2 | ST2:.Date_Time[0] | [5 empty] | 6157 | 0
ST2Date_Time1 | STRING | IOD_ST2 | ST2:.Date_Time[1] | [5 empty] | 6157 | 0
ST2Date_Time2 | STRING | IOD_ST2 | ST2:.Date_Time[2] | [5 empty] | 6157 | 0
ST2Date_Time3 | STRING | IOD_ST2 | ST2:.Date_Time[3] | [5 empty] | 6157 | 0
ST2DateTimeDan | BYTE | IOD_ST2 | ST2:.DateTime.Dan | [5 empty] | 6157 | 0
ST2DateTimeLeto | BYTE | IOD_ST2 | ST2:.DateTime.Leto | [5 empty] | 6157 | 0
ST2DateTimeLeto2 | INT | IOD_ST2 | ST2:.DateTime.Leto2 | [5 empty] | 6157 | 0
ST2DateTimeMesec | BYTE | IOD_ST2 | ST2:.DateTime.Mesec | [5 empty] | 6157 | 0
ST2DateTimeMinuta | BYTE | IOD_ST2 | ST2:.DateTime.Minuta | [5 empty] | 6157 | 0
ST2DateTimePLC_Dan | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Dan | [5 empty] | 6157 | 0
ST2DateTimePLC_DanVTednu | BYTE | IOD_ST2 | ST2:.DateTime.PLC_DanVTednu | [5 empty] | 6157 | 0
ST2DateTimePLC_Leto | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Leto | [5 empty] | 6157 | 0
ST2DateTimePLC_Mesec | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Mesec | [5 empty] | 6157 | 0
ST2DateTimePLC_Minuta | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Minuta | [5 empty] | 6157 | 0
ST2DateTimePLC_Sekunda | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Sekunda | [5 empty] | 6157 | 0
ST2DateTimePLC_Ura | BYTE | IOD_ST2 | ST2:.DateTime.PLC_Ura | [5 empty] | 6157 | 0
ST2DateTimeSekunda | BYTE | IOD_ST2 | ST2:.DateTime.Sekunda | [5 empty] | 6157 | 0
ST2DateTimeUra | BYTE | IOD_ST2 | ST2:.DateTime.Ura | [5 empty] | 6157 | 0
ST2DI2_I10_Rezerva3 | DIGITAL | IOD_ST2 | ST2:.DI2_I10_Rezerva3 | [5 empty] | 6157 | 0
ST2DI2_I11_Rezerva4 | DIGITAL | IOD_ST2 | ST2:.DI2_I11_Rezerva4 | [5 empty] | 6157 | 0
ST2DI2_I12_Rezerva5 | DIGITAL | IOD_ST2 | ST2:.DI2_I12_Rezerva5 | [5 empty] | 6157 | 0
ST2DI2_I13_Rezerva6 | DIGITAL | IOD_ST2 | ST2:.DI2_I13_Rezerva6 | [5 empty] | 6157 | 0
ST2DI2_I8_Rezerva1 | DIGITAL | IOD_ST2 | ST2:.DI2_I8_Rezerva1 | [5 empty] | 6157 | 0
ST2DI2_I9_Rezerva2 | DIGITAL | IOD_ST2 | ST2:.DI2_I9_Rezerva2 | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM21_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_SkupnaNapaka | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Izkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Izpad | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Vkljucen | [5 empty] | 6157 | 0
ST2DI_SB_IROGSM22_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_SkupnaNapaka | [5 empty] | 6157 | 0
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AA_Izolacija_NOT_OK | [5 empty] | 6157 | 0
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AB_Izolacija_NOT_OK | [5 empty] | 6157 | 0
ST2ErrComNSX1 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[1] | [5 empty] | 6157 | 0
ST2ErrComNSX2 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[2] | [5 empty] | 6157 | 0
ST2ErrComNSX3 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[3] | [5 empty] | 6157 | 0
ST2ErrComNSX4 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[4] | [5 empty] | 6157 | 0
ST2ErrComNSX5 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[5] | [5 empty] | 6157 | 0
ST2ErrComNSX6 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[6] | [5 empty] | 6157 | 0
ST2ErrComPMM1 | DIGITAL | IOD_ST2 | ST2:.ErrComPMM[1] | [5 empty] | 6157 | 0
ST2ErrComPort2 | DIGITAL | IOD_ST2 | ST2:.ErrComPort2 | [5 empty] | 6157 | 0
ST2ErrorComPMM1Error | DIGITAL | IOD_ST2 | ST2:.ErrorComPMM[1].Error | [5 empty] | 6157 | 0
ST2ErrorComPMM1Status | INT | IOD_ST2 | ST2:.ErrorComPMM[1].Status | [5 empty] | 6157 | 0
ST2HIA1_vlaga_s | INT | IOD_ST2 | ST2:.HIA1_vlaga_s | [5 empty] | 6157 | 0
ST2HIA2_vlaga_s | INT | IOD_ST2 | ST2:.HIA2_vlaga_s | [5 empty] | 6157 | 0
ST2HIA3_vlaga_s | INT | IOD_ST2 | ST2:.HIA3_vlaga_s | [5 empty] | 6157 | 0
ST2HIA4_vlaga_s | INT | IOD_ST2 | ST2:.HIA4_vlaga_s | [5 empty] | 6157 | 0
ST2HIA5_vlaga_s | INT | IOD_ST2 | ST2:.HIA5_vlaga_s | [5 empty] | 6157 | 0
ST2HIA6_vlaga_s | INT | IOD_ST2 | ST2:.HIA6_vlaga_s | [5 empty] | 6157 | 0
ST2HIA7_vlaga_s | INT | IOD_ST2 | ST2:.HIA7_vlaga_s | [5 empty] | 6157 | 0
ST2HIA8_vlaga_s | INT | IOD_ST2 | ST2:.HIA8_vlaga_s | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok1 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok10 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok11 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok12 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok13 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok14 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok15 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok16 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok17 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok18 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok19 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok2 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok20 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok21 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok22 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok23 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok24 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok25 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok26 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok27 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok28 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok29 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok3 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok30 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok31 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok32 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok33 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok34 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok35 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok36 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok37 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok38 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok39 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok4 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok40 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok41 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok42 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok43 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok44 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok5 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok6 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok7 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok8 | [5 empty] | 6157 | 0
ST2iPMM_VirA_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok9 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok1 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok10 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok11 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok12 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok13 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok14 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok15 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok16 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok17 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok18 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok19 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok2 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok20 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok21 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok22 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok23 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok24 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok25 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok26 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok27 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok28 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok29 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok3 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok30 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok31 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok32 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok33 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok34 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok35 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok36 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok37 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok38 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok39 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok4 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok40 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok41 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok42 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok43 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok44 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok5 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok6 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok7 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok8 | [5 empty] | 6157 | 0
ST2iPMM_VirB_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok9 | [5 empty] | 6157 | 0
ST2kom_nast_cas_izpada | STRING | IOD_ST2 | ST2:.kom_nast_cas_izpada | [5 empty] | 6157 | 0
ST2napaka_kom_panel | DIGITAL | IOD_ST2 | ST2:.napaka_kom_panel | [5 empty] | 6157 | 0
ST2napaka_kom_scada | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada | [5 empty] | 6157 | 0
ST2napaka_kom_scada2 | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada2 | [5 empty] | 6157 | 0
ST2NapakaSenzorSkupno | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorSkupno | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA1 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA2 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA3 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA4 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA5 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA6 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA7 | [5 empty] | 6157 | 0
ST2NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA8 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA1 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA2 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA3 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA4 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA5 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA6 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA7 | [5 empty] | 6157 | 0
ST2NapakaTSTempTIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA8 | [5 empty] | 6157 | 0
ST2NSX1ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX1ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX1ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX1ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX1ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX1ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX1ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX1ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX1ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX1ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[1].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX1ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX1ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX1ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX1ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX1ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX1ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX1CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL1 | [5 empty] | 6157 | 0
ST2NSX1CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL2 | [5 empty] | 6157 | 0
ST2NSX1CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL3 | [5 empty] | 6157 | 0
ST2NSX1CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].CosFTotal | [5 empty] | 6157 | 0
ST2NSX1CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX1CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX1CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX1CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX1CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX1CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX1CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX1CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX1CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX1CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX1CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX1CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX1DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX1DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX1FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX1MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX1MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX1MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX1MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX1MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX1MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX1MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX1MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX1MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX1MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX1MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX1MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX1MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX1MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX1MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX1MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX1MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX1MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX1MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX1MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX1MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX1MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX1MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX1MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX1MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX1MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX1MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX1MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX1MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX1MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX1MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX1MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX1MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX1MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX1MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX1MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX1MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX1MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX1MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX1MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX1MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX1PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX1PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX1PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX1PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX1RazEner_D | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D | [5 empty] | 6157 | 0
ST2NSX1RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX1RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX1RazEner_M | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M | [5 empty] | 6157 | 0
ST2NSX1RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX1RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX1RazEner_T | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T | [5 empty] | 6157 | 0
ST2NSX1RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX1RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX1ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX1ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX1ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX1ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX1ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMAX | [5 empty] | 6157 | 0
ST2NSX1ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMIN | [5 empty] | 6157 | 0
ST2NSX1StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[1].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX1THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI1_P | [5 empty] | 6157 | 0
ST2NSX1THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI2_P | [5 empty] | 6157 | 0
ST2NSX1THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI3_P | [5 empty] | 6157 | 0
ST2NSX1THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV12_P | [5 empty] | 6157 | 0
ST2NSX1THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX1THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV23_P | [5 empty] | 6157 | 0
ST2NSX1THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX1THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV31_P | [5 empty] | 6157 | 0
ST2NSX1THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX1VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX1VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX1VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX1VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX1VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX1VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX1VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX1VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX1VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX2ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX2ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX2ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX2ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX2ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX2ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX2ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX2ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX2ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX2ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[2].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX2ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX2ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX2ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX2ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX2ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX2ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX2CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL1 | [5 empty] | 6157 | 0
ST2NSX2CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL2 | [5 empty] | 6157 | 0
ST2NSX2CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL3 | [5 empty] | 6157 | 0
ST2NSX2CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].CosFTotal | [5 empty] | 6157 | 0
ST2NSX2CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX2CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX2CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX2CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX2CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX2CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX2CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX2CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX2CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX2CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX2CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX2CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX2DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX2DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX2FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX2MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX2MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX2MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX2MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX2MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX2MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX2MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX2MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX2MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX2MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX2MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX2MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX2MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX2MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX2MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX2MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX2MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX2MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX2MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX2MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX2MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX2MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX2MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX2MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX2MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX2MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX2MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX2MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX2MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX2MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX2MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX2MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX2MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX2MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX2MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX2MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX2MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX2MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX2MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX2MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX2MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX2PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX2PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX2PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX2PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX2RazEner_D | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D | [5 empty] | 6157 | 0
ST2NSX2RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX2RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX2RazEner_M | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M | [5 empty] | 6157 | 0
ST2NSX2RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX2RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX2RazEner_T | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T | [5 empty] | 6157 | 0
ST2NSX2RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX2RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX2ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX2ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX2ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX2ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX2ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMAX | [5 empty] | 6157 | 0
ST2NSX2ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMIN | [5 empty] | 6157 | 0
ST2NSX2StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[2].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX2THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI1_P | [5 empty] | 6157 | 0
ST2NSX2THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI2_P | [5 empty] | 6157 | 0
ST2NSX2THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI3_P | [5 empty] | 6157 | 0
ST2NSX2THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV12_P | [5 empty] | 6157 | 0
ST2NSX2THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX2THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV23_P | [5 empty] | 6157 | 0
ST2NSX2THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX2THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV31_P | [5 empty] | 6157 | 0
ST2NSX2THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX2VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX2VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX2VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX2VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX2VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX2VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX2VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX2VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX2VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX3ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX3ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX3ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX3ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX3ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX3ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX3ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX3ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX3ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX3ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[3].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX3ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX3ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX3ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX3ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX3ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX3ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX3CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL1 | [5 empty] | 6157 | 0
ST2NSX3CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL2 | [5 empty] | 6157 | 0
ST2NSX3CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL3 | [5 empty] | 6157 | 0
ST2NSX3CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].CosFTotal | [5 empty] | 6157 | 0
ST2NSX3CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX3CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX3CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX3CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX3CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX3CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX3CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX3CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX3CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX3CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX3CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX3CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX3DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX3DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX3FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX3MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX3MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX3MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX3MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX3MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX3MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX3MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX3MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX3MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX3MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX3MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX3MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX3MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX3MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX3MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX3MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX3MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX3MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX3MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX3MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX3MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX3MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX3MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX3MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX3MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX3MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX3MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX3MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX3MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX3MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX3MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX3MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX3MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX3MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX3MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX3MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX3MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX3MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX3MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX3MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX3MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX3PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX3PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX3PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX3PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX3RazEner_D | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D | [5 empty] | 6157 | 0
ST2NSX3RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX3RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX3RazEner_M | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M | [5 empty] | 6157 | 0
ST2NSX3RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX3RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX3RazEner_T | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T | [5 empty] | 6157 | 0
ST2NSX3RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX3RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX3ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX3ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX3ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX3ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX3ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMAX | [5 empty] | 6157 | 0
ST2NSX3ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMIN | [5 empty] | 6157 | 0
ST2NSX3StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[3].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX3THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI1_P | [5 empty] | 6157 | 0
ST2NSX3THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI2_P | [5 empty] | 6157 | 0
ST2NSX3THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI3_P | [5 empty] | 6157 | 0
ST2NSX3THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV12_P | [5 empty] | 6157 | 0
ST2NSX3THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX3THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV23_P | [5 empty] | 6157 | 0
ST2NSX3THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX3THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV31_P | [5 empty] | 6157 | 0
ST2NSX3THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX3VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX3VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX3VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX3VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX3VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX3VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX3VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX3VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX3VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX4ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX4ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX4ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX4ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX4ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX4ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX4ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX4ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX4ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX4ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[4].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX4ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX4ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX4ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX4ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX4ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX4ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX4CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL1 | [5 empty] | 6157 | 0
ST2NSX4CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL2 | [5 empty] | 6157 | 0
ST2NSX4CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL3 | [5 empty] | 6157 | 0
ST2NSX4CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].CosFTotal | [5 empty] | 6157 | 0
ST2NSX4CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX4CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX4CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX4CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX4CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX4CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX4CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX4CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX4CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX4CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX4CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX4CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX4DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX4DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX4FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX4MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX4MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX4MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX4MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX4MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX4MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX4MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX4MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX4MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX4MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX4MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX4MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX4MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX4MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX4MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX4MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX4MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX4MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX4MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX4MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX4MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX4MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX4MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX4MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX4MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX4MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX4MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX4MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX4MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX4MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX4MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX4MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX4MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX4MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX4MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX4MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX4MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX4MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX4MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX4MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX4MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX4PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX4PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX4PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX4PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX4RazEner_D | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D | [5 empty] | 6157 | 0
ST2NSX4RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX4RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX4RazEner_M | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M | [5 empty] | 6157 | 0
ST2NSX4RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX4RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX4RazEner_T | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T | [5 empty] | 6157 | 0
ST2NSX4RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX4RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX4ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX4ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX4ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX4ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX4ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMAX | [5 empty] | 6157 | 0
ST2NSX4ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMIN | [5 empty] | 6157 | 0
ST2NSX4StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[4].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX4THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI1_P | [5 empty] | 6157 | 0
ST2NSX4THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI2_P | [5 empty] | 6157 | 0
ST2NSX4THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI3_P | [5 empty] | 6157 | 0
ST2NSX4THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV12_P | [5 empty] | 6157 | 0
ST2NSX4THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX4THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV23_P | [5 empty] | 6157 | 0
ST2NSX4THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX4THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV31_P | [5 empty] | 6157 | 0
ST2NSX4THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX4VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX4VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX4VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX4VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX4VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX4VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX4VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX4VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX4VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX5ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX5ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX5ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX5ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX5ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX5ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX5ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX5ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX5ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX5ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[5].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX5ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX5ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX5ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX5ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX5ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX5ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX5CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL1 | [5 empty] | 6157 | 0
ST2NSX5CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL2 | [5 empty] | 6157 | 0
ST2NSX5CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL3 | [5 empty] | 6157 | 0
ST2NSX5CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].CosFTotal | [5 empty] | 6157 | 0
ST2NSX5CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX5CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX5CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX5CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX5CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX5CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX5CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX5CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX5CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX5CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX5CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX5CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX5DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX5DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX5FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX5MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX5MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX5MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX5MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX5MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX5MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX5MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX5MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX5MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX5MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX5MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX5MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX5MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX5MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX5MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX5MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX5MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX5MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX5MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX5MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX5MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX5MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX5MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX5MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX5MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX5MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX5MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX5MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX5MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX5MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX5MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX5MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX5MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX5MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX5MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX5MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX5MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX5MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX5MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX5MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX5MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX5PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX5PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX5PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX5PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX5RazEner_D | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D | [5 empty] | 6157 | 0
ST2NSX5RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX5RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX5RazEner_M | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M | [5 empty] | 6157 | 0
ST2NSX5RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX5RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX5RazEner_T | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T | [5 empty] | 6157 | 0
ST2NSX5RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX5RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX5ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX5ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX5ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX5ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX5ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMAX | [5 empty] | 6157 | 0
ST2NSX5ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMIN | [5 empty] | 6157 | 0
ST2NSX5StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[5].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX5THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI1_P | [5 empty] | 6157 | 0
ST2NSX5THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI2_P | [5 empty] | 6157 | 0
ST2NSX5THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI3_P | [5 empty] | 6157 | 0
ST2NSX5THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV12_P | [5 empty] | 6157 | 0
ST2NSX5THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX5THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV23_P | [5 empty] | 6157 | 0
ST2NSX5THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX5THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV31_P | [5 empty] | 6157 | 0
ST2NSX5THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX5VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX5VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX5VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX5VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX5VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX5VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX5VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX5VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX5VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX6ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX6ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveNegativeEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX6ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActivePositiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX6ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerDemand_kW | [5 empty] | 6157 | 0
ST2NSX6ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX6ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX6ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX6ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerMaxDemand_kW | [5 empty] | 6157 | 0
ST2NSX6ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX6ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[6].ApparentEnergy_kVAh | [5 empty] | 6157 | 0
ST2NSX6ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerDemand_kVA | [5 empty] | 6157 | 0
ST2NSX6ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerMaxDemand_kVA | [5 empty] | 6157 | 0
ST2NSX6ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX6ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX6ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX6ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX6CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL1 | [5 empty] | 6157 | 0
ST2NSX6CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL2 | [5 empty] | 6157 | 0
ST2NSX6CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL3 | [5 empty] | 6157 | 0
ST2NSX6CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].CosFTotal | [5 empty] | 6157 | 0
ST2NSX6CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulNegativeActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX6CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulPositiveActiveEnergy_kWh | [5 empty] | 6157 | 0
ST2NSX6CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL1_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL2_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL3_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL1_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL2_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL3_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxN_A | [5 empty] | 6157 | 0
ST2NSX6CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandN_A | [5 empty] | 6157 | 0
ST2NSX6CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX6CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX6CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX6CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentN_A | [5 empty] | 6157 | 0
ST2NSX6CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI1_P | [5 empty] | 6157 | 0
ST2NSX6CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI2_P | [5 empty] | 6157 | 0
ST2NSX6CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI3_P | [5 empty] | 6157 | 0
ST2NSX6CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbN_P | [5 empty] | 6157 | 0
ST2NSX6DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].DelovnaEnergija_TEMP | [5 empty] | 6157 | 0
ST2NSX6DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX6FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX6MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX6MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX6MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX6MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX6MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX6MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX6MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX6MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL1 | [5 empty] | 6157 | 0
ST2NSX6MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL2 | [5 empty] | 6157 | 0
ST2NSX6MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL3 | [5 empty] | 6157 | 0
ST2NSX6MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFTotal | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX6MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX6MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MAX_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX6MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX6MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX6MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX6MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX6MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI1_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI2_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI3_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV12_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV23_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV31_P | [5 empty] | 6157 | 0
ST2NSX6MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX6MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX6MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL1_kW | [5 empty] | 6157 | 0
ST2NSX6MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL2_kW | [5 empty] | 6157 | 0
ST2NSX6MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL3_kW | [5 empty] | 6157 | 0
ST2NSX6MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerTotal_kW | [5 empty] | 6157 | 0
ST2NSX6MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL1_kVA | [5 empty] | 6157 | 0
ST2NSX6MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL2_kVA | [5 empty] | 6157 | 0
ST2NSX6MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL3_kVA | [5 empty] | 6157 | 0
ST2NSX6MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerTotal_kVA | [5 empty] | 6157 | 0
ST2NSX6MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL1 | [5 empty] | 6157 | 0
ST2NSX6MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL2 | [5 empty] | 6157 | 0
ST2NSX6MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL3 | [5 empty] | 6157 | 0
ST2NSX6MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFTotal | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentAvgI1I2I3_A | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL1_A | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL2_A | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL3_A | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentMaxL1L2L3N_A | [5 empty] | 6157 | 0
ST2NSX6MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentN_A | [5 empty] | 6157 | 0
ST2NSX6MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MIN_Frequency_Hz | [5 empty] | 6157 | 0
ST2NSX6MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX6MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX6MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX6MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX6MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI1_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI2_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI3_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV12_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV1N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV23_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV2N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV31_P | [5 empty] | 6157 | 0
ST2NSX6MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV3N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX6MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV3N_V | [5 empty] | 6157 | 0
ST2NSX6PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL1 | [5 empty] | 6157 | 0
ST2NSX6PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL2 | [5 empty] | 6157 | 0
ST2NSX6PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL3 | [5 empty] | 6157 | 0
ST2NSX6PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorTotal | [5 empty] | 6157 | 0
ST2NSX6RazEner_D | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D | [5 empty] | 6157 | 0
ST2NSX6RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_SCADA | [5 empty] | 6157 | 0
ST2NSX6RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_TEMP | [5 empty] | 6157 | 0
ST2NSX6RazEner_M | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M | [5 empty] | 6157 | 0
ST2NSX6RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_SCADA | [5 empty] | 6157 | 0
ST2NSX6RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_TEMP | [5 empty] | 6157 | 0
ST2NSX6RazEner_T | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T | [5 empty] | 6157 | 0
ST2NSX6RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_SCADA | [5 empty] | 6157 | 0
ST2NSX6RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_TEMP | [5 empty] | 6157 | 0
ST2NSX6ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX6ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveNegativeEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX6ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePositiveEnergy_kVArh | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL1_kVAr | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL2_kVAr | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL3_kVAr | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerMaxDemand_kVAr | [5 empty] | 6157 | 0
ST2NSX6ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerTotal_kVAr | [5 empty] | 6157 | 0
ST2NSX6ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMAX | [5 empty] | 6157 | 0
ST2NSX6ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMIN | [5 empty] | 6157 | 0
ST2NSX6StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[6].StatusSwitch | [5 empty] | 6157 | 0
ST2NSX6THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI1_P | [5 empty] | 6157 | 0
ST2NSX6THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI2_P | [5 empty] | 6157 | 0
ST2NSX6THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI3_P | [5 empty] | 6157 | 0
ST2NSX6THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV12_P | [5 empty] | 6157 | 0
ST2NSX6THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV1N_P | [5 empty] | 6157 | 0
ST2NSX6THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV23_P | [5 empty] | 6157 | 0
ST2NSX6THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV2N_P | [5 empty] | 6157 | 0
ST2NSX6THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV31_P | [5 empty] | 6157 | 0
ST2NSX6THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV3N_P | [5 empty] | 6157 | 0
ST2NSX6VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToN_V | [5 empty] | 6157 | 0
ST2NSX6VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToPh_V | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV12_P | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV1N_P | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV23_P | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV2N_P | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV31_P | [5 empty] | 6157 | 0
ST2NSX6VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV3N_P | [5 empty] | 6157 | 0
ST2NSX6VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV12_V | [5 empty] | 6157 | 0
ST2NSX6VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV1N_V | [5 empty] | 6157 | 0
ST2NSX6VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV23_V | [5 empty] | 6157 | 0
ST2NSX6VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV2N_V | [5 empty] | 6157 | 0
ST2NSX6VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV31_V | [5 empty] | 6157 | 0
ST2NSX6VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV3N_V | [5 empty] | 6157 | 0
ST2PLC_SB_IROGSM21_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM21_F2_2_NOT_OK | [5 empty] | 6157 | 0
ST2PLC_SB_IROGSM22_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM22_F2_2_NOT_OK | [5 empty] | 6157 | 0
ST2PMMQA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QA1_GlStik_IZKLOP_IZPAD | [5 empty] | 6157 | 0
ST2PMMQB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QB1_GlStik_IZKLOP_IZPAD | [5 empty] | 6157 | 0
ST2PMMSkNapaka_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_med60in80 | [5 empty] | 6157 | 0
ST2PMMSkNapaka_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_nad80 | [5 empty] | 6157 | 0
ST2PMMSkNapakaVirA_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_med60in80 | [5 empty] | 6157 | 0
ST2PMMSkNapakaVirA_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_nad80 | [5 empty] | 6157 | 0
ST2PMMSkNapakaVirB_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_med60in80 | [5 empty] | 6157 | 0
ST2PMMSkNapakaVirB_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_nad80 | [5 empty] | 6157 | 0
ST2PMMVirACurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[10] | [5 empty] | 6157 | 0
ST2PMMVirACurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[11] | [5 empty] | 6157 | 0
ST2PMMVirACurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[12] | [5 empty] | 6157 | 0
ST2PMMVirACurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[13] | [5 empty] | 6157 | 0
ST2PMMVirACurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[14] | [5 empty] | 6157 | 0
ST2PMMVirACurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[15] | [5 empty] | 6157 | 0
ST2PMMVirACurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[16] | [5 empty] | 6157 | 0
ST2PMMVirACurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[17] | [5 empty] | 6157 | 0
ST2PMMVirACurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[18] | [5 empty] | 6157 | 0
ST2PMMVirACurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[19] | [5 empty] | 6157 | 0
ST2PMMVirACurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[1] | [5 empty] | 6157 | 0
ST2PMMVirACurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[20] | [5 empty] | 6157 | 0
ST2PMMVirACurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[21] | [5 empty] | 6157 | 0
ST2PMMVirACurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[22] | [5 empty] | 6157 | 0
ST2PMMVirACurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[23] | [5 empty] | 6157 | 0
ST2PMMVirACurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[24] | [5 empty] | 6157 | 0
ST2PMMVirACurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[25] | [5 empty] | 6157 | 0
ST2PMMVirACurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[26] | [5 empty] | 6157 | 0
ST2PMMVirACurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[27] | [5 empty] | 6157 | 0
ST2PMMVirACurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[28] | [5 empty] | 6157 | 0
ST2PMMVirACurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[29] | [5 empty] | 6157 | 0
ST2PMMVirACurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[2] | [5 empty] | 6157 | 0
ST2PMMVirACurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[30] | [5 empty] | 6157 | 0
ST2PMMVirACurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[31] | [5 empty] | 6157 | 0
ST2PMMVirACurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[32] | [5 empty] | 6157 | 0
ST2PMMVirACurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[33] | [5 empty] | 6157 | 0
ST2PMMVirACurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[34] | [5 empty] | 6157 | 0
ST2PMMVirACurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[35] | [5 empty] | 6157 | 0
ST2PMMVirACurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[36] | [5 empty] | 6157 | 0
ST2PMMVirACurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[37] | [5 empty] | 6157 | 0
ST2PMMVirACurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[38] | [5 empty] | 6157 | 0
ST2PMMVirACurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[39] | [5 empty] | 6157 | 0
ST2PMMVirACurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[3] | [5 empty] | 6157 | 0
ST2PMMVirACurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[40] | [5 empty] | 6157 | 0
ST2PMMVirACurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[41] | [5 empty] | 6157 | 0
ST2PMMVirACurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[42] | [5 empty] | 6157 | 0
ST2PMMVirACurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[43] | [5 empty] | 6157 | 0
ST2PMMVirACurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[44] | [5 empty] | 6157 | 0
ST2PMMVirACurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[4] | [5 empty] | 6157 | 0
ST2PMMVirACurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[5] | [5 empty] | 6157 | 0
ST2PMMVirACurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[6] | [5 empty] | 6157 | 0
ST2PMMVirACurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[7] | [5 empty] | 6157 | 0
ST2PMMVirACurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[8] | [5 empty] | 6157 | 0
ST2PMMVirACurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[9] | [5 empty] | 6157 | 0
ST2PMMVirA_fsys | REAL | IOD_ST2 | ST2:.PMM.VirA_fsys | [5 empty] | 6157 | 0
ST2PMMVirA_Isys | REAL | IOD_ST2 | ST2:.PMM.VirA_Isys | [5 empty] | 6157 | 0
ST2PMMVirA_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirA_NapakaOzemljitve | [5 empty] | 6157 | 0
ST2PMMVirA_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirA_PFsys | [5 empty] | 6157 | 0
ST2PMMVirA_Psys | REAL | IOD_ST2 | ST2:.PMM.VirA_Psys | [5 empty] | 6157 | 0
ST2PMMVirA_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirA_Qsys | [5 empty] | 6157 | 0
ST2PMMVirA_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirA_Ssys | [5 empty] | 6157 | 0
ST2PMMVirA_Usys | REAL | IOD_ST2 | ST2:.PMM.VirA_Usys | [5 empty] | 6157 | 0
ST2PMMVirAActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirAActiveEnergyConsumed_kWh | [5 empty] | 6157 | 0
ST2PMMVirAActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseA_kW | [5 empty] | 6157 | 0
ST2PMMVirAActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseB_kW | [5 empty] | 6157 | 0
ST2PMMVirAActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseC_kW | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_60to80 | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_over80 | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_60to80 | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_over80 | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_60to80 | [5 empty] | 6157 | 0
ST2PMMVirAAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_over80 | [5 empty] | 6157 | 0
ST2PMMVirAAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseA | [5 empty] | 6157 | 0
ST2PMMVirAAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseB | [5 empty] | 6157 | 0
ST2PMMVirAAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseC | [5 empty] | 6157 | 0
ST2PMMVirACurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseA_A | [5 empty] | 6157 | 0
ST2PMMVirACurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseB_A | [5 empty] | 6157 | 0
ST2PMMVirACurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseC_A | [5 empty] | 6157 | 0
ST2PMMVirAReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirAReactiveEnergyConsumed_kVARh | [5 empty] | 6157 | 0
ST2PMMVirAReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseA | [5 empty] | 6157 | 0
ST2PMMVirAReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseB | [5 empty] | 6157 | 0
ST2PMMVirAReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseC | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAB_V | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAN_V | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBC_V | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBN_V | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCA_V | [5 empty] | 6157 | 0
ST2PMMVirAVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCN_V | [5 empty] | 6157 | 0
ST2PMMVirBCurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[10] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[11] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[12] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[13] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[14] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[15] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[16] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[17] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[18] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[19] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[1] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[20] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[21] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[22] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[23] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[24] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[25] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[26] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[27] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[28] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[29] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[2] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[30] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[31] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[32] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[33] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[34] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[35] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[36] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[37] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[38] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[39] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[3] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[40] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[41] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[42] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[43] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[44] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[4] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[5] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[6] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[7] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[8] | [5 empty] | 6157 | 0
ST2PMMVirBCurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[9] | [5 empty] | 6157 | 0
ST2PMMVirB_fsys | REAL | IOD_ST2 | ST2:.PMM.VirB_fsys | [5 empty] | 6157 | 0
ST2PMMVirB_Isys | REAL | IOD_ST2 | ST2:.PMM.VirB_Isys | [5 empty] | 6157 | 0
ST2PMMVirB_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirB_NapakaOzemljitve | [5 empty] | 6157 | 0
ST2PMMVirB_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirB_PFsys | [5 empty] | 6157 | 0
ST2PMMVirB_Psys | REAL | IOD_ST2 | ST2:.PMM.VirB_Psys | [5 empty] | 6157 | 0
ST2PMMVirB_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirB_Qsys | [5 empty] | 6157 | 0
ST2PMMVirB_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirB_Ssys | [5 empty] | 6157 | 0
ST2PMMVirB_Usys | REAL | IOD_ST2 | ST2:.PMM.VirB_Usys | [5 empty] | 6157 | 0
ST2PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirBActiveEnergyConsumed_kWh | [5 empty] | 6157 | 0
ST2PMMVirBActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseA_kW | [5 empty] | 6157 | 0
ST2PMMVirBActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseB_kW | [5 empty] | 6157 | 0
ST2PMMVirBActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseC_kW | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_60to80 | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_over80 | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_60to80 | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_over80 | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_60to80 | [5 empty] | 6157 | 0
ST2PMMVirBAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_over80 | [5 empty] | 6157 | 0
ST2PMMVirBAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseA | [5 empty] | 6157 | 0
ST2PMMVirBAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseB | [5 empty] | 6157 | 0
ST2PMMVirBAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseC | [5 empty] | 6157 | 0
ST2PMMVirBCurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseA_A | [5 empty] | 6157 | 0
ST2PMMVirBCurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseB_A | [5 empty] | 6157 | 0
ST2PMMVirBCurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseC_A | [5 empty] | 6157 | 0
ST2PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirBReactiveEnergyConsumed_kVARh | [5 empty] | 6157 | 0
ST2PMMVirBReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseA | [5 empty] | 6157 | 0
ST2PMMVirBReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseB | [5 empty] | 6157 | 0
ST2PMMVirBReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseC | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAB_V | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAN_V | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBC_V | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBN_V | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCA_V | [5 empty] | 6157 | 0
ST2PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCN_V | [5 empty] | 6157 | 0
ST2PrevisokaTemp | DIGITAL | IOD_ST2 | ST2:.PrevisokaTemp | [5 empty] | 6157 | 0
ST2razlitjeLAH1 | DIGITAL | IOD_ST2 | ST2:.razlitjeLAH1 | [5 empty] | 6157 | 0
ST2SetDateTime | DIGITAL | IOD_ST2 | ST2:.SetDateTime | [5 empty] | 6157 | 0
ST2SetDateTimeDemand | DIGITAL | IOD_ST2 | ST2:.SetDateTimeDemand | [5 empty] | 6157 | 0
ST2SetDateTimeError | DIGITAL | IOD_ST2 | ST2:.SetDateTimeError | [5 empty] | 6157 | 0
ST2SetDateTimeFinished | DIGITAL | IOD_ST2 | ST2:.SetDateTimeFinished | [5 empty] | 6157 | 0
ST2SlabaBaterijaPLC | DIGITAL | IOD_ST2 | ST2:.SlabaBaterijaPLC | [5 empty] | 6157 | 0
ST2TIA1_alarm | INT | IOD_ST2 | ST2:.TIA1_alarm | [5 empty] | 6157 | 0
ST2TIA1_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA1_previs_temp | [5 empty] | 6157 | 0
ST2TIA1_temp_s | INT | IOD_ST2 | ST2:.TIA1_temp_s | [5 empty] | 6157 | 0
ST2TIA2_alarm | INT | IOD_ST2 | ST2:.TIA2_alarm | [5 empty] | 6157 | 0
ST2TIA2_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA2_previs_temp | [5 empty] | 6157 | 0
ST2TIA2_temp_s | INT | IOD_ST2 | ST2:.TIA2_temp_s | [5 empty] | 6157 | 0
ST2TIA3_alarm | INT | IOD_ST2 | ST2:.TIA3_alarm | [5 empty] | 6157 | 0
ST2TIA3_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA3_previs_temp | [5 empty] | 6157 | 0
ST2TIA3_temp_s | INT | IOD_ST2 | ST2:.TIA3_temp_s | [5 empty] | 6157 | 0
ST2TIA4_alarm | INT | IOD_ST2 | ST2:.TIA4_alarm | [5 empty] | 6157 | 0
ST2TIA4_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA4_previs_temp | [5 empty] | 6157 | 0
ST2TIA4_temp_s | INT | IOD_ST2 | ST2:.TIA4_temp_s | [5 empty] | 6157 | 0
ST2TIA5_alarm | INT | IOD_ST2 | ST2:.TIA5_alarm | [5 empty] | 6157 | 0
ST2TIA5_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA5_previs_temp | [5 empty] | 6157 | 0
ST2TIA5_temp_s | INT | IOD_ST2 | ST2:.TIA5_temp_s | [5 empty] | 6157 | 0
ST2TIA6_alarm | INT | IOD_ST2 | ST2:.TIA6_alarm | [5 empty] | 6157 | 0
ST2TIA6_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA6_previs_temp | [5 empty] | 6157 | 0
ST2TIA6_temp_s | INT | IOD_ST2 | ST2:.TIA6_temp_s | [5 empty] | 6157 | 0
ST2TIA7_alarm | INT | IOD_ST2 | ST2:.TIA7_alarm | [5 empty] | 6157 | 0
ST2TIA7_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA7_previs_temp | [5 empty] | 6157 | 0
ST2TIA7_temp_s | INT | IOD_ST2 | ST2:.TIA7_temp_s | [5 empty] | 6157 | 0
ST2TIA8_alarm | INT | IOD_ST2 | ST2:.TIA8_alarm | [5 empty] | 6157 | 0
ST2TIA8_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA8_previs_temp | [5 empty] | 6157 | 0
ST2TIA8_temp_s | INT | IOD_ST2 | ST2:.TIA8_temp_s | [5 empty] | 6157 | 0
ST2ups_alarm | DIGITAL | IOD_ST2 | ST2:.ups_alarm | [5 empty] | 6157 | 0
ST2ups_baterijski_nac | DIGITAL | IOD_ST2 | ST2:.ups_baterijski_nac | [5 empty] | 6157 | 0
ST2ups_polnjenje | DIGITAL | IOD_ST2 | ST2:.ups_polnjenje | [5 empty] | 6157 | 0
ST2UserCurrentLevel | BYTE | IOD_ST2 | ST2:.UserCurrentLevel | [5 empty] | 6157 | 0
ST2UserCurrentName | STRING | IOD_ST2 | ST2:.UserCurrentName | [5 empty] | 6157 | 0
ST2UserDisplay | STRING | IOD_ST2 | ST2:.UserDisplay | [5 empty] | 6157 | 0
ST2UserLoggedIn | DIGITAL | IOD_ST2 | ST2:.UserLoggedIn | [5 empty] | 6157 | 0
ST2XVH_AlarmOn | DIGITAL | IOD_ST2 | ST2:.XVH_AlarmOn | [5 empty] | 6157 | 0
ST2Server_B_Izpad | DIGITAL | IOD_ST2_mem | D200
ST2Server_A_Izpad | DIGITAL | IOD_ST2_mem | D201
AST2_omogoci_sms | DIGITAL | IOD_ST2_disk | D1[100]
ST2NapakaSenzorVlagaHIA1_om | DIGITAL | IOD_ST2_disk | D102
ST2NapakaSenzorVlagaHIA2_om | DIGITAL | IOD_ST2_disk | D103
ST2NapakaSenzorVlagaHIA3_om | DIGITAL | IOD_ST2_disk | D104
ST2NapakaSenzorVlagaHIA4_om | DIGITAL | IOD_ST2_disk | D105
ST2NapakaSenzorVlagaHIA5_om | DIGITAL | IOD_ST2_disk | D106
ST2NapakaSenzorVlagaHIA6_om | DIGITAL | IOD_ST2_disk | D107
ST2NapakaSenzorVlagaHIA7_om | DIGITAL | IOD_ST2_disk | D108
ST2NapakaSenzorVlagaHIA8_om | DIGITAL | IOD_ST2_disk | D109
ST2NapakaTSTempTIA1_om | DIGITAL | IOD_ST2_disk | D110
ST2NapakaTSTempTIA2_om | DIGITAL | IOD_ST2_disk | D111
ST2NapakaTSTempTIA3_om | DIGITAL | IOD_ST2_disk | D112
ST2NapakaTSTempTIA4_om | DIGITAL | IOD_ST2_disk | D113
ST2NapakaTSTempTIA5_om | DIGITAL | IOD_ST2_disk | D114
ST2NapakaTSTempTIA6_om | DIGITAL | IOD_ST2_disk | D115
ST2NapakaTSTempTIA7_om | DIGITAL | IOD_ST2_disk | D116
ST2NapakaTSTempTIA8_om | DIGITAL | IOD_ST2_disk | D117
ST2TIA1_previs_temp_om | DIGITAL | IOD_ST2_disk | D118
ST2TIA2_previs_temp_om | DIGITAL | IOD_ST2_disk | D119
ST2TIA3_previs_temp_om | DIGITAL | IOD_ST2_disk | D120
ST2TIA4_previs_temp_om | DIGITAL | IOD_ST2_disk | D121
ST2TIA5_previs_temp_om | DIGITAL | IOD_ST2_disk | D122
ST2TIA6_previs_temp_om | DIGITAL | IOD_ST2_disk | D123
ST2TIA7_previs_temp_om | DIGITAL | IOD_ST2_disk | D124
ST2TIA8_previs_temp_om | DIGITAL | IOD_ST2_disk | D125
ST2razlitjeLAH1_om | DIGITAL | IOD_ST2_disk | D126
ST2Server_A_Izpad_om | DIGITAL | IOD_ST2_disk | D127
ST2Server_B_Izpad_om | DIGITAL | IOD_ST2_disk | D128
ST2napaka_kom_panel_om | DIGITAL | IOD_ST2_disk | D129
ST2SetDateTimeError_om | DIGITAL | IOD_ST2_disk | D130
ST2SlabaBaterijaPLC_om | DIGITAL | IOD_ST2_disk | D131
ST2ups_baterijski_nac_om | DIGITAL | IOD_ST2_disk | D132
ST2ups_alarm_om | DIGITAL | IOD_ST2_disk | D133
ST2ups_polnjenje_om | DIGITAL | IOD_ST2_disk | D134
ST2UserloggedIn_mem | INT | IOD_ST2_mem | I1
ST2_ComSCADA_stevec1 | INT | IOD_ST2_mem | I2
ST2_ComSCADA_stevec2 | INT | IOD_ST2_mem | I3
ST2_ComSCADA_stevec3 | INT | IOD_ST2_mem | I4
ST2_ComSCADA_stevec4 | INT | IOD_ST2_mem | I5
BST2_omogoci_sms | DIGITAL | IOD_ST2_disk | D200[100]
ST2PMMVirACurrent1_med60in80 | DIGITAL | IOD_ST2_disk | D302
ST2PMMVirACurrent2_med60in80 | DIGITAL | IOD_ST2_disk | D303
ST2PMMVirACurrent3_med60in80 | DIGITAL | IOD_ST2_disk | D304
ST2PMMVirACurrent4_med60in80 | DIGITAL | IOD_ST2_disk | D305
ST2PMMVirACurrent5_med60in80 | DIGITAL | IOD_ST2_disk | D306
ST2PMMVirACurrent6_med60in80 | DIGITAL | IOD_ST2_disk | D307
ST2PMMVirACurrent7_med60in80 | DIGITAL | IOD_ST2_disk | D308
ST2PMMVirACurrent8_med60in80 | DIGITAL | IOD_ST2_disk | D309
ST2PMMVirACurrent9_med60in80 | DIGITAL | IOD_ST2_disk | D310
ST2PMMVirACurrent10_med60in80 | DIGITAL | IOD_ST2_disk | D311
ST2PMMVirACurrent11_med60in80 | DIGITAL | IOD_ST2_disk | D312
ST2PMMVirACurrent12_med60in80 | DIGITAL | IOD_ST2_disk | D313
ST2PMMVirACurrent13_med60in80 | DIGITAL | IOD_ST2_disk | D314
ST2PMMVirACurrent14_med60in80 | DIGITAL | IOD_ST2_disk | D315
ST2PMMVirACurrent15_med60in80 | DIGITAL | IOD_ST2_disk | D316
ST2PMMVirACurrent16_med60in80 | DIGITAL | IOD_ST2_disk | D317
ST2PMMVirACurrent17_med60in80 | DIGITAL | IOD_ST2_disk | D318
ST2PMMVirACurrent18_med60in80 | DIGITAL | IOD_ST2_disk | D319
ST2PMMVirACurrent19_med60in80 | DIGITAL | IOD_ST2_disk | D320
ST2PMMVirACurrent20_med60in80 | DIGITAL | IOD_ST2_disk | D321
ST2PMMVirACurrent21_med60in80 | DIGITAL | IOD_ST2_disk | D322
ST2PMMVirACurrent22_med60in80 | DIGITAL | IOD_ST2_disk | D323
ST2PMMVirACurrent23_med60in80 | DIGITAL | IOD_ST2_disk | D324
ST2PMMVirACurrent24_med60in80 | DIGITAL | IOD_ST2_disk | D325
ST2PMMVirACurrent25_med60in80 | DIGITAL | IOD_ST2_disk | D326
ST2PMMVirACurrent26_med60in80 | DIGITAL | IOD_ST2_disk | D327
ST2PMMVirACurrent27_med60in80 | DIGITAL | IOD_ST2_disk | D328
ST2PMMVirACurrent28_med60in80 | DIGITAL | IOD_ST2_disk | D329
ST2PMMVirACurrent29_med60in80 | DIGITAL | IOD_ST2_disk | D330
ST2PMMVirACurrent30_med60in80 | DIGITAL | IOD_ST2_disk | D331
ST2PMMVirACurrent31_med60in80 | DIGITAL | IOD_ST2_disk | D332
ST2PMMVirACurrent32_med60in80 | DIGITAL | IOD_ST2_disk | D333
ST2PMMVirACurrent33_med60in80 | DIGITAL | IOD_ST2_disk | D334
ST2PMMVirACurrent34_med60in80 | DIGITAL | IOD_ST2_disk | D335
ST2PMMVirACurrent35_med60in80 | DIGITAL | IOD_ST2_disk | D336
ST2PMMVirACurrent36_med60in80 | DIGITAL | IOD_ST2_disk | D337
ST2PMMVirACurrent37_med60in80 | DIGITAL | IOD_ST2_disk | D338
ST2PMMVirACurrent38_med60in80 | DIGITAL | IOD_ST2_disk | D339
ST2PMMVirACurrent39_med60in80 | DIGITAL | IOD_ST2_disk | D340
ST2PMMVirACurrent40_med60in80 | DIGITAL | IOD_ST2_disk | D341
ST2PMMVirACurrent41_med60in80 | DIGITAL | IOD_ST2_disk | D342
ST2PMMVirACurrent42_med60in80 | DIGITAL | IOD_ST2_disk | D343
ST2PMMVirACurrent43_med60in80 | DIGITAL | IOD_ST2_disk | D344
ST2PMMVirACurrent44_med60in80 | DIGITAL | IOD_ST2_disk | D345
ST2PMMVirACurrent1_nad80 | DIGITAL | IOD_ST2_disk | D346
ST2PMMVirACurrent2_nad80 | DIGITAL | IOD_ST2_disk | D347
ST2PMMVirACurrent3_nad80 | DIGITAL | IOD_ST2_disk | D348
ST2PMMVirACurrent4_nad80 | DIGITAL | IOD_ST2_disk | D349
ST2PMMVirACurrent5_nad80 | DIGITAL | IOD_ST2_disk | D350
ST2PMMVirACurrent6_nad80 | DIGITAL | IOD_ST2_disk | D351
ST2PMMVirACurrent7_nad80 | DIGITAL | IOD_ST2_disk | D352
ST2PMMVirACurrent8_nad80 | DIGITAL | IOD_ST2_disk | D353
ST2PMMVirACurrent9_nad80 | DIGITAL | IOD_ST2_disk | D354
ST2PMMVirACurrent10_nad80 | DIGITAL | IOD_ST2_disk | D355
ST2PMMVirACurrent11_nad80 | DIGITAL | IOD_ST2_disk | D356
ST2PMMVirACurrent12_nad80 | DIGITAL | IOD_ST2_disk | D357
ST2PMMVirACurrent13_nad80 | DIGITAL | IOD_ST2_disk | D358
ST2PMMVirACurrent14_nad80 | DIGITAL | IOD_ST2_disk | D359
ST2PMMVirACurrent15_nad80 | DIGITAL | IOD_ST2_disk | D360
ST2PMMVirACurrent16_nad80 | DIGITAL | IOD_ST2_disk | D361
ST2PMMVirACurrent17_nad80 | DIGITAL | IOD_ST2_disk | D362
ST2PMMVirACurrent18_nad80 | DIGITAL | IOD_ST2_disk | D363
ST2PMMVirACurrent19_nad80 | DIGITAL | IOD_ST2_disk | D364
ST2PMMVirACurrent20_nad80 | DIGITAL | IOD_ST2_disk | D365
ST2PMMVirACurrent21_nad80 | DIGITAL | IOD_ST2_disk | D366
ST2PMMVirACurrent22_nad80 | DIGITAL | IOD_ST2_disk | D367
ST2PMMVirACurrent23_nad80 | DIGITAL | IOD_ST2_disk | D368
ST2PMMVirACurrent24_nad80 | DIGITAL | IOD_ST2_disk | D369
ST2PMMVirACurrent25_nad80 | DIGITAL | IOD_ST2_disk | D370
ST2PMMVirACurrent26_nad80 | DIGITAL | IOD_ST2_disk | D371
ST2PMMVirACurrent27_nad80 | DIGITAL | IOD_ST2_disk | D372
ST2PMMVirACurrent28_nad80 | DIGITAL | IOD_ST2_disk | D373
ST2PMMVirACurrent29_nad80 | DIGITAL | IOD_ST2_disk | D374
ST2PMMVirACurrent30_nad80 | DIGITAL | IOD_ST2_disk | D375
ST2PMMVirACurrent31_nad80 | DIGITAL | IOD_ST2_disk | D376
ST2PMMVirACurrent32_nad80 | DIGITAL | IOD_ST2_disk | D377
ST2PMMVirACurrent33_nad80 | DIGITAL | IOD_ST2_disk | D378
ST2PMMVirACurrent34_nad80 | DIGITAL | IOD_ST2_disk | D379
ST2PMMVirACurrent35_nad80 | DIGITAL | IOD_ST2_disk | D380
ST2PMMVirACurrent36_nad80 | DIGITAL | IOD_ST2_disk | D381
ST2PMMVirACurrent37_nad80 | DIGITAL | IOD_ST2_disk | D382
ST2PMMVirACurrent38_nad80 | DIGITAL | IOD_ST2_disk | D383
ST2PMMVirACurrent39_nad80 | DIGITAL | IOD_ST2_disk | D384
ST2PMMVirACurrent40_nad80 | DIGITAL | IOD_ST2_disk | D385
ST2PMMVirACurrent41_nad80 | DIGITAL | IOD_ST2_disk | D386
ST2PMMVirACurrent42_nad80 | DIGITAL | IOD_ST2_disk | D387
ST2PMMVirACurrent43_nad80 | DIGITAL | IOD_ST2_disk | D388
ST2PMMVirACurrent44_nad80 | DIGITAL | IOD_ST2_disk | D389
ST2PMMPoljeVirATok1_16_nad80 | DIGITAL | IOD_ST2_disk | D400[16]
ST2PMMPoljeVirATok17_32_nad80 | DIGITAL | IOD_ST2_disk | D417[16]
ST2PMMPoljeVirATok33_44_nad80 | DIGITAL | IOD_ST2_disk | D434[16]
ST2PMMPoljeVirBTok1_16_nad80 | DIGITAL | IOD_ST2_disk | D451[16]
ST2PMMPoljeVirBTok17_32_nad80 | DIGITAL | IOD_ST2_disk | D468[16]
ST2PMMPoljeVirBTok33_44_nad80 | DIGITAL | IOD_ST2_disk | D485[16]
ST2PMMPoljeVirATok1_16_med60_80 | DIGITAL | IOD_ST2_disk | D502[16]
ST2PMMPoljeVirATok17_32_med60_80 | DIGITAL | IOD_ST2_disk | D519[16]
ST2PMMPoljeVirATok33_44_med60_80 | DIGITAL | IOD_ST2_disk | D536[16]
ST2PMMPoljeVirBTok1_16_med60_80 | DIGITAL | IOD_ST2_disk | D553[16]
ST2PMMPoljeVirBTok17_32_med60_80 | DIGITAL | IOD_ST2_disk | D570[16]
ST2PMMPoljeVirBTok33_44_med60_80 | DIGITAL | IOD_ST2_disk | D587[16]
ST2PrikaziPMM | DIGITAL | IOD_ST2_disk | D603
ST2PMM_2x63_VirB_zavihek | DIGITAL | IOD_ST2_disk | D604
ST2PMM_2x63_VirA_zavihek | DIGITAL | IOD_ST2_disk | D605
ST2PMMOverCurrentBetw1_VirA | DIGITAL | IOD_ST2_disk | D606
ST2PMMOverCurrentBetw1_VirB | DIGITAL | IOD_ST2_disk | D607
ST2PMMOverCurrentOver1_VirA | DIGITAL | IOD_ST2_disk | D608
ST2PMMOverCurrentOver1_VirB | DIGITAL | IOD_ST2_disk | D609
ST2PMMOverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_ST2_disk | D610
ST2PMMOverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_ST2_disk | D611
ST2PMMOverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_ST2_disk | D612
ST2PMMOverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_ST2_disk | D613
ST2PMM1OverVoltage_Omogoci | DIGITAL | IOD_ST2_disk | D614
ST2ErrComPMM_Omogoci | DIGITAL | IOD_ST2_disk | D615
ST2PMMVirACurrent1_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D616
ST2PMMVirACurrent2_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D617
ST2PMMVirACurrent3_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D618
ST2PMMVirACurrent4_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D619
ST2PMMVirACurrent5_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D620
ST2PMMVirACurrent6_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D621
ST2PMMVirACurrent7_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D622
ST2PMMVirACurrent8_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D623
ST2PMMVirACurrent9_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D624
ST2PMMVirACurrent10_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D625
ST2PMMVirACurrent11_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D626
ST2PMMVirACurrent12_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D627
ST2PMMVirACurrent13_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D628
ST2PMMVirACurrent14_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D629
ST2PMMVirACurrent15_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D630
ST2PMMVirACurrent16_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D631
ST2PMMVirACurrent17_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D632
ST2PMMVirACurrent18_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D633
ST2PMMVirACurrent19_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D634
ST2PMMVirACurrent20_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D635
ST2PMMVirACurrent21_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D636
ST2PMMVirACurrent22_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D637
ST2PMMVirACurrent23_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D638
ST2PMMVirACurrent24_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D639
ST2PMMVirACurrent25_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D640
ST2PMMVirACurrent26_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D641
ST2PMMVirACurrent27_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D642
ST2PMMVirACurrent28_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D643
ST2PMMVirACurrent29_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D644
ST2PMMVirACurrent30_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D645
ST2PMMVirACurrent31_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D646
ST2PMMVirACurrent32_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D647
ST2PMMVirACurrent33_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D648
ST2PMMVirACurrent34_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D649
ST2PMMVirACurrent35_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D650
ST2PMMVirACurrent36_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D651
ST2PMMVirACurrent37_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D652
ST2PMMVirACurrent38_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D653
ST2PMMVirACurrent39_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D654
ST2PMMVirACurrent40_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D655
ST2PMMVirACurrent41_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D656
ST2PMMVirACurrent42_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D657
ST2PMMVirACurrent43_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D658
ST2PMMVirACurrent44_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D659
ST2PMMVirACurrent1_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D660
ST2PMMVirACurrent2_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D661
ST2PMMVirACurrent3_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D662
ST2PMMVirACurrent4_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D663
ST2PMMVirACurrent5_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D664
ST2PMMVirACurrent6_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D665
ST2PMMVirACurrent7_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D666
ST2PMMVirACurrent8_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D667
ST2PMMVirACurrent9_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D668
ST2PMMVirACurrent10_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D669
ST2PMMVirACurrent11_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D670
ST2PMMVirACurrent12_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D671
ST2PMMVirACurrent13_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D672
ST2PMMVirACurrent14_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D673
ST2PMMVirACurrent15_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D674
ST2PMMVirACurrent16_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D675
ST2PMMVirACurrent17_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D676
ST2PMMVirACurrent18_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D677
ST2PMMVirACurrent19_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D678
ST2PMMVirACurrent20_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D679
ST2PMMVirACurrent21_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D680
ST2PMMVirACurrent22_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D681
ST2PMMVirACurrent23_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D682
ST2PMMVirACurrent24_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D683
ST2PMMVirACurrent25_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D684
ST2PMMVirACurrent26_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D685
ST2PMMVirACurrent27_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D686
ST2PMMVirACurrent28_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D687
ST2PMMVirACurrent29_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D688
ST2PMMVirACurrent30_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D689
ST2PMMVirACurrent31_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D690
ST2PMMVirACurrent32_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D691
ST2PMMVirACurrent33_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D692
ST2PMMVirACurrent34_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D693
ST2PMMVirACurrent35_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D694
ST2PMMVirACurrent36_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D695
ST2PMMVirACurrent37_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D696
ST2PMMVirACurrent38_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D697
ST2PMMVirACurrent39_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D698
ST2PMMVirACurrent40_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D699
ST2PMMVirACurrent41_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D700
ST2PMMVirACurrent42_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D701
ST2PMMVirACurrent43_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D702
ST2PMMVirACurrent44_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D703
ST2PMMOverCurrentBetw1_VirB_1 | DIGITAL | IOD_ST2_disk | D704
ST2PMMOverCurrentBetw1_VirA_1 | DIGITAL | IOD_ST2_disk | D705
ST2PMMOverCurrentOver1_VirB_1 | DIGITAL | IOD_ST2_disk | D706
ST2PMMOverCurrentOver1_VirA_1 | DIGITAL | IOD_ST2_disk | D707
ST2PMMOverCurrentBetw1_VirB_2 | DIGITAL | IOD_ST2_disk | D708
ST2PMMOverCurrentBetw1_VirA_2 | DIGITAL | IOD_ST2_disk | D709
ST2PMMOverCurrentBetw1_VirB_3 | DIGITAL | IOD_ST2_disk | D710
ST2PMMOverCurrentBetw1_VirA_3 | DIGITAL | IOD_ST2_disk | D711
ST2PMMOverCurrentOver1_VirB_2 | DIGITAL | IOD_ST2_disk | D712
ST2PMMOverCurrentOver1_VirA_2 | DIGITAL | IOD_ST2_disk | D713
ST2PMMOverCurrentOver1_VirB_3 | DIGITAL | IOD_ST2_disk | D714
ST2PMMOverCurrentOver1_VirA_3 | DIGITAL | IOD_ST2_disk | D715
ST2VsotaVirB_1_16B_med | INT | IOD_ST2_disk | I6
ST2VsotaVirB_17_32B_med | INT | IOD_ST2_disk | I7
ST2VsotaVirB_33_44B_med | INT | IOD_ST2_disk | I8
ST2VsotaVirA_1_16A_med | INT | IOD_ST2_disk | I9
ST2VsotaVirA_17_32A_med | INT | IOD_ST2_disk | I10
ST2VsotaVirA_33_44A_med | INT | IOD_ST2_disk | I11
ST2VsotaVirB_1_16B_nad | INT | IOD_ST2_disk | I12
ST2VsotaVirB_17_32B_nad | INT | IOD_ST2_disk | I13
ST2VsotaVirB_33_44B_nad | INT | IOD_ST2_disk | I14
ST2VsotaVirA_1_16A_nad | INT | IOD_ST2_disk | I15
ST2VsotaVirA_17_32A_nad | INT | IOD_ST2_disk | I16
ST2VsotaVirA_33_44A_nad | INT | IOD_ST2_disk | I17
ST2PMMVirBCurrent1_med60in80 | DIGITAL | IOD_ST2_disk | D716
ST2PMMVirBCurrent2_med60in80 | DIGITAL | IOD_ST2_disk | D717
ST2PMMVirBCurrent3_med60in80 | DIGITAL | IOD_ST2_disk | D718
ST2PMMVirBCurrent4_med60in80 | DIGITAL | IOD_ST2_disk | D719
ST2PMMVirBCurrent5_med60in80 | DIGITAL | IOD_ST2_disk | D720
ST2PMMVirBCurrent6_med60in80 | DIGITAL | IOD_ST2_disk | D721
ST2PMMVirBCurrent7_med60in80 | DIGITAL | IOD_ST2_disk | D722
ST2PMMVirBCurrent8_med60in80 | DIGITAL | IOD_ST2_disk | D723
ST2PMMVirBCurrent9_med60in80 | DIGITAL | IOD_ST2_disk | D724
ST2PMMVirBCurrent10_med60in80 | DIGITAL | IOD_ST2_disk | D725
ST2PMMVirBCurrent11_med60in80 | DIGITAL | IOD_ST2_disk | D726
ST2PMMVirBCurrent12_med60in80 | DIGITAL | IOD_ST2_disk | D727
ST2PMMVirBCurrent13_med60in80 | DIGITAL | IOD_ST2_disk | D728
ST2PMMVirBCurrent14_med60in80 | DIGITAL | IOD_ST2_disk | D729
ST2PMMVirBCurrent15_med60in80 | DIGITAL | IOD_ST2_disk | D730
ST2PMMVirBCurrent16_med60in80 | DIGITAL | IOD_ST2_disk | D731
ST2PMMVirBCurrent17_med60in80 | DIGITAL | IOD_ST2_disk | D732
ST2PMMVirBCurrent18_med60in80 | DIGITAL | IOD_ST2_disk | D733
ST2PMMVirBCurrent19_med60in80 | DIGITAL | IOD_ST2_disk | D734
ST2PMMVirBCurrent20_med60in80 | DIGITAL | IOD_ST2_disk | D735
ST2PMMVirBCurrent21_med60in80 | DIGITAL | IOD_ST2_disk | D736
ST2PMMVirBCurrent22_med60in80 | DIGITAL | IOD_ST2_disk | D737
ST2PMMVirBCurrent23_med60in80 | DIGITAL | IOD_ST2_disk | D738
ST2PMMVirBCurrent24_med60in80 | DIGITAL | IOD_ST2_disk | D739
ST2PMMVirBCurrent25_med60in80 | DIGITAL | IOD_ST2_disk | D740
ST2PMMVirBCurrent26_med60in80 | DIGITAL | IOD_ST2_disk | D741
ST2PMMVirBCurrent27_med60in80 | DIGITAL | IOD_ST2_disk | D742
ST2PMMVirBCurrent28_med60in80 | DIGITAL | IOD_ST2_disk | D743
ST2PMMVirBCurrent29_med60in80 | DIGITAL | IOD_ST2_disk | D744
ST2PMMVirBCurrent30_med60in80 | DIGITAL | IOD_ST2_disk | D745
ST2PMMVirBCurrent31_med60in80 | DIGITAL | IOD_ST2_disk | D746
ST2PMMVirBCurrent32_med60in80 | DIGITAL | IOD_ST2_disk | D747
ST2PMMVirBCurrent33_med60in80 | DIGITAL | IOD_ST2_disk | D748
ST2PMMVirBCurrent34_med60in80 | DIGITAL | IOD_ST2_disk | D749
ST2PMMVirBCurrent35_med60in80 | DIGITAL | IOD_ST2_disk | D750
ST2PMMVirBCurrent36_med60in80 | DIGITAL | IOD_ST2_disk | D751
ST2PMMVirBCurrent37_med60in80 | DIGITAL | IOD_ST2_disk | D752
ST2PMMVirBCurrent38_med60in80 | DIGITAL | IOD_ST2_disk | D753
ST2PMMVirBCurrent39_med60in80 | DIGITAL | IOD_ST2_disk | D754
ST2PMMVirBCurrent40_med60in80 | DIGITAL | IOD_ST2_disk | D755
ST2PMMVirBCurrent41_med60in80 | DIGITAL | IOD_ST2_disk | D756
ST2PMMVirBCurrent42_med60in80 | DIGITAL | IOD_ST2_disk | D757
ST2PMMVirBCurrent43_med60in80 | DIGITAL | IOD_ST2_disk | D758
ST2PMMVirBCurrent44_med60in80 | DIGITAL | IOD_ST2_disk | D759
ST2PMMVirBCurrent1_nad80 | DIGITAL | IOD_ST2_disk | D760
ST2PMMVirBCurrent2_nad80 | DIGITAL | IOD_ST2_disk | D761
ST2PMMVirBCurrent3_nad80 | DIGITAL | IOD_ST2_disk | D762
ST2PMMVirBCurrent4_nad80 | DIGITAL | IOD_ST2_disk | D763
ST2PMMVirBCurrent5_nad80 | DIGITAL | IOD_ST2_disk | D764
ST2PMMVirBCurrent6_nad80 | DIGITAL | IOD_ST2_disk | D765
ST2PMMVirBCurrent7_nad80 | DIGITAL | IOD_ST2_disk | D766
ST2PMMVirBCurrent8_nad80 | DIGITAL | IOD_ST2_disk | D767
ST2PMMVirBCurrent9_nad80 | DIGITAL | IOD_ST2_disk | D768
ST2PMMVirBCurrent10_nad80 | DIGITAL | IOD_ST2_disk | D769
ST2PMMVirBCurrent11_nad80 | DIGITAL | IOD_ST2_disk | D770
ST2PMMVirBCurrent12_nad80 | DIGITAL | IOD_ST2_disk | D771
ST2PMMVirBCurrent13_nad80 | DIGITAL | IOD_ST2_disk | D772
ST2PMMVirBCurrent14_nad80 | DIGITAL | IOD_ST2_disk | D773
ST2PMMVirBCurrent15_nad80 | DIGITAL | IOD_ST2_disk | D774
ST2PMMVirBCurrent16_nad80 | DIGITAL | IOD_ST2_disk | D775
ST2PMMVirBCurrent17_nad80 | DIGITAL | IOD_ST2_disk | D776
ST2PMMVirBCurrent18_nad80 | DIGITAL | IOD_ST2_disk | D777
ST2PMMVirBCurrent19_nad80 | DIGITAL | IOD_ST2_disk | D778
ST2PMMVirBCurrent20_nad80 | DIGITAL | IOD_ST2_disk | D779
ST2PMMVirBCurrent21_nad80 | DIGITAL | IOD_ST2_disk | D780
ST2PMMVirBCurrent22_nad80 | DIGITAL | IOD_ST2_disk | D781
ST2PMMVirBCurrent23_nad80 | DIGITAL | IOD_ST2_disk | D782
ST2PMMVirBCurrent24_nad80 | DIGITAL | IOD_ST2_disk | D783
ST2PMMVirBCurrent25_nad80 | DIGITAL | IOD_ST2_disk | D784
ST2PMMVirBCurrent26_nad80 | DIGITAL | IOD_ST2_disk | D785
ST2PMMVirBCurrent27_nad80 | DIGITAL | IOD_ST2_disk | D786
ST2PMMVirBCurrent28_nad80 | DIGITAL | IOD_ST2_disk | D787
ST2PMMVirBCurrent29_nad80 | DIGITAL | IOD_ST2_disk | D788
ST2PMMVirBCurrent30_nad80 | DIGITAL | IOD_ST2_disk | D789
ST2PMMVirBCurrent31_nad80 | DIGITAL | IOD_ST2_disk | D790
ST2PMMVirBCurrent32_nad80 | DIGITAL | IOD_ST2_disk | D791
ST2PMMVirBCurrent33_nad80 | DIGITAL | IOD_ST2_disk | D792
ST2PMMVirBCurrent34_nad80 | DIGITAL | IOD_ST2_disk | D793
ST2PMMVirBCurrent35_nad80 | DIGITAL | IOD_ST2_disk | D794
ST2PMMVirBCurrent36_nad80 | DIGITAL | IOD_ST2_disk | D795
ST2PMMVirBCurrent37_nad80 | DIGITAL | IOD_ST2_disk | D796
ST2PMMVirBCurrent38_nad80 | DIGITAL | IOD_ST2_disk | D797
ST2PMMVirBCurrent39_nad80 | DIGITAL | IOD_ST2_disk | D798
ST2PMMVirBCurrent40_nad80 | DIGITAL | IOD_ST2_disk | D799
ST2PMMVirBCurrent41_nad80 | DIGITAL | IOD_ST2_disk | D800
ST2PMMVirBCurrent42_nad80 | DIGITAL | IOD_ST2_disk | D801
ST2PMMVirBCurrent43_nad80 | DIGITAL | IOD_ST2_disk | D802
ST2PMMVirBCurrent44_nad80 | DIGITAL | IOD_ST2_disk | D803
ST2PMMVirBCurrent1_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D804
ST2PMMVirBCurrent2_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D805
ST2PMMVirBCurrent3_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D806
ST2PMMVirBCurrent4_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D807
ST2PMMVirBCurrent5_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D808
ST2PMMVirBCurrent6_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D809
ST2PMMVirBCurrent7_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D810
ST2PMMVirBCurrent8_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D811
ST2PMMVirBCurrent9_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D812
ST2PMMVirBCurrent10_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D813
ST2PMMVirBCurrent11_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D814
ST2PMMVirBCurrent12_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D815
ST2PMMVirBCurrent13_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D816
ST2PMMVirBCurrent14_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D817
ST2PMMVirBCurrent15_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D818
ST2PMMVirBCurrent16_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D819
ST2PMMVirBCurrent17_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D820
ST2PMMVirBCurrent18_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D821
ST2PMMVirBCurrent19_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D822
ST2PMMVirBCurrent20_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D823
ST2PMMVirBCurrent21_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D824
ST2PMMVirBCurrent22_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D825
ST2PMMVirBCurrent23_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D826
ST2PMMVirBCurrent24_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D827
ST2PMMVirBCurrent25_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D828
ST2PMMVirBCurrent26_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D829
ST2PMMVirBCurrent27_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D830
ST2PMMVirBCurrent28_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D831
ST2PMMVirBCurrent29_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D832
ST2PMMVirBCurrent30_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D833
ST2PMMVirBCurrent31_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D834
ST2PMMVirBCurrent32_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D835
ST2PMMVirBCurrent33_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D836
ST2PMMVirBCurrent34_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D837
ST2PMMVirBCurrent35_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D838
ST2PMMVirBCurrent36_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D839
ST2PMMVirBCurrent37_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D840
ST2PMMVirBCurrent38_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D841
ST2PMMVirBCurrent39_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D842
ST2PMMVirBCurrent40_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D843
ST2PMMVirBCurrent41_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D844
ST2PMMVirBCurrent42_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D845
ST2PMMVirBCurrent43_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D846
ST2PMMVirBCurrent44_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D847
ST2PMMVirBCurrent1_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D848
ST2PMMVirBCurrent2_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D849
ST2PMMVirBCurrent3_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D850
ST2PMMVirBCurrent4_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D851
ST2PMMVirBCurrent5_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D852
ST2PMMVirBCurrent6_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D853
ST2PMMVirBCurrent7_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D854
ST2PMMVirBCurrent8_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D855
ST2PMMVirBCurrent9_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D856
ST2PMMVirBCurrent10_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D857
ST2PMMVirBCurrent11_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D858
ST2PMMVirBCurrent12_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D859
ST2PMMVirBCurrent13_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D860
ST2PMMVirBCurrent14_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D861
ST2PMMVirBCurrent15_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D862
ST2PMMVirBCurrent16_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D863
ST2PMMVirBCurrent17_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D864
ST2PMMVirBCurrent18_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D865
ST2PMMVirBCurrent19_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D866
ST2PMMVirBCurrent20_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D867
ST2PMMVirBCurrent21_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D868
ST2PMMVirBCurrent22_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D869
ST2PMMVirBCurrent23_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D870
ST2PMMVirBCurrent24_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D871
ST2PMMVirBCurrent25_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D872
ST2PMMVirBCurrent26_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D873
ST2PMMVirBCurrent27_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D874
ST2PMMVirBCurrent28_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D875
ST2PMMVirBCurrent29_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D876
ST2PMMVirBCurrent30_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D877
ST2PMMVirBCurrent31_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D878
ST2PMMVirBCurrent32_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D879
ST2PMMVirBCurrent33_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D880
ST2PMMVirBCurrent34_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D881
ST2PMMVirBCurrent35_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D882
ST2PMMVirBCurrent36_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D883
ST2PMMVirBCurrent37_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D884
ST2PMMVirBCurrent38_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D885
ST2PMMVirBCurrent39_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D886
ST2PMMVirBCurrent40_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D887
ST2PMMVirBCurrent41_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D888
ST2PMMVirBCurrent42_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D889
ST2PMMVirBCurrent43_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D890
ST2PMMVirBCurrent44_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D891
ST2PLC_SB_IROGSM21_F2_2_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D892
ST2PLC_SB_IROGSM22_F2_2_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D893
ST2DI_SB_IROGSM21_Q0_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D894
ST2DI_SB_IROGSM21_Q0_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D895
ST2DI_SB_IROGSM21_Q11_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D896
ST2DI_SB_IROGSM21_Q11_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D897
ST2DI_SB_IROGSM21_Q12_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D898
ST2DI_SB_IROGSM21_Q12_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D899
ST2DI_SB_IROGSM21_Q13_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D900
ST2DI_SB_IROGSM21_Q13_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D901
ST2DI_SB_IROGSM21_Q14_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D902
ST2DI_SB_IROGSM21_Q14_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D903
ST2DI_SB_IROGSM21_Q15_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D904
ST2DI_SB_IROGSM21_Q15_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D905
ST2DI_SB_IROGSM22_Q0_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D906
ST2DI_SB_IROGSM22_Q0_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D907
ST2DI_SB_IROGSM22_Q11_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D908
ST2DI_SB_IROGSM22_Q11_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D909
ST2DI_SB_IROGSM22_Q12_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D910
ST2DI_SB_IROGSM22_Q12_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D911
ST2DI_SB_IROGSM22_Q13_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D912
ST2DI_SB_IROGSM22_Q13_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D913
ST2DI_SB_IROGSM22_Q14_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D914
ST2DI_SB_IROGSM22_Q14_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D915
ST2DI_SB_IROGSM22_Q15_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D916
ST2DI_SB_IROGSM22_Q15_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D917
ST2NSX1StatusSwitch_Omogoci | INT | IOD_ST2_disk | I18
ST2NSX2StatusSwitch_Omogoci | INT | IOD_ST2_disk | I19
ST2NSX3StatusSwitch_Omogoci | INT | IOD_ST2_disk | I20
ST2NSX4StatusSwitch_Omogoci | INT | IOD_ST2_disk | I21
ST2NSX5StatusSwitch_Omogoci | INT | IOD_ST2_disk | I22
ST2NSX6StatusSwitch_Omogoci | INT | IOD_ST2_disk | I23
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D928
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D929
ST2_DanEnergNSX1 | LONG | IOD_ST2_disk | L0[30]
ST2_CasDDanEnergNSX1 | INT | IOD_ST2_disk | I30[30]
ST2_CasMDanEnergNSX1 | INT | IOD_ST2_disk | I60[30]
ST2_TedenEnergNSX1 | LONG | IOD_ST2_disk | L30[30]
ST2_CasDTedenEnergNSX1 | INT | IOD_ST2_disk | I90[30]
ST2_CasMTedenEnergNSX1 | INT | IOD_ST2_disk | I120[30]
ST2_MesecEnergNSX1 | LONG | IOD_ST2_disk | L90[30]
ST2_CasDMesecEnergNSX1 | INT | IOD_ST2_disk | I150[30]
ST2_CasMMesecEnergNSX1 | INT | IOD_ST2_disk | I180[30]
ST2_StSt_DanEnergNSX1 | LONG | IOD_ST2_disk | L121
ST2_StSt_TedenEnergNSX1 | LONG | IOD_ST2_disk | L122
ST2_StSt_MesecEnergNSX1 | LONG | IOD_ST2_disk | L123
ST2_StStCasDDanEnergNSX1 | INT | IOD_ST2_disk | I211
ST2_StStCasMDanEnergNSX1 | INT | IOD_ST2_disk | I212
ST2_StStCasDTedenEnergNSX1 | INT | IOD_ST2_disk | I213
ST2_StStCasMTedenEnergNSX1 | INT | IOD_ST2_disk | I214
ST2_StStCasDMesecEnergNSX1 | INT | IOD_ST2_disk | I215
ST2_StStCasMMesecEnergNSX1 | INT | IOD_ST2_disk | I216
ST2_MaxDnevnaEnergija1 | LONG | IOD_ST2_disk | L124 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija1 | LONG | IOD_ST2_disk | L125 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija1 | LONG | IOD_ST2_disk | L126 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX1 | LONG | IOD_ST2_disk | L127
ST2_Anali_razlika_tedenNSX1 | LONG | IOD_ST2_disk | L128
ST2_Anali_razlika_mesNSX1 | LONG | IOD_ST2_disk | L129
ST2Circ_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1002
ST2Circ_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1003
ST2Circ_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1004
ST2Circ_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1005
ST2Circ_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1006
ST2Circ_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1007
ST2_DanEnergNSX2 | LONG | IOD_ST2_disk | L130[30]
ST2_CasDDanEnergNSX2 | INT | IOD_ST2_disk | I220[30]
ST2_CasMDanEnergNSX2 | INT | IOD_ST2_disk | I250[30]
ST2_TedenEnergNSX2 | LONG | IOD_ST2_disk | L160[30]
ST2_CasDTedenEnergNSX2 | INT | IOD_ST2_disk | I280[30]
ST2_CasMTedenEnergNSX2 | INT | IOD_ST2_disk | I310[30]
ST2_MesecEnergNSX2 | LONG | IOD_ST2_disk | L190[30]
ST2_CasDMesecEnergNSX2 | INT | IOD_ST2_disk | I340[30]
ST2_CasMMesecEnergNSX2 | INT | IOD_ST2_disk | I370[30]
ST2_StSt_DanEnergNSX2 | LONG | IOD_ST2_disk | L221
ST2_StSt_TedenEnergNSX2 | LONG | IOD_ST2_disk | L222
ST2_StSt_MesecEnergNSX2 | LONG | IOD_ST2_disk | L223
ST2_StStCasDDanEnergNSX2 | INT | IOD_ST2_disk | I400
ST2_StStCasMDanEnergNSX2 | INT | IOD_ST2_disk | I401
ST2_StStCasDTedenEnergNSX2 | INT | IOD_ST2_disk | I402
ST2_StStCasMTedenEnergNSX2 | INT | IOD_ST2_disk | I403
ST2_StStCasDMesecEnergNSX2 | INT | IOD_ST2_disk | I404
ST2_StStCasMMesecEnergNSX2 | INT | IOD_ST2_disk | I405
ST2_MaxDnevnaEnergija2 | LONG | IOD_ST2_disk | L224 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija2 | LONG | IOD_ST2_disk | L225 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija2 | LONG | IOD_ST2_disk | L226 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX2 | LONG | IOD_ST2_disk | L227
ST2_Anali_razlika_tedenNSX2 | LONG | IOD_ST2_disk | L228
ST2_Anali_razlika_mesNSX2 | LONG | IOD_ST2_disk | L229
ST2_DanEnergNSX3 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX3 | INT | IOD_ST2_disk | I410[30]
ST2_CasMDanEnergNSX3 | INT | IOD_ST2_disk | I440[30]
ST2_TedenEnergNSX3 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX3 | INT | IOD_ST2_disk | I470[30]
ST2_CasMTedenEnergNSX3 | INT | IOD_ST2_disk | I500[30]
ST2_MesecEnergNSX3 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX3 | INT | IOD_ST2_disk | I530[30]
ST2_CasMMesecEnergNSX3 | INT | IOD_ST2_disk | I560[30]
ST2_StSt_DanEnergNSX3 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX3 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX3 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX3 | INT | IOD_ST2_disk | I590
ST2_StStCasMDanEnergNSX3 | INT | IOD_ST2_disk | I591
ST2_StStCasDTedenEnergNSX3 | INT | IOD_ST2_disk | I592
ST2_StStCasMTedenEnergNSX3 | INT | IOD_ST2_disk | I593
ST2_StStCasDMesecEnergNSX3 | INT | IOD_ST2_disk | I594
ST2_StStCasMMesecEnergNSX3 | INT | IOD_ST2_disk | I595
ST2_MaxDnevnaEnergija3 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija3 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija3 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX3 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX3 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX3 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX4 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX4 | INT | IOD_ST2_disk | I600[30]
ST2_CasMDanEnergNSX4 | INT | IOD_ST2_disk | I630[30]
ST2_TedenEnergNSX4 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX4 | INT | IOD_ST2_disk | I660[30]
ST2_CasMTedenEnergNSX4 | INT | IOD_ST2_disk | I690[30]
ST2_MesecEnergNSX4 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX4 | INT | IOD_ST2_disk | I720[30]
ST2_CasMMesecEnergNSX4 | INT | IOD_ST2_disk | I750[30]
ST2_StSt_DanEnergNSX4 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX4 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX4 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX4 | INT | IOD_ST2_disk | I780
ST2_StStCasMDanEnergNSX4 | INT | IOD_ST2_disk | I781
ST2_StStCasDTedenEnergNSX4 | INT | IOD_ST2_disk | I782
ST2_StStCasMTedenEnergNSX4 | INT | IOD_ST2_disk | I783
ST2_StStCasDMesecEnergNSX4 | INT | IOD_ST2_disk | I784
ST2_StStCasMMesecEnergNSX4 | INT | IOD_ST2_disk | I785
ST2_MaxDnevnaEnergija4 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija4 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija4 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX4 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX4 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX4 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX5 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX5 | INT | IOD_ST2_disk | I790[30]
ST2_CasMDanEnergNSX5 | INT | IOD_ST2_disk | I820[30]
ST2_TedenEnergNSX5 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX5 | INT | IOD_ST2_disk | I850[30]
ST2_CasMTedenEnergNSX5 | INT | IOD_ST2_disk | I880[30]
ST2_MesecEnergNSX5 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX5 | INT | IOD_ST2_disk | I910[30]
ST2_CasMMesecEnergNSX5 | INT | IOD_ST2_disk | I940[30]
ST2_StSt_DanEnergNSX5 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX5 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX5 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX5 | INT | IOD_ST2_disk | I970
ST2_StStCasMDanEnergNSX5 | INT | IOD_ST2_disk | I971
ST2_StStCasDTedenEnergNSX5 | INT | IOD_ST2_disk | I972
ST2_StStCasMTedenEnergNSX5 | INT | IOD_ST2_disk | I973
ST2_StStCasDMesecEnergNSX5 | INT | IOD_ST2_disk | I974
ST2_StStCasMMesecEnergNSX5 | INT | IOD_ST2_disk | I975
ST2_MaxDnevnaEnergija5 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija5 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija5 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX5 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX5 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX5 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX6 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX6 | INT | IOD_ST2_disk | I980[30]
ST2_CasMDanEnergNSX6 | INT | IOD_ST2_disk | I1010[30]
ST2_TedenEnergNSX6 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX6 | INT | IOD_ST2_disk | I1040[30]
ST2_CasMTedenEnergNSX6 | INT | IOD_ST2_disk | I1070[30]
ST2_MesecEnergNSX6 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX6 | INT | IOD_ST2_disk | I1100[30]
ST2_CasMMesecEnergNSX6 | INT | IOD_ST2_disk | I1130[30]
ST2_StSt_DanEnergNSX6 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX6 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX6 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX6 | INT | IOD_ST2_disk | I1160
ST2_StStCasMDanEnergNSX6 | INT | IOD_ST2_disk | I1161
ST2_StStCasDTedenEnergNSX6 | INT | IOD_ST2_disk | I1162
ST2_StStCasMTedenEnergNSX6 | INT | IOD_ST2_disk | I1163
ST2_StStCasDMesecEnergNSX6 | INT | IOD_ST2_disk | I1164
ST2_StStCasMMesecEnergNSX6 | INT | IOD_ST2_disk | I1165
ST2_MaxDnevnaEnergija6 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija6 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija6 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX6 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX6 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX6 | LONG | IOD_ST2_disk | L329
ST2DI_SB_IROGSM21_Q13_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D930
ST2DI_SB_IROGSM21_Q14_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D931
ST2DI_SB_IROGSM21_Q15_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D932
ST2DI_SB_IROGSM22_Q13_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D933
ST2DI_SB_IROGSM22_Q14_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D934
ST2DI_SB_IROGSM22_Q15_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D935

## variable_1
ST2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada1
ST2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada2
ST2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada1
ST2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada2
ST2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada1
ST2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada2
ST2ComError | DIGITAL | IOD_ST2 | ST2:.ComError
ST2ComSCADA | DIGITAL | IOD_ST2 | ST2:.ComSCADA
ST2ComSCADA1 | DIGITAL | IOD_ST2 | ST2:.ComSCADA1
ST2ComSCADA2 | DIGITAL | IOD_ST2 | ST2:.ComSCADA2
ST2ComSCADA3 | DIGITAL | IOD_ST2 | ST2:.ComSCADA3
ST2Date_Time0 | STRING | IOD_ST2 | ST2:.Date_Time[0]
ST2Date_Time1 | STRING | IOD_ST2 | ST2:.Date_Time[1]
ST2Date_Time2 | STRING | IOD_ST2 | ST2:.Date_Time[2]
ST2Date_Time3 | STRING | IOD_ST2 | ST2:.Date_Time[3]
ST2DateTimeDan | INT | IOD_ST2 | ST2:.DateTime.Dan | BYTE
ST2DateTimeLeto | INT | IOD_ST2 | ST2:.DateTime.Leto | BYTE
ST2DateTimeLeto2 | INT | IOD_ST2 | ST2:.DateTime.Leto2
ST2DateTimeMesec | INT | IOD_ST2 | ST2:.DateTime.Mesec | BYTE
ST2DateTimeMinuta | INT | IOD_ST2 | ST2:.DateTime.Minuta | BYTE
ST2DateTimePLC_Dan | INT | IOD_ST2 | ST2:.DateTime.PLC_Dan | BYTE
ST2DateTimePLC_DanVTednu | INT | IOD_ST2 | ST2:.DateTime.PLC_DanVTednu | BYTE
ST2DateTimePLC_Leto | INT | IOD_ST2 | ST2:.DateTime.PLC_Leto | BYTE
ST2DateTimePLC_Mesec | INT | IOD_ST2 | ST2:.DateTime.PLC_Mesec | BYTE
ST2DateTimePLC_Minuta | INT | IOD_ST2 | ST2:.DateTime.PLC_Minuta | BYTE
ST2DateTimePLC_Sekunda | INT | IOD_ST2 | ST2:.DateTime.PLC_Sekunda | BYTE
ST2DateTimePLC_Ura | INT | IOD_ST2 | ST2:.DateTime.PLC_Ura | BYTE
ST2DateTimeSekunda | INT | IOD_ST2 | ST2:.DateTime.Sekunda | BYTE
ST2DateTimeUra | INT | IOD_ST2 | ST2:.DateTime.Ura | BYTE
ST2DI2_I10_Rezerva3 | DIGITAL | IOD_ST2 | ST2:.DI2_I10_Rezerva3
ST2DI2_I11_Rezerva4 | DIGITAL | IOD_ST2 | ST2:.DI2_I11_Rezerva4
ST2DI2_I12_Rezerva5 | DIGITAL | IOD_ST2 | ST2:.DI2_I12_Rezerva5
ST2DI2_I13_Rezerva6 | DIGITAL | IOD_ST2 | ST2:.DI2_I13_Rezerva6
ST2DI2_I8_Rezerva1 | DIGITAL | IOD_ST2 | ST2:.DI2_I8_Rezerva1
ST2DI2_I9_Rezerva2 | DIGITAL | IOD_ST2 | ST2:.DI2_I9_Rezerva2
ST2DI_SB_IROGSM21_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Izkljucen
ST2DI_SB_IROGSM21_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Vkljucen
ST2DI_SB_IROGSM21_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Izkljucen
ST2DI_SB_IROGSM21_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Vkljucen
ST2DI_SB_IROGSM21_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Izkljucen
ST2DI_SB_IROGSM21_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Vkljucen
ST2DI_SB_IROGSM21_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Izpad
ST2DI_SB_IROGSM21_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Vkljucen
ST2DI_SB_IROGSM21_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Izpad
ST2DI_SB_IROGSM21_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Vkljucen
ST2DI_SB_IROGSM21_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Izpad
ST2DI_SB_IROGSM21_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Vkljucen
ST2DI_SB_IROGSM21_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_SkupnaNapaka
ST2DI_SB_IROGSM22_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Izkljucen
ST2DI_SB_IROGSM22_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Vkljucen
ST2DI_SB_IROGSM22_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Izkljucen
ST2DI_SB_IROGSM22_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Vkljucen
ST2DI_SB_IROGSM22_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Izkljucen
ST2DI_SB_IROGSM22_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Vkljucen
ST2DI_SB_IROGSM22_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Izpad
ST2DI_SB_IROGSM22_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Vkljucen
ST2DI_SB_IROGSM22_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Izpad
ST2DI_SB_IROGSM22_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Vkljucen
ST2DI_SB_IROGSM22_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Izpad
ST2DI_SB_IROGSM22_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Vkljucen
ST2DI_SB_IROGSM22_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_SkupnaNapaka
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AA_Izolacija_NOT_OK
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AB_Izolacija_NOT_OK
ST2ErrComNSX1 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[1]
ST2ErrComNSX2 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[2]
ST2ErrComNSX3 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[3]
ST2ErrComNSX4 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[4]
ST2ErrComNSX5 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[5]
ST2ErrComNSX6 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[6]
ST2ErrComPMM1 | DIGITAL | IOD_ST2 | ST2:.ErrComPMM[1]
ST2ErrComPort2 | DIGITAL | IOD_ST2 | ST2:.ErrComPort2
ST2ErrorComPMM1Error | DIGITAL | IOD_ST2 | ST2:.ErrorComPMM[1].Error
ST2ErrorComPMM1Status | INT | IOD_ST2 | ST2:.ErrorComPMM[1].Status
ST2HIA1_vlaga_s | INT | IOD_ST2 | ST2:.HIA1_vlaga_s
ST2HIA2_vlaga_s | INT | IOD_ST2 | ST2:.HIA2_vlaga_s
ST2HIA3_vlaga_s | INT | IOD_ST2 | ST2:.HIA3_vlaga_s
ST2HIA4_vlaga_s | INT | IOD_ST2 | ST2:.HIA4_vlaga_s
ST2HIA5_vlaga_s | INT | IOD_ST2 | ST2:.HIA5_vlaga_s
ST2HIA6_vlaga_s | INT | IOD_ST2 | ST2:.HIA6_vlaga_s
ST2HIA7_vlaga_s | INT | IOD_ST2 | ST2:.HIA7_vlaga_s
ST2HIA8_vlaga_s | INT | IOD_ST2 | ST2:.HIA8_vlaga_s
ST2iPMM_VirA_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok1
ST2iPMM_VirA_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok10
ST2iPMM_VirA_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok11
ST2iPMM_VirA_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok12
ST2iPMM_VirA_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok13
ST2iPMM_VirA_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok14
ST2iPMM_VirA_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok15
ST2iPMM_VirA_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok16
ST2iPMM_VirA_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok17
ST2iPMM_VirA_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok18
ST2iPMM_VirA_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok19
ST2iPMM_VirA_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok2
ST2iPMM_VirA_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok20
ST2iPMM_VirA_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok21
ST2iPMM_VirA_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok22
ST2iPMM_VirA_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok23
ST2iPMM_VirA_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok24
ST2iPMM_VirA_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok25
ST2iPMM_VirA_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok26
ST2iPMM_VirA_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok27
ST2iPMM_VirA_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok28
ST2iPMM_VirA_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok29
ST2iPMM_VirA_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok3
ST2iPMM_VirA_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok30
ST2iPMM_VirA_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok31
ST2iPMM_VirA_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok32
ST2iPMM_VirA_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok33
ST2iPMM_VirA_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok34
ST2iPMM_VirA_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok35
ST2iPMM_VirA_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok36
ST2iPMM_VirA_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok37
ST2iPMM_VirA_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok38
ST2iPMM_VirA_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok39
ST2iPMM_VirA_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok4
ST2iPMM_VirA_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok40
ST2iPMM_VirA_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok41
ST2iPMM_VirA_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok42
ST2iPMM_VirA_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok43
ST2iPMM_VirA_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok44
ST2iPMM_VirA_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok5
ST2iPMM_VirA_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok6
ST2iPMM_VirA_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok7
ST2iPMM_VirA_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok8
ST2iPMM_VirA_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok9
ST2iPMM_VirB_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok1
ST2iPMM_VirB_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok10
ST2iPMM_VirB_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok11
ST2iPMM_VirB_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok12
ST2iPMM_VirB_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok13
ST2iPMM_VirB_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok14
ST2iPMM_VirB_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok15
ST2iPMM_VirB_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok16
ST2iPMM_VirB_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok17
ST2iPMM_VirB_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok18
ST2iPMM_VirB_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok19
ST2iPMM_VirB_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok2
ST2iPMM_VirB_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok20
ST2iPMM_VirB_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok21
ST2iPMM_VirB_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok22
ST2iPMM_VirB_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok23
ST2iPMM_VirB_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok24
ST2iPMM_VirB_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok25
ST2iPMM_VirB_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok26
ST2iPMM_VirB_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok27
ST2iPMM_VirB_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok28
ST2iPMM_VirB_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok29
ST2iPMM_VirB_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok3
ST2iPMM_VirB_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok30
ST2iPMM_VirB_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok31
ST2iPMM_VirB_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok32
ST2iPMM_VirB_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok33
ST2iPMM_VirB_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok34
ST2iPMM_VirB_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok35
ST2iPMM_VirB_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok36
ST2iPMM_VirB_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok37
ST2iPMM_VirB_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok38
ST2iPMM_VirB_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok39
ST2iPMM_VirB_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok4
ST2iPMM_VirB_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok40
ST2iPMM_VirB_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok41
ST2iPMM_VirB_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok42
ST2iPMM_VirB_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok43
ST2iPMM_VirB_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok44
ST2iPMM_VirB_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok5
ST2iPMM_VirB_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok6
ST2iPMM_VirB_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok7
ST2iPMM_VirB_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok8
ST2iPMM_VirB_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok9
ST2kom_nast_cas_izpada | STRING | IOD_ST2 | ST2:.kom_nast_cas_izpada
ST2napaka_kom_panel | DIGITAL | IOD_ST2 | ST2:.napaka_kom_panel
ST2napaka_kom_scada | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada
ST2napaka_kom_scada2 | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada2
ST2NapakaSenzorSkupno | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorSkupno
ST2NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA1
ST2NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA2
ST2NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA3
ST2NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA4
ST2NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA5
ST2NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA6
ST2NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA7
ST2NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA8
ST2NapakaTSTempTIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA1
ST2NapakaTSTempTIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA2
ST2NapakaTSTempTIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA3
ST2NapakaTSTempTIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA4
ST2NapakaTSTempTIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA5
ST2NapakaTSTempTIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA6
ST2NapakaTSTempTIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA7
ST2NapakaTSTempTIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA8
ST2NSX1ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveEnergy_kWh
ST2NSX1ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveNegativeEnergy_kWh
ST2NSX1ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActivePositiveEnergy_kWh
ST2NSX1ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerDemand_kW
ST2NSX1ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL1_kW
ST2NSX1ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL2_kW
ST2NSX1ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL3_kW
ST2NSX1ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerMaxDemand_kW
ST2NSX1ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerTotal_kW
ST2NSX1ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[1].ApparentEnergy_kVAh
ST2NSX1ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerDemand_kVA
ST2NSX1ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerMaxDemand_kVA
ST2NSX1ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL1_kVA
ST2NSX1ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL2_kVA
ST2NSX1ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL3_kVA
ST2NSX1ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerTotal_kVA
ST2NSX1CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL1
ST2NSX1CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL2
ST2NSX1CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL3
ST2NSX1CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].CosFTotal
ST2NSX1CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulNegativeActiveEnergy_kWh
ST2NSX1CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulPositiveActiveEnergy_kWh
ST2NSX1CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentAvgI1I2I3_A
ST2NSX1CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL1_A
ST2NSX1CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL2_A
ST2NSX1CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL3_A
ST2NSX1CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL1_A
ST2NSX1CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL2_A
ST2NSX1CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL3_A
ST2NSX1CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxN_A
ST2NSX1CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandN_A
ST2NSX1CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL1_A
ST2NSX1CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL2_A
ST2NSX1CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL3_A
ST2NSX1CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentN_A
ST2NSX1CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI1_P
ST2NSX1CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI2_P
ST2NSX1CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI3_P
ST2NSX1CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbN_P
ST2NSX1DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].DelovnaEnergija_TEMP
ST2NSX1DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL1_kVAr
ST2NSX1DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL2_kVAr
ST2NSX1DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL3_kVAr
ST2NSX1DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerTotal_kVAr
ST2NSX1Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].Frequency_Hz
ST2NSX1FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL1_kVAr
ST2NSX1FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL2_kVAr
ST2NSX1FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL3_kVAr
ST2NSX1FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerTotal_kVAr
ST2NSX1MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL1_kW
ST2NSX1MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL2_kW
ST2NSX1MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL3_kW
ST2NSX1MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerTotal_kW
ST2NSX1MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL1_kVA
ST2NSX1MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL2_kVA
ST2NSX1MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL3_kVA
ST2NSX1MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerTotal_kVA
ST2NSX1MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL1
ST2NSX1MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL2
ST2NSX1MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL3
ST2NSX1MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFTotal
ST2NSX1MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentAvgI1I2I3_A
ST2NSX1MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL1_A
ST2NSX1MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL2_A
ST2NSX1MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL3_A
ST2NSX1MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentMaxL1L2L3N_A
ST2NSX1MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentN_A
ST2NSX1MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL1_kVAr
ST2NSX1MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL2_kVAr
ST2NSX1MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL3_kVAr
ST2NSX1MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerTotal_kVAr
ST2NSX1MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MAX_Frequency_Hz
ST2NSX1MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL1_kVAr
ST2NSX1MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL2_kVAr
ST2NSX1MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL3_kVAr
ST2NSX1MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerTotal_kVAr
ST2NSX1MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL1
ST2NSX1MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL2
ST2NSX1MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL3
ST2NSX1MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorTotal
ST2NSX1MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL1_kVAr
ST2NSX1MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL2_kVAr
ST2NSX1MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL3_kVAr
ST2NSX1MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerTotal_kVAr
ST2NSX1MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI1_P
ST2NSX1MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI2_P
ST2NSX1MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI3_P
ST2NSX1MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV12_P
ST2NSX1MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV1N_P
ST2NSX1MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV23_P
ST2NSX1MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV2N_P
ST2NSX1MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV31_P
ST2NSX1MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV3N_P
ST2NSX1MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToN_V
ST2NSX1MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToPh_V
ST2NSX1MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV12_P
ST2NSX1MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV1N_P
ST2NSX1MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV23_P
ST2NSX1MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV2N_P
ST2NSX1MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV31_P
ST2NSX1MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV3N_P
ST2NSX1MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV12_V
ST2NSX1MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV1N_V
ST2NSX1MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV23_V
ST2NSX1MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV2N_V
ST2NSX1MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV31_V
ST2NSX1MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV3N_V
ST2NSX1MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL1_kW
ST2NSX1MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL2_kW
ST2NSX1MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL3_kW
ST2NSX1MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerTotal_kW
ST2NSX1MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL1_kVA
ST2NSX1MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL2_kVA
ST2NSX1MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL3_kVA
ST2NSX1MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerTotal_kVA
ST2NSX1MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL1
ST2NSX1MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL2
ST2NSX1MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL3
ST2NSX1MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFTotal
ST2NSX1MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentAvgI1I2I3_A
ST2NSX1MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL1_A
ST2NSX1MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL2_A
ST2NSX1MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL3_A
ST2NSX1MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentMaxL1L2L3N_A
ST2NSX1MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentN_A
ST2NSX1MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL1_kVAr
ST2NSX1MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL2_kVAr
ST2NSX1MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL3_kVAr
ST2NSX1MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerTotal_kVAr
ST2NSX1MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MIN_Frequency_Hz
ST2NSX1MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL1_kVAr
ST2NSX1MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL2_kVAr
ST2NSX1MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL3_kVAr
ST2NSX1MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerTotal_kVAr
ST2NSX1MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL1
ST2NSX1MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL2
ST2NSX1MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL3
ST2NSX1MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorTotal
ST2NSX1MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL1_kVAr
ST2NSX1MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL2_kVAr
ST2NSX1MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL3_kVAr
ST2NSX1MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerTotal_kVAr
ST2NSX1MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI1_P
ST2NSX1MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI2_P
ST2NSX1MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI3_P
ST2NSX1MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV12_P
ST2NSX1MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV1N_P
ST2NSX1MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV23_P
ST2NSX1MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV2N_P
ST2NSX1MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV31_P
ST2NSX1MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV3N_P
ST2NSX1MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToN_V
ST2NSX1MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToPh_V
ST2NSX1MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV12_P
ST2NSX1MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV1N_P
ST2NSX1MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV23_P
ST2NSX1MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV2N_P
ST2NSX1MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV31_P
ST2NSX1MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV3N_P
ST2NSX1MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV12_V
ST2NSX1MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV1N_V
ST2NSX1MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV23_V
ST2NSX1MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV2N_V
ST2NSX1MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV31_V
ST2NSX1MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV3N_V
ST2NSX1PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL1
ST2NSX1PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL2
ST2NSX1PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL3
ST2NSX1PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorTotal
ST2NSX1RazEner_D | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D
ST2NSX1RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_SCADA
ST2NSX1RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_TEMP
ST2NSX1RazEner_M | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M
ST2NSX1RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_SCADA
ST2NSX1RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_TEMP
ST2NSX1RazEner_T | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T
ST2NSX1RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_SCADA
ST2NSX1RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_TEMP
ST2NSX1ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveEnergy_kVArh
ST2NSX1ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveNegativeEnergy_kVArh
ST2NSX1ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePositiveEnergy_kVArh
ST2NSX1ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerDemand_kVAr
ST2NSX1ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL1_kVAr
ST2NSX1ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL2_kVAr
ST2NSX1ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL3_kVAr
ST2NSX1ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerMaxDemand_kVAr
ST2NSX1ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerTotal_kVAr
ST2NSX1ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMAX
ST2NSX1ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMIN
ST2NSX1StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[1].StatusSwitch
ST2NSX1THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI1_P
ST2NSX1THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI2_P
ST2NSX1THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI3_P
ST2NSX1THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV12_P
ST2NSX1THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV1N_P
ST2NSX1THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV23_P
ST2NSX1THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV2N_P
ST2NSX1THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV31_P
ST2NSX1THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV3N_P
ST2NSX1VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToN_V
ST2NSX1VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToPh_V
ST2NSX1VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV12_P
ST2NSX1VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV1N_P
ST2NSX1VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV23_P
ST2NSX1VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV2N_P
ST2NSX1VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV31_P
ST2NSX1VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV3N_P
ST2NSX1VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV12_V
ST2NSX1VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV1N_V
ST2NSX1VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV23_V
ST2NSX1VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV2N_V
ST2NSX1VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV31_V
ST2NSX1VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV3N_V
ST2NSX2ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveEnergy_kWh
ST2NSX2ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveNegativeEnergy_kWh
ST2NSX2ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActivePositiveEnergy_kWh
ST2NSX2ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerDemand_kW
ST2NSX2ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL1_kW
ST2NSX2ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL2_kW
ST2NSX2ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL3_kW
ST2NSX2ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerMaxDemand_kW
ST2NSX2ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerTotal_kW
ST2NSX2ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[2].ApparentEnergy_kVAh
ST2NSX2ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerDemand_kVA
ST2NSX2ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerMaxDemand_kVA
ST2NSX2ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL1_kVA
ST2NSX2ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL2_kVA
ST2NSX2ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL3_kVA
ST2NSX2ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerTotal_kVA
ST2NSX2CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL1
ST2NSX2CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL2
ST2NSX2CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL3
ST2NSX2CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].CosFTotal
ST2NSX2CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulNegativeActiveEnergy_kWh
ST2NSX2CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulPositiveActiveEnergy_kWh
ST2NSX2CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentAvgI1I2I3_A
ST2NSX2CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL1_A
ST2NSX2CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL2_A
ST2NSX2CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL3_A
ST2NSX2CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL1_A
ST2NSX2CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL2_A
ST2NSX2CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL3_A
ST2NSX2CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxN_A
ST2NSX2CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandN_A
ST2NSX2CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL1_A
ST2NSX2CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL2_A
ST2NSX2CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL3_A
ST2NSX2CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentN_A
ST2NSX2CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI1_P
ST2NSX2CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI2_P
ST2NSX2CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI3_P
ST2NSX2CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbN_P
ST2NSX2DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].DelovnaEnergija_TEMP
ST2NSX2DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL1_kVAr
ST2NSX2DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL2_kVAr
ST2NSX2DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL3_kVAr
ST2NSX2DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerTotal_kVAr
ST2NSX2Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].Frequency_Hz
ST2NSX2FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL1_kVAr
ST2NSX2FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL2_kVAr
ST2NSX2FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL3_kVAr
ST2NSX2FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerTotal_kVAr
ST2NSX2MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL1_kW
ST2NSX2MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL2_kW
ST2NSX2MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL3_kW
ST2NSX2MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerTotal_kW
ST2NSX2MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL1_kVA
ST2NSX2MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL2_kVA
ST2NSX2MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL3_kVA
ST2NSX2MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerTotal_kVA
ST2NSX2MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL1
ST2NSX2MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL2
ST2NSX2MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL3
ST2NSX2MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFTotal
ST2NSX2MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentAvgI1I2I3_A
ST2NSX2MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL1_A
ST2NSX2MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL2_A
ST2NSX2MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL3_A
ST2NSX2MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentMaxL1L2L3N_A
ST2NSX2MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentN_A
ST2NSX2MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL1_kVAr
ST2NSX2MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL2_kVAr
ST2NSX2MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL3_kVAr
ST2NSX2MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerTotal_kVAr
ST2NSX2MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MAX_Frequency_Hz
ST2NSX2MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL1_kVAr
ST2NSX2MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL2_kVAr
ST2NSX2MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL3_kVAr
ST2NSX2MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerTotal_kVAr
ST2NSX2MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL1
ST2NSX2MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL2
ST2NSX2MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL3
ST2NSX2MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorTotal
ST2NSX2MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL1_kVAr
ST2NSX2MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL2_kVAr
ST2NSX2MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL3_kVAr
ST2NSX2MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerTotal_kVAr
ST2NSX2MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI1_P
ST2NSX2MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI2_P
ST2NSX2MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI3_P
ST2NSX2MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV12_P
ST2NSX2MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV1N_P
ST2NSX2MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV23_P
ST2NSX2MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV2N_P
ST2NSX2MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV31_P
ST2NSX2MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV3N_P
ST2NSX2MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToN_V
ST2NSX2MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToPh_V
ST2NSX2MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV12_P
ST2NSX2MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV1N_P
ST2NSX2MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV23_P
ST2NSX2MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV2N_P
ST2NSX2MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV31_P
ST2NSX2MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV3N_P
ST2NSX2MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV12_V
ST2NSX2MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV1N_V
ST2NSX2MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV23_V
ST2NSX2MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV2N_V
ST2NSX2MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV31_V
ST2NSX2MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV3N_V
ST2NSX2MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL1_kW
ST2NSX2MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL2_kW
ST2NSX2MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL3_kW
ST2NSX2MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerTotal_kW
ST2NSX2MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL1_kVA
ST2NSX2MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL2_kVA
ST2NSX2MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL3_kVA
ST2NSX2MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerTotal_kVA
ST2NSX2MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL1
ST2NSX2MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL2
ST2NSX2MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL3
ST2NSX2MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFTotal
ST2NSX2MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentAvgI1I2I3_A
ST2NSX2MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL1_A
ST2NSX2MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL2_A
ST2NSX2MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL3_A
ST2NSX2MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentMaxL1L2L3N_A
ST2NSX2MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentN_A
ST2NSX2MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL1_kVAr
ST2NSX2MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL2_kVAr
ST2NSX2MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL3_kVAr
ST2NSX2MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerTotal_kVAr
ST2NSX2MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MIN_Frequency_Hz
ST2NSX2MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL1_kVAr
ST2NSX2MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL2_kVAr
ST2NSX2MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL3_kVAr
ST2NSX2MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerTotal_kVAr
ST2NSX2MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL1
ST2NSX2MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL2
ST2NSX2MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL3
ST2NSX2MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorTotal
ST2NSX2MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL1_kVAr
ST2NSX2MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL2_kVAr
ST2NSX2MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL3_kVAr
ST2NSX2MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerTotal_kVAr
ST2NSX2MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI1_P
ST2NSX2MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI2_P
ST2NSX2MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI3_P
ST2NSX2MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV12_P
ST2NSX2MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV1N_P
ST2NSX2MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV23_P
ST2NSX2MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV2N_P
ST2NSX2MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV31_P
ST2NSX2MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV3N_P
ST2NSX2MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToN_V
ST2NSX2MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToPh_V
ST2NSX2MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV12_P
ST2NSX2MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV1N_P
ST2NSX2MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV23_P
ST2NSX2MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV2N_P
ST2NSX2MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV31_P
ST2NSX2MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV3N_P
ST2NSX2MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV12_V
ST2NSX2MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV1N_V
ST2NSX2MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV23_V
ST2NSX2MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV2N_V
ST2NSX2MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV31_V
ST2NSX2MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV3N_V
ST2NSX2PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL1
ST2NSX2PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL2
ST2NSX2PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL3
ST2NSX2PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorTotal
ST2NSX2RazEner_D | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D
ST2NSX2RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_SCADA
ST2NSX2RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_TEMP
ST2NSX2RazEner_M | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M
ST2NSX2RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_SCADA
ST2NSX2RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_TEMP
ST2NSX2RazEner_T | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T
ST2NSX2RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_SCADA
ST2NSX2RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_TEMP
ST2NSX2ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveEnergy_kVArh
ST2NSX2ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveNegativeEnergy_kVArh
ST2NSX2ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePositiveEnergy_kVArh
ST2NSX2ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerDemand_kVAr
ST2NSX2ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL1_kVAr
ST2NSX2ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL2_kVAr
ST2NSX2ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL3_kVAr
ST2NSX2ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerMaxDemand_kVAr
ST2NSX2ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerTotal_kVAr
ST2NSX2ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMAX
ST2NSX2ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMIN
ST2NSX2StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[2].StatusSwitch
ST2NSX2THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI1_P
ST2NSX2THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI2_P
ST2NSX2THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI3_P
ST2NSX2THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV12_P
ST2NSX2THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV1N_P
ST2NSX2THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV23_P
ST2NSX2THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV2N_P
ST2NSX2THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV31_P
ST2NSX2THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV3N_P
ST2NSX2VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToN_V
ST2NSX2VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToPh_V
ST2NSX2VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV12_P
ST2NSX2VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV1N_P
ST2NSX2VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV23_P
ST2NSX2VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV2N_P
ST2NSX2VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV31_P
ST2NSX2VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV3N_P
ST2NSX2VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV12_V
ST2NSX2VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV1N_V
ST2NSX2VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV23_V
ST2NSX2VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV2N_V
ST2NSX2VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV31_V
ST2NSX2VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV3N_V
ST2NSX3ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveEnergy_kWh
ST2NSX3ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveNegativeEnergy_kWh
ST2NSX3ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActivePositiveEnergy_kWh
ST2NSX3ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerDemand_kW
ST2NSX3ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL1_kW
ST2NSX3ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL2_kW
ST2NSX3ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL3_kW
ST2NSX3ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerMaxDemand_kW
ST2NSX3ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerTotal_kW
ST2NSX3ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[3].ApparentEnergy_kVAh
ST2NSX3ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerDemand_kVA
ST2NSX3ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerMaxDemand_kVA
ST2NSX3ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL1_kVA
ST2NSX3ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL2_kVA
ST2NSX3ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL3_kVA
ST2NSX3ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerTotal_kVA
ST2NSX3CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL1
ST2NSX3CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL2
ST2NSX3CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL3
ST2NSX3CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].CosFTotal
ST2NSX3CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulNegativeActiveEnergy_kWh
ST2NSX3CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulPositiveActiveEnergy_kWh
ST2NSX3CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentAvgI1I2I3_A
ST2NSX3CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL1_A
ST2NSX3CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL2_A
ST2NSX3CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL3_A
ST2NSX3CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL1_A
ST2NSX3CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL2_A
ST2NSX3CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL3_A
ST2NSX3CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxN_A
ST2NSX3CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandN_A
ST2NSX3CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL1_A
ST2NSX3CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL2_A
ST2NSX3CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL3_A
ST2NSX3CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentN_A
ST2NSX3CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI1_P
ST2NSX3CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI2_P
ST2NSX3CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI3_P
ST2NSX3CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbN_P
ST2NSX3DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].DelovnaEnergija_TEMP
ST2NSX3DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL1_kVAr
ST2NSX3DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL2_kVAr
ST2NSX3DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL3_kVAr
ST2NSX3DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerTotal_kVAr
ST2NSX3Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].Frequency_Hz
ST2NSX3FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL1_kVAr
ST2NSX3FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL2_kVAr
ST2NSX3FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL3_kVAr
ST2NSX3FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerTotal_kVAr
ST2NSX3MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL1_kW
ST2NSX3MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL2_kW
ST2NSX3MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL3_kW
ST2NSX3MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerTotal_kW
ST2NSX3MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL1_kVA
ST2NSX3MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL2_kVA
ST2NSX3MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL3_kVA
ST2NSX3MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerTotal_kVA
ST2NSX3MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL1
ST2NSX3MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL2
ST2NSX3MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL3
ST2NSX3MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFTotal
ST2NSX3MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentAvgI1I2I3_A
ST2NSX3MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL1_A
ST2NSX3MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL2_A
ST2NSX3MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL3_A
ST2NSX3MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentMaxL1L2L3N_A
ST2NSX3MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentN_A
ST2NSX3MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL1_kVAr
ST2NSX3MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL2_kVAr
ST2NSX3MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL3_kVAr
ST2NSX3MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerTotal_kVAr
ST2NSX3MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MAX_Frequency_Hz
ST2NSX3MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL1_kVAr
ST2NSX3MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL2_kVAr
ST2NSX3MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL3_kVAr
ST2NSX3MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerTotal_kVAr
ST2NSX3MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL1
ST2NSX3MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL2
ST2NSX3MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL3
ST2NSX3MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorTotal
ST2NSX3MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL1_kVAr
ST2NSX3MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL2_kVAr
ST2NSX3MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL3_kVAr
ST2NSX3MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerTotal_kVAr
ST2NSX3MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI1_P
ST2NSX3MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI2_P
ST2NSX3MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI3_P
ST2NSX3MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV12_P
ST2NSX3MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV1N_P
ST2NSX3MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV23_P
ST2NSX3MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV2N_P
ST2NSX3MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV31_P
ST2NSX3MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV3N_P
ST2NSX3MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToN_V
ST2NSX3MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToPh_V
ST2NSX3MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV12_P
ST2NSX3MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV1N_P
ST2NSX3MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV23_P
ST2NSX3MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV2N_P
ST2NSX3MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV31_P
ST2NSX3MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV3N_P
ST2NSX3MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV12_V
ST2NSX3MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV1N_V
ST2NSX3MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV23_V
ST2NSX3MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV2N_V
ST2NSX3MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV31_V
ST2NSX3MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV3N_V
ST2NSX3MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL1_kW
ST2NSX3MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL2_kW
ST2NSX3MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL3_kW
ST2NSX3MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerTotal_kW
ST2NSX3MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL1_kVA
ST2NSX3MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL2_kVA
ST2NSX3MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL3_kVA
ST2NSX3MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerTotal_kVA
ST2NSX3MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL1
ST2NSX3MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL2
ST2NSX3MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL3
ST2NSX3MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFTotal
ST2NSX3MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentAvgI1I2I3_A
ST2NSX3MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL1_A
ST2NSX3MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL2_A
ST2NSX3MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL3_A
ST2NSX3MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentMaxL1L2L3N_A
ST2NSX3MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentN_A
ST2NSX3MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL1_kVAr
ST2NSX3MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL2_kVAr
ST2NSX3MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL3_kVAr
ST2NSX3MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerTotal_kVAr
ST2NSX3MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MIN_Frequency_Hz
ST2NSX3MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL1_kVAr
ST2NSX3MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL2_kVAr
ST2NSX3MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL3_kVAr
ST2NSX3MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerTotal_kVAr
ST2NSX3MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL1
ST2NSX3MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL2
ST2NSX3MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL3
ST2NSX3MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorTotal
ST2NSX3MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL1_kVAr
ST2NSX3MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL2_kVAr
ST2NSX3MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL3_kVAr
ST2NSX3MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerTotal_kVAr
ST2NSX3MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI1_P
ST2NSX3MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI2_P
ST2NSX3MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI3_P
ST2NSX3MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV12_P
ST2NSX3MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV1N_P
ST2NSX3MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV23_P
ST2NSX3MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV2N_P
ST2NSX3MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV31_P
ST2NSX3MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV3N_P
ST2NSX3MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToN_V
ST2NSX3MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToPh_V
ST2NSX3MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV12_P
ST2NSX3MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV1N_P
ST2NSX3MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV23_P
ST2NSX3MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV2N_P
ST2NSX3MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV31_P
ST2NSX3MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV3N_P
ST2NSX3MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV12_V
ST2NSX3MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV1N_V
ST2NSX3MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV23_V
ST2NSX3MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV2N_V
ST2NSX3MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV31_V
ST2NSX3MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV3N_V
ST2NSX3PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL1
ST2NSX3PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL2
ST2NSX3PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL3
ST2NSX3PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorTotal
ST2NSX3RazEner_D | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D
ST2NSX3RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_SCADA
ST2NSX3RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_TEMP
ST2NSX3RazEner_M | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M
ST2NSX3RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_SCADA
ST2NSX3RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_TEMP
ST2NSX3RazEner_T | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T
ST2NSX3RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_SCADA
ST2NSX3RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_TEMP
ST2NSX3ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveEnergy_kVArh
ST2NSX3ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveNegativeEnergy_kVArh
ST2NSX3ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePositiveEnergy_kVArh
ST2NSX3ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerDemand_kVAr
ST2NSX3ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL1_kVAr
ST2NSX3ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL2_kVAr
ST2NSX3ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL3_kVAr
ST2NSX3ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerMaxDemand_kVAr
ST2NSX3ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerTotal_kVAr
ST2NSX3ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMAX
ST2NSX3ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMIN
ST2NSX3StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[3].StatusSwitch
ST2NSX3THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI1_P
ST2NSX3THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI2_P
ST2NSX3THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI3_P
ST2NSX3THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV12_P
ST2NSX3THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV1N_P
ST2NSX3THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV23_P
ST2NSX3THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV2N_P
ST2NSX3THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV31_P
ST2NSX3THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV3N_P
ST2NSX3VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToN_V
ST2NSX3VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToPh_V
ST2NSX3VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV12_P
ST2NSX3VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV1N_P
ST2NSX3VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV23_P
ST2NSX3VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV2N_P
ST2NSX3VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV31_P
ST2NSX3VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV3N_P
ST2NSX3VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV12_V
ST2NSX3VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV1N_V
ST2NSX3VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV23_V
ST2NSX3VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV2N_V
ST2NSX3VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV31_V
ST2NSX3VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV3N_V
ST2NSX4ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveEnergy_kWh
ST2NSX4ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveNegativeEnergy_kWh
ST2NSX4ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActivePositiveEnergy_kWh
ST2NSX4ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerDemand_kW
ST2NSX4ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL1_kW
ST2NSX4ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL2_kW
ST2NSX4ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL3_kW
ST2NSX4ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerMaxDemand_kW
ST2NSX4ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerTotal_kW
ST2NSX4ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[4].ApparentEnergy_kVAh
ST2NSX4ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerDemand_kVA
ST2NSX4ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerMaxDemand_kVA
ST2NSX4ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL1_kVA
ST2NSX4ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL2_kVA
ST2NSX4ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL3_kVA
ST2NSX4ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerTotal_kVA
ST2NSX4CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL1
ST2NSX4CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL2
ST2NSX4CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL3
ST2NSX4CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].CosFTotal
ST2NSX4CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulNegativeActiveEnergy_kWh
ST2NSX4CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulPositiveActiveEnergy_kWh
ST2NSX4CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentAvgI1I2I3_A
ST2NSX4CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL1_A
ST2NSX4CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL2_A
ST2NSX4CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL3_A
ST2NSX4CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL1_A
ST2NSX4CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL2_A
ST2NSX4CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL3_A
ST2NSX4CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxN_A
ST2NSX4CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandN_A
ST2NSX4CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL1_A
ST2NSX4CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL2_A
ST2NSX4CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL3_A
ST2NSX4CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentN_A
ST2NSX4CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI1_P
ST2NSX4CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI2_P
ST2NSX4CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI3_P
ST2NSX4CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbN_P
ST2NSX4DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].DelovnaEnergija_TEMP
ST2NSX4DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL1_kVAr
ST2NSX4DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL2_kVAr
ST2NSX4DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL3_kVAr
ST2NSX4DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerTotal_kVAr
ST2NSX4Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].Frequency_Hz
ST2NSX4FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL1_kVAr
ST2NSX4FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL2_kVAr
ST2NSX4FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL3_kVAr
ST2NSX4FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerTotal_kVAr
ST2NSX4MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL1_kW
ST2NSX4MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL2_kW
ST2NSX4MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL3_kW
ST2NSX4MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerTotal_kW
ST2NSX4MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL1_kVA
ST2NSX4MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL2_kVA
ST2NSX4MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL3_kVA
ST2NSX4MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerTotal_kVA
ST2NSX4MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL1
ST2NSX4MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL2
ST2NSX4MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL3
ST2NSX4MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFTotal
ST2NSX4MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentAvgI1I2I3_A
ST2NSX4MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL1_A
ST2NSX4MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL2_A
ST2NSX4MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL3_A
ST2NSX4MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentMaxL1L2L3N_A
ST2NSX4MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentN_A
ST2NSX4MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL1_kVAr
ST2NSX4MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL2_kVAr
ST2NSX4MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL3_kVAr
ST2NSX4MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerTotal_kVAr
ST2NSX4MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MAX_Frequency_Hz
ST2NSX4MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL1_kVAr
ST2NSX4MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL2_kVAr
ST2NSX4MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL3_kVAr
ST2NSX4MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerTotal_kVAr
ST2NSX4MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL1
ST2NSX4MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL2
ST2NSX4MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL3
ST2NSX4MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorTotal
ST2NSX4MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL1_kVAr
ST2NSX4MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL2_kVAr
ST2NSX4MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL3_kVAr
ST2NSX4MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerTotal_kVAr
ST2NSX4MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI1_P
ST2NSX4MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI2_P
ST2NSX4MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI3_P
ST2NSX4MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV12_P
ST2NSX4MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV1N_P
ST2NSX4MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV23_P
ST2NSX4MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV2N_P
ST2NSX4MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV31_P
ST2NSX4MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV3N_P
ST2NSX4MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToN_V
ST2NSX4MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToPh_V
ST2NSX4MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV12_P
ST2NSX4MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV1N_P
ST2NSX4MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV23_P
ST2NSX4MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV2N_P
ST2NSX4MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV31_P
ST2NSX4MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV3N_P
ST2NSX4MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV12_V
ST2NSX4MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV1N_V
ST2NSX4MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV23_V
ST2NSX4MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV2N_V
ST2NSX4MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV31_V
ST2NSX4MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV3N_V
ST2NSX4MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL1_kW
ST2NSX4MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL2_kW
ST2NSX4MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL3_kW
ST2NSX4MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerTotal_kW
ST2NSX4MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL1_kVA
ST2NSX4MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL2_kVA
ST2NSX4MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL3_kVA
ST2NSX4MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerTotal_kVA
ST2NSX4MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL1
ST2NSX4MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL2
ST2NSX4MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL3
ST2NSX4MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFTotal
ST2NSX4MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentAvgI1I2I3_A
ST2NSX4MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL1_A
ST2NSX4MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL2_A
ST2NSX4MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL3_A
ST2NSX4MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentMaxL1L2L3N_A
ST2NSX4MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentN_A
ST2NSX4MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL1_kVAr
ST2NSX4MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL2_kVAr
ST2NSX4MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL3_kVAr
ST2NSX4MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerTotal_kVAr
ST2NSX4MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MIN_Frequency_Hz
ST2NSX4MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL1_kVAr
ST2NSX4MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL2_kVAr
ST2NSX4MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL3_kVAr
ST2NSX4MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerTotal_kVAr
ST2NSX4MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL1
ST2NSX4MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL2
ST2NSX4MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL3
ST2NSX4MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorTotal
ST2NSX4MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL1_kVAr
ST2NSX4MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL2_kVAr
ST2NSX4MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL3_kVAr
ST2NSX4MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerTotal_kVAr
ST2NSX4MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI1_P
ST2NSX4MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI2_P
ST2NSX4MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI3_P
ST2NSX4MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV12_P
ST2NSX4MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV1N_P
ST2NSX4MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV23_P
ST2NSX4MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV2N_P
ST2NSX4MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV31_P
ST2NSX4MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV3N_P
ST2NSX4MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToN_V
ST2NSX4MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToPh_V
ST2NSX4MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV12_P
ST2NSX4MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV1N_P
ST2NSX4MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV23_P
ST2NSX4MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV2N_P
ST2NSX4MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV31_P
ST2NSX4MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV3N_P
ST2NSX4MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV12_V
ST2NSX4MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV1N_V
ST2NSX4MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV23_V
ST2NSX4MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV2N_V
ST2NSX4MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV31_V
ST2NSX4MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV3N_V
ST2NSX4PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL1
ST2NSX4PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL2
ST2NSX4PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL3
ST2NSX4PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorTotal
ST2NSX4RazEner_D | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D
ST2NSX4RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_SCADA
ST2NSX4RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_TEMP
ST2NSX4RazEner_M | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M
ST2NSX4RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_SCADA
ST2NSX4RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_TEMP
ST2NSX4RazEner_T | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T
ST2NSX4RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_SCADA
ST2NSX4RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_TEMP
ST2NSX4ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveEnergy_kVArh
ST2NSX4ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveNegativeEnergy_kVArh
ST2NSX4ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePositiveEnergy_kVArh
ST2NSX4ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerDemand_kVAr
ST2NSX4ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL1_kVAr
ST2NSX4ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL2_kVAr
ST2NSX4ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL3_kVAr
ST2NSX4ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerMaxDemand_kVAr
ST2NSX4ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerTotal_kVAr
ST2NSX4ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMAX
ST2NSX4ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMIN
ST2NSX4StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[4].StatusSwitch
ST2NSX4THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI1_P
ST2NSX4THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI2_P
ST2NSX4THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI3_P
ST2NSX4THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV12_P
ST2NSX4THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV1N_P
ST2NSX4THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV23_P
ST2NSX4THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV2N_P
ST2NSX4THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV31_P
ST2NSX4THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV3N_P
ST2NSX4VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToN_V
ST2NSX4VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToPh_V
ST2NSX4VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV12_P
ST2NSX4VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV1N_P
ST2NSX4VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV23_P
ST2NSX4VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV2N_P
ST2NSX4VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV31_P
ST2NSX4VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV3N_P
ST2NSX4VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV12_V
ST2NSX4VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV1N_V
ST2NSX4VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV23_V
ST2NSX4VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV2N_V
ST2NSX4VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV31_V
ST2NSX4VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV3N_V
ST2NSX5ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveEnergy_kWh
ST2NSX5ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveNegativeEnergy_kWh
ST2NSX5ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActivePositiveEnergy_kWh
ST2NSX5ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerDemand_kW
ST2NSX5ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL1_kW
ST2NSX5ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL2_kW
ST2NSX5ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL3_kW
ST2NSX5ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerMaxDemand_kW
ST2NSX5ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerTotal_kW
ST2NSX5ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[5].ApparentEnergy_kVAh
ST2NSX5ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerDemand_kVA
ST2NSX5ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerMaxDemand_kVA
ST2NSX5ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL1_kVA
ST2NSX5ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL2_kVA
ST2NSX5ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL3_kVA
ST2NSX5ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerTotal_kVA
ST2NSX5CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL1
ST2NSX5CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL2
ST2NSX5CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL3
ST2NSX5CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].CosFTotal
ST2NSX5CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulNegativeActiveEnergy_kWh
ST2NSX5CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulPositiveActiveEnergy_kWh
ST2NSX5CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentAvgI1I2I3_A
ST2NSX5CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL1_A
ST2NSX5CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL2_A
ST2NSX5CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL3_A
ST2NSX5CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL1_A
ST2NSX5CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL2_A
ST2NSX5CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL3_A
ST2NSX5CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxN_A
ST2NSX5CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandN_A
ST2NSX5CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL1_A
ST2NSX5CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL2_A
ST2NSX5CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL3_A
ST2NSX5CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentN_A
ST2NSX5CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI1_P
ST2NSX5CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI2_P
ST2NSX5CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI3_P
ST2NSX5CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbN_P
ST2NSX5DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].DelovnaEnergija_TEMP
ST2NSX5DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL1_kVAr
ST2NSX5DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL2_kVAr
ST2NSX5DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL3_kVAr
ST2NSX5DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerTotal_kVAr
ST2NSX5Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].Frequency_Hz
ST2NSX5FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL1_kVAr
ST2NSX5FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL2_kVAr
ST2NSX5FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL3_kVAr
ST2NSX5FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerTotal_kVAr
ST2NSX5MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL1_kW
ST2NSX5MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL2_kW
ST2NSX5MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL3_kW
ST2NSX5MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerTotal_kW
ST2NSX5MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL1_kVA
ST2NSX5MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL2_kVA
ST2NSX5MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL3_kVA
ST2NSX5MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerTotal_kVA
ST2NSX5MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL1
ST2NSX5MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL2
ST2NSX5MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL3
ST2NSX5MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFTotal
ST2NSX5MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentAvgI1I2I3_A
ST2NSX5MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL1_A
ST2NSX5MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL2_A
ST2NSX5MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL3_A
ST2NSX5MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentMaxL1L2L3N_A
ST2NSX5MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentN_A
ST2NSX5MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL1_kVAr
ST2NSX5MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL2_kVAr
ST2NSX5MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL3_kVAr
ST2NSX5MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerTotal_kVAr
ST2NSX5MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MAX_Frequency_Hz
ST2NSX5MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL1_kVAr
ST2NSX5MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL2_kVAr
ST2NSX5MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL3_kVAr
ST2NSX5MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerTotal_kVAr
ST2NSX5MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL1
ST2NSX5MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL2
ST2NSX5MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL3
ST2NSX5MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorTotal
ST2NSX5MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL1_kVAr
ST2NSX5MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL2_kVAr
ST2NSX5MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL3_kVAr
ST2NSX5MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerTotal_kVAr
ST2NSX5MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI1_P
ST2NSX5MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI2_P
ST2NSX5MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI3_P
ST2NSX5MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV12_P
ST2NSX5MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV1N_P
ST2NSX5MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV23_P
ST2NSX5MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV2N_P
ST2NSX5MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV31_P
ST2NSX5MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV3N_P
ST2NSX5MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToN_V
ST2NSX5MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToPh_V
ST2NSX5MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV12_P
ST2NSX5MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV1N_P
ST2NSX5MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV23_P
ST2NSX5MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV2N_P
ST2NSX5MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV31_P
ST2NSX5MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV3N_P
ST2NSX5MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV12_V
ST2NSX5MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV1N_V
ST2NSX5MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV23_V
ST2NSX5MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV2N_V
ST2NSX5MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV31_V
ST2NSX5MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV3N_V
ST2NSX5MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL1_kW
ST2NSX5MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL2_kW
ST2NSX5MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL3_kW
ST2NSX5MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerTotal_kW
ST2NSX5MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL1_kVA
ST2NSX5MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL2_kVA
ST2NSX5MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL3_kVA
ST2NSX5MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerTotal_kVA
ST2NSX5MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL1
ST2NSX5MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL2
ST2NSX5MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL3
ST2NSX5MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFTotal
ST2NSX5MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentAvgI1I2I3_A
ST2NSX5MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL1_A
ST2NSX5MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL2_A
ST2NSX5MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL3_A
ST2NSX5MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentMaxL1L2L3N_A
ST2NSX5MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentN_A
ST2NSX5MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL1_kVAr
ST2NSX5MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL2_kVAr
ST2NSX5MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL3_kVAr
ST2NSX5MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerTotal_kVAr
ST2NSX5MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MIN_Frequency_Hz
ST2NSX5MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL1_kVAr
ST2NSX5MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL2_kVAr
ST2NSX5MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL3_kVAr
ST2NSX5MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerTotal_kVAr
ST2NSX5MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL1
ST2NSX5MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL2
ST2NSX5MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL3
ST2NSX5MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorTotal
ST2NSX5MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL1_kVAr
ST2NSX5MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL2_kVAr
ST2NSX5MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL3_kVAr
ST2NSX5MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerTotal_kVAr
ST2NSX5MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI1_P
ST2NSX5MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI2_P
ST2NSX5MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI3_P
ST2NSX5MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV12_P
ST2NSX5MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV1N_P
ST2NSX5MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV23_P
ST2NSX5MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV2N_P
ST2NSX5MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV31_P
ST2NSX5MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV3N_P
ST2NSX5MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToN_V
ST2NSX5MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToPh_V
ST2NSX5MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV12_P
ST2NSX5MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV1N_P
ST2NSX5MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV23_P
ST2NSX5MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV2N_P
ST2NSX5MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV31_P
ST2NSX5MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV3N_P
ST2NSX5MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV12_V
ST2NSX5MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV1N_V
ST2NSX5MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV23_V
ST2NSX5MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV2N_V
ST2NSX5MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV31_V
ST2NSX5MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV3N_V
ST2NSX5PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL1
ST2NSX5PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL2
ST2NSX5PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL3
ST2NSX5PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorTotal
ST2NSX5RazEner_D | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D
ST2NSX5RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_SCADA
ST2NSX5RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_TEMP
ST2NSX5RazEner_M | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M
ST2NSX5RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_SCADA
ST2NSX5RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_TEMP
ST2NSX5RazEner_T | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T
ST2NSX5RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_SCADA
ST2NSX5RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_TEMP
ST2NSX5ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveEnergy_kVArh
ST2NSX5ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveNegativeEnergy_kVArh
ST2NSX5ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePositiveEnergy_kVArh
ST2NSX5ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerDemand_kVAr
ST2NSX5ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL1_kVAr
ST2NSX5ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL2_kVAr
ST2NSX5ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL3_kVAr
ST2NSX5ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerMaxDemand_kVAr
ST2NSX5ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerTotal_kVAr
ST2NSX5ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMAX
ST2NSX5ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMIN
ST2NSX5StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[5].StatusSwitch
ST2NSX5THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI1_P
ST2NSX5THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI2_P
ST2NSX5THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI3_P
ST2NSX5THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV12_P
ST2NSX5THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV1N_P
ST2NSX5THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV23_P
ST2NSX5THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV2N_P
ST2NSX5THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV31_P
ST2NSX5THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV3N_P
ST2NSX5VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToN_V
ST2NSX5VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToPh_V
ST2NSX5VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV12_P
ST2NSX5VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV1N_P
ST2NSX5VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV23_P
ST2NSX5VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV2N_P
ST2NSX5VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV31_P
ST2NSX5VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV3N_P
ST2NSX5VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV12_V
ST2NSX5VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV1N_V
ST2NSX5VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV23_V
ST2NSX5VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV2N_V
ST2NSX5VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV31_V
ST2NSX5VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV3N_V
ST2NSX6ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveEnergy_kWh
ST2NSX6ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveNegativeEnergy_kWh
ST2NSX6ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActivePositiveEnergy_kWh
ST2NSX6ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerDemand_kW
ST2NSX6ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL1_kW
ST2NSX6ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL2_kW
ST2NSX6ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL3_kW
ST2NSX6ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerMaxDemand_kW
ST2NSX6ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerTotal_kW
ST2NSX6ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[6].ApparentEnergy_kVAh
ST2NSX6ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerDemand_kVA
ST2NSX6ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerMaxDemand_kVA
ST2NSX6ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL1_kVA
ST2NSX6ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL2_kVA
ST2NSX6ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL3_kVA
ST2NSX6ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerTotal_kVA
ST2NSX6CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL1
ST2NSX6CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL2
ST2NSX6CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL3
ST2NSX6CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].CosFTotal
ST2NSX6CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulNegativeActiveEnergy_kWh
ST2NSX6CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulPositiveActiveEnergy_kWh
ST2NSX6CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentAvgI1I2I3_A
ST2NSX6CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL1_A
ST2NSX6CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL2_A
ST2NSX6CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL3_A
ST2NSX6CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL1_A
ST2NSX6CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL2_A
ST2NSX6CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL3_A
ST2NSX6CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxN_A
ST2NSX6CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandN_A
ST2NSX6CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL1_A
ST2NSX6CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL2_A
ST2NSX6CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL3_A
ST2NSX6CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentN_A
ST2NSX6CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI1_P
ST2NSX6CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI2_P
ST2NSX6CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI3_P
ST2NSX6CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbN_P
ST2NSX6DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].DelovnaEnergija_TEMP
ST2NSX6DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL1_kVAr
ST2NSX6DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL2_kVAr
ST2NSX6DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL3_kVAr
ST2NSX6DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerTotal_kVAr
ST2NSX6Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].Frequency_Hz
ST2NSX6FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL1_kVAr
ST2NSX6FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL2_kVAr
ST2NSX6FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL3_kVAr
ST2NSX6FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerTotal_kVAr
ST2NSX6MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL1_kW
ST2NSX6MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL2_kW
ST2NSX6MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL3_kW
ST2NSX6MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerTotal_kW
ST2NSX6MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL1_kVA
ST2NSX6MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL2_kVA
ST2NSX6MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL3_kVA
ST2NSX6MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerTotal_kVA
ST2NSX6MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL1
ST2NSX6MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL2
ST2NSX6MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL3
ST2NSX6MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFTotal
ST2NSX6MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentAvgI1I2I3_A
ST2NSX6MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL1_A
ST2NSX6MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL2_A
ST2NSX6MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL3_A
ST2NSX6MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentMaxL1L2L3N_A
ST2NSX6MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentN_A
ST2NSX6MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL1_kVAr
ST2NSX6MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL2_kVAr
ST2NSX6MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL3_kVAr
ST2NSX6MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerTotal_kVAr
ST2NSX6MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MAX_Frequency_Hz
ST2NSX6MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL1_kVAr
ST2NSX6MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL2_kVAr
ST2NSX6MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL3_kVAr
ST2NSX6MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerTotal_kVAr
ST2NSX6MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL1
ST2NSX6MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL2
ST2NSX6MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL3
ST2NSX6MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorTotal
ST2NSX6MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL1_kVAr
ST2NSX6MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL2_kVAr
ST2NSX6MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL3_kVAr
ST2NSX6MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerTotal_kVAr
ST2NSX6MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI1_P
ST2NSX6MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI2_P
ST2NSX6MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI3_P
ST2NSX6MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV12_P
ST2NSX6MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV1N_P
ST2NSX6MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV23_P
ST2NSX6MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV2N_P
ST2NSX6MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV31_P
ST2NSX6MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV3N_P
ST2NSX6MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToN_V
ST2NSX6MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToPh_V
ST2NSX6MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV12_P
ST2NSX6MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV1N_P
ST2NSX6MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV23_P
ST2NSX6MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV2N_P
ST2NSX6MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV31_P
ST2NSX6MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV3N_P
ST2NSX6MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV12_V
ST2NSX6MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV1N_V
ST2NSX6MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV23_V
ST2NSX6MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV2N_V
ST2NSX6MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV31_V
ST2NSX6MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV3N_V
ST2NSX6MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL1_kW
ST2NSX6MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL2_kW
ST2NSX6MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL3_kW
ST2NSX6MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerTotal_kW
ST2NSX6MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL1_kVA
ST2NSX6MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL2_kVA
ST2NSX6MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL3_kVA
ST2NSX6MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerTotal_kVA
ST2NSX6MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL1
ST2NSX6MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL2
ST2NSX6MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL3
ST2NSX6MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFTotal
ST2NSX6MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentAvgI1I2I3_A
ST2NSX6MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL1_A
ST2NSX6MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL2_A
ST2NSX6MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL3_A
ST2NSX6MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentMaxL1L2L3N_A
ST2NSX6MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentN_A
ST2NSX6MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL1_kVAr
ST2NSX6MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL2_kVAr
ST2NSX6MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL3_kVAr
ST2NSX6MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerTotal_kVAr
ST2NSX6MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MIN_Frequency_Hz
ST2NSX6MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL1_kVAr
ST2NSX6MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL2_kVAr
ST2NSX6MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL3_kVAr
ST2NSX6MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerTotal_kVAr
ST2NSX6MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL1
ST2NSX6MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL2
ST2NSX6MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL3
ST2NSX6MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorTotal
ST2NSX6MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL1_kVAr
ST2NSX6MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL2_kVAr
ST2NSX6MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL3_kVAr
ST2NSX6MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerTotal_kVAr
ST2NSX6MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI1_P
ST2NSX6MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI2_P
ST2NSX6MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI3_P
ST2NSX6MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV12_P
ST2NSX6MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV1N_P
ST2NSX6MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV23_P
ST2NSX6MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV2N_P
ST2NSX6MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV31_P
ST2NSX6MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV3N_P
ST2NSX6MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToN_V
ST2NSX6MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToPh_V
ST2NSX6MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV12_P
ST2NSX6MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV1N_P
ST2NSX6MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV23_P
ST2NSX6MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV2N_P
ST2NSX6MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV31_P
ST2NSX6MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV3N_P
ST2NSX6MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV12_V
ST2NSX6MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV1N_V
ST2NSX6MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV23_V
ST2NSX6MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV2N_V
ST2NSX6MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV31_V
ST2NSX6MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV3N_V
ST2NSX6PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL1
ST2NSX6PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL2
ST2NSX6PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL3
ST2NSX6PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorTotal
ST2NSX6RazEner_D | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D
ST2NSX6RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_SCADA
ST2NSX6RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_TEMP
ST2NSX6RazEner_M | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M
ST2NSX6RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_SCADA
ST2NSX6RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_TEMP
ST2NSX6RazEner_T | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T
ST2NSX6RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_SCADA
ST2NSX6RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_TEMP
ST2NSX6ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveEnergy_kVArh
ST2NSX6ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveNegativeEnergy_kVArh
ST2NSX6ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePositiveEnergy_kVArh
ST2NSX6ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerDemand_kVAr
ST2NSX6ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL1_kVAr
ST2NSX6ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL2_kVAr
ST2NSX6ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL3_kVAr
ST2NSX6ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerMaxDemand_kVAr
ST2NSX6ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerTotal_kVAr
ST2NSX6ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMAX
ST2NSX6ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMIN
ST2NSX6StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[6].StatusSwitch
ST2NSX6THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI1_P
ST2NSX6THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI2_P
ST2NSX6THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI3_P
ST2NSX6THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV12_P
ST2NSX6THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV1N_P
ST2NSX6THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV23_P
ST2NSX6THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV2N_P
ST2NSX6THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV31_P
ST2NSX6THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV3N_P
ST2NSX6VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToN_V
ST2NSX6VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToPh_V
ST2NSX6VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV12_P
ST2NSX6VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV1N_P
ST2NSX6VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV23_P
ST2NSX6VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV2N_P
ST2NSX6VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV31_P
ST2NSX6VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV3N_P
ST2NSX6VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV12_V
ST2NSX6VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV1N_V
ST2NSX6VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV23_V
ST2NSX6VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV2N_V
ST2NSX6VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV31_V
ST2NSX6VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV3N_V
ST2PLC_SB_IROGSM21_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM21_F2_2_NOT_OK
ST2PLC_SB_IROGSM22_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM22_F2_2_NOT_OK
ST2PMMQA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QA1_GlStik_IZKLOP_IZPAD
ST2PMMQB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QB1_GlStik_IZKLOP_IZPAD
ST2PMMSkNapaka_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_med60in80
ST2PMMSkNapaka_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_nad80
ST2PMMSkNapakaVirA_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_med60in80
ST2PMMSkNapakaVirA_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_nad80
ST2PMMSkNapakaVirB_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_med60in80
ST2PMMSkNapakaVirB_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_nad80
ST2PMMVirACurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[10]
ST2PMMVirACurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[11]
ST2PMMVirACurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[12]
ST2PMMVirACurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[13]
ST2PMMVirACurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[14]
ST2PMMVirACurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[15]
ST2PMMVirACurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[16]
ST2PMMVirACurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[17]
ST2PMMVirACurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[18]
ST2PMMVirACurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[19]
ST2PMMVirACurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[1]
ST2PMMVirACurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[20]
ST2PMMVirACurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[21]
ST2PMMVirACurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[22]
ST2PMMVirACurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[23]
ST2PMMVirACurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[24]
ST2PMMVirACurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[25]
ST2PMMVirACurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[26]
ST2PMMVirACurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[27]
ST2PMMVirACurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[28]
ST2PMMVirACurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[29]
ST2PMMVirACurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[2]
ST2PMMVirACurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[30]
ST2PMMVirACurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[31]
ST2PMMVirACurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[32]
ST2PMMVirACurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[33]
ST2PMMVirACurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[34]
ST2PMMVirACurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[35]
ST2PMMVirACurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[36]
ST2PMMVirACurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[37]
ST2PMMVirACurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[38]
ST2PMMVirACurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[39]
ST2PMMVirACurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[3]
ST2PMMVirACurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[40]
ST2PMMVirACurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[41]
ST2PMMVirACurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[42]
ST2PMMVirACurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[43]
ST2PMMVirACurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[44]
ST2PMMVirACurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[4]
ST2PMMVirACurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[5]
ST2PMMVirACurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[6]
ST2PMMVirACurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[7]
ST2PMMVirACurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[8]
ST2PMMVirACurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[9]
ST2PMMVirA_fsys | REAL | IOD_ST2 | ST2:.PMM.VirA_fsys
ST2PMMVirA_Isys | REAL | IOD_ST2 | ST2:.PMM.VirA_Isys
ST2PMMVirA_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirA_NapakaOzemljitve
ST2PMMVirA_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirA_PFsys
ST2PMMVirA_Psys | REAL | IOD_ST2 | ST2:.PMM.VirA_Psys
ST2PMMVirA_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirA_Qsys
ST2PMMVirA_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirA_Ssys
ST2PMMVirA_Usys | REAL | IOD_ST2 | ST2:.PMM.VirA_Usys
ST2PMMVirAActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirAActiveEnergyConsumed_kWh
ST2PMMVirAActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseA_kW
ST2PMMVirAActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseB_kW
ST2PMMVirAActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseC_kW
ST2PMMVirAAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_60to80
ST2PMMVirAAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_over80
ST2PMMVirAAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_60to80
ST2PMMVirAAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_over80
ST2PMMVirAAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_60to80
ST2PMMVirAAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_over80
ST2PMMVirAAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseA
ST2PMMVirAAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseB
ST2PMMVirAAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseC
ST2PMMVirACurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseA_A
ST2PMMVirACurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseB_A
ST2PMMVirACurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseC_A
ST2PMMVirAReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirAReactiveEnergyConsumed_kVARh
ST2PMMVirAReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseA
ST2PMMVirAReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseB
ST2PMMVirAReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseC
ST2PMMVirAVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAB_V
ST2PMMVirAVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAN_V
ST2PMMVirAVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBC_V
ST2PMMVirAVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBN_V
ST2PMMVirAVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCA_V
ST2PMMVirAVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCN_V
ST2PMMVirBCurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[10]
ST2PMMVirBCurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[11]
ST2PMMVirBCurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[12]
ST2PMMVirBCurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[13]
ST2PMMVirBCurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[14]
ST2PMMVirBCurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[15]
ST2PMMVirBCurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[16]
ST2PMMVirBCurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[17]
ST2PMMVirBCurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[18]
ST2PMMVirBCurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[19]
ST2PMMVirBCurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[1]
ST2PMMVirBCurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[20]
ST2PMMVirBCurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[21]
ST2PMMVirBCurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[22]
ST2PMMVirBCurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[23]
ST2PMMVirBCurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[24]
ST2PMMVirBCurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[25]
ST2PMMVirBCurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[26]
ST2PMMVirBCurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[27]
ST2PMMVirBCurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[28]
ST2PMMVirBCurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[29]
ST2PMMVirBCurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[2]
ST2PMMVirBCurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[30]
ST2PMMVirBCurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[31]
ST2PMMVirBCurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[32]
ST2PMMVirBCurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[33]
ST2PMMVirBCurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[34]
ST2PMMVirBCurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[35]
ST2PMMVirBCurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[36]
ST2PMMVirBCurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[37]
ST2PMMVirBCurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[38]
ST2PMMVirBCurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[39]
ST2PMMVirBCurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[3]
ST2PMMVirBCurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[40]
ST2PMMVirBCurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[41]
ST2PMMVirBCurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[42]
ST2PMMVirBCurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[43]
ST2PMMVirBCurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[44]
ST2PMMVirBCurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[4]
ST2PMMVirBCurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[5]
ST2PMMVirBCurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[6]
ST2PMMVirBCurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[7]
ST2PMMVirBCurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[8]
ST2PMMVirBCurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[9]
ST2PMMVirB_fsys | REAL | IOD_ST2 | ST2:.PMM.VirB_fsys
ST2PMMVirB_Isys | REAL | IOD_ST2 | ST2:.PMM.VirB_Isys
ST2PMMVirB_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirB_NapakaOzemljitve
ST2PMMVirB_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirB_PFsys
ST2PMMVirB_Psys | REAL | IOD_ST2 | ST2:.PMM.VirB_Psys
ST2PMMVirB_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirB_Qsys
ST2PMMVirB_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirB_Ssys
ST2PMMVirB_Usys | REAL | IOD_ST2 | ST2:.PMM.VirB_Usys
ST2PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirBActiveEnergyConsumed_kWh
ST2PMMVirBActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseA_kW
ST2PMMVirBActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseB_kW
ST2PMMVirBActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseC_kW
ST2PMMVirBAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_60to80
ST2PMMVirBAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_over80
ST2PMMVirBAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_60to80
ST2PMMVirBAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_over80
ST2PMMVirBAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_60to80
ST2PMMVirBAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_over80
ST2PMMVirBAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseA
ST2PMMVirBAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseB
ST2PMMVirBAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseC
ST2PMMVirBCurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseA_A
ST2PMMVirBCurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseB_A
ST2PMMVirBCurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseC_A
ST2PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirBReactiveEnergyConsumed_kVARh
ST2PMMVirBReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseA
ST2PMMVirBReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseB
ST2PMMVirBReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseC
ST2PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAB_V
ST2PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAN_V
ST2PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBC_V
ST2PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBN_V
ST2PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCA_V
ST2PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCN_V
ST2PrevisokaTemp | DIGITAL | IOD_ST2 | ST2:.PrevisokaTemp
ST2razlitjeLAH1 | DIGITAL | IOD_ST2 | ST2:.razlitjeLAH1
ST2SetDateTime | DIGITAL | IOD_ST2 | ST2:.SetDateTime
ST2SetDateTimeDemand | DIGITAL | IOD_ST2 | ST2:.SetDateTimeDemand
ST2SetDateTimeError | DIGITAL | IOD_ST2 | ST2:.SetDateTimeError
ST2SetDateTimeFinished | DIGITAL | IOD_ST2 | ST2:.SetDateTimeFinished
ST2SlabaBaterijaPLC | DIGITAL | IOD_ST2 | ST2:.SlabaBaterijaPLC
ST2TIA1_alarm | INT | IOD_ST2 | ST2:.TIA1_alarm
ST2TIA1_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA1_previs_temp
ST2TIA1_temp_s | INT | IOD_ST2 | ST2:.TIA1_temp_s
ST2TIA2_alarm | INT | IOD_ST2 | ST2:.TIA2_alarm
ST2TIA2_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA2_previs_temp
ST2TIA2_temp_s | INT | IOD_ST2 | ST2:.TIA2_temp_s
ST2TIA3_alarm | INT | IOD_ST2 | ST2:.TIA3_alarm
ST2TIA3_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA3_previs_temp
ST2TIA3_temp_s | INT | IOD_ST2 | ST2:.TIA3_temp_s
ST2TIA4_alarm | INT | IOD_ST2 | ST2:.TIA4_alarm
ST2TIA4_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA4_previs_temp
ST2TIA4_temp_s | INT | IOD_ST2 | ST2:.TIA4_temp_s
ST2TIA5_alarm | INT | IOD_ST2 | ST2:.TIA5_alarm
ST2TIA5_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA5_previs_temp
ST2TIA5_temp_s | INT | IOD_ST2 | ST2:.TIA5_temp_s
ST2TIA6_alarm | INT | IOD_ST2 | ST2:.TIA6_alarm
ST2TIA6_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA6_previs_temp
ST2TIA6_temp_s | INT | IOD_ST2 | ST2:.TIA6_temp_s
ST2TIA7_alarm | INT | IOD_ST2 | ST2:.TIA7_alarm
ST2TIA7_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA7_previs_temp
ST2TIA7_temp_s | INT | IOD_ST2 | ST2:.TIA7_temp_s
ST2TIA8_alarm | INT | IOD_ST2 | ST2:.TIA8_alarm
ST2TIA8_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA8_previs_temp
ST2TIA8_temp_s | INT | IOD_ST2 | ST2:.TIA8_temp_s
ST2ups_alarm | DIGITAL | IOD_ST2 | ST2:.ups_alarm
ST2ups_baterijski_nac | DIGITAL | IOD_ST2 | ST2:.ups_baterijski_nac
ST2ups_polnjenje | DIGITAL | IOD_ST2 | ST2:.ups_polnjenje
ST2UserCurrentLevel | INT | IOD_ST2 | ST2:.UserCurrentLevel | BYTE
ST2UserCurrentName | STRING | IOD_ST2 | ST2:.UserCurrentName
ST2UserDisplay | STRING | IOD_ST2 | ST2:.UserDisplay
ST2UserLoggedIn | DIGITAL | IOD_ST2 | ST2:.UserLoggedIn
ST2XVH_AlarmOn | DIGITAL | IOD_ST2 | ST2:.XVH_AlarmOn

## variable_2
ST2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada1
ST2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Dnevne_energija_scada2
ST2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada1
ST2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Mesecna_energija_scada2
ST2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada1
ST2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_ST2 | ST2:.Circ_Vpis_Tedenska_energija_scada2
ST2ComError | DIGITAL | IOD_ST2 | ST2:.ComError
ST2ComSCADA | DIGITAL | IOD_ST2 | ST2:.ComSCADA
ST2ComSCADA1 | DIGITAL | IOD_ST2 | ST2:.ComSCADA1
ST2ComSCADA2 | DIGITAL | IOD_ST2 | ST2:.ComSCADA2
ST2ComSCADA3 | DIGITAL | IOD_ST2 | ST2:.ComSCADA3
ST2DI2_I10_Rezerva3 | DIGITAL | IOD_ST2 | ST2:.DI2_I10_Rezerva3
ST2DI2_I11_Rezerva4 | DIGITAL | IOD_ST2 | ST2:.DI2_I11_Rezerva4
ST2DI2_I12_Rezerva5 | DIGITAL | IOD_ST2 | ST2:.DI2_I12_Rezerva5
ST2DI2_I13_Rezerva6 | DIGITAL | IOD_ST2 | ST2:.DI2_I13_Rezerva6
ST2DI2_I8_Rezerva1 | DIGITAL | IOD_ST2 | ST2:.DI2_I8_Rezerva1
ST2DI2_I9_Rezerva2 | DIGITAL | IOD_ST2 | ST2:.DI2_I9_Rezerva2
ST2DI_SB_IROGSM21_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Izkljucen
ST2DI_SB_IROGSM21_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q0_Vkljucen
ST2DI_SB_IROGSM21_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Izkljucen
ST2DI_SB_IROGSM21_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q11_Vkljucen
ST2DI_SB_IROGSM21_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Izkljucen
ST2DI_SB_IROGSM21_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q12_Vkljucen
ST2DI_SB_IROGSM21_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Izpad
ST2DI_SB_IROGSM21_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q13_Vkljucen
ST2DI_SB_IROGSM21_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Izpad
ST2DI_SB_IROGSM21_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q14_Vkljucen
ST2DI_SB_IROGSM21_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Izpad
ST2DI_SB_IROGSM21_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_Q15_Vkljucen
ST2DI_SB_IROGSM21_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM21_SkupnaNapaka
ST2DI_SB_IROGSM22_Q0_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Izkljucen
ST2DI_SB_IROGSM22_Q0_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q0_Vkljucen
ST2DI_SB_IROGSM22_Q11_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Izkljucen
ST2DI_SB_IROGSM22_Q11_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q11_Vkljucen
ST2DI_SB_IROGSM22_Q12_Izkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Izkljucen
ST2DI_SB_IROGSM22_Q12_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q12_Vkljucen
ST2DI_SB_IROGSM22_Q13_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Izpad
ST2DI_SB_IROGSM22_Q13_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q13_Vkljucen
ST2DI_SB_IROGSM22_Q14_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Izpad
ST2DI_SB_IROGSM22_Q14_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q14_Vkljucen
ST2DI_SB_IROGSM22_Q15_Izpad | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Izpad
ST2DI_SB_IROGSM22_Q15_Vkljucen | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_Q15_Vkljucen
ST2DI_SB_IROGSM22_SkupnaNapaka | DIGITAL | IOD_ST2 | ST2:.DI_SB_IROGSM22_SkupnaNapaka
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AA_Izolacija_NOT_OK
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_ST2 | ST2:.DI_SBi_RAZS_AB_Izolacija_NOT_OK
ST2ErrComNSX1 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[1]
ST2ErrComNSX2 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[2]
ST2ErrComNSX3 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[3]
ST2ErrComNSX4 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[4]
ST2ErrComNSX5 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[5]
ST2ErrComNSX6 | DIGITAL | IOD_ST2 | ST2:.ErrComNSX[6]
ST2ErrComPMM1 | DIGITAL | IOD_ST2 | ST2:.ErrComPMM[1]
ST2ErrComPort2 | DIGITAL | IOD_ST2 | ST2:.ErrComPort2
ST2ErrorComPMM1Error | DIGITAL | IOD_ST2 | ST2:.ErrorComPMM[1].Error
ST2napaka_kom_panel | DIGITAL | IOD_ST2 | ST2:.napaka_kom_panel
ST2napaka_kom_scada | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada
ST2napaka_kom_scada2 | DIGITAL | IOD_ST2 | ST2:.napaka_kom_scada2
ST2NapakaSenzorSkupno | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorSkupno
ST2NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA1
ST2NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA2
ST2NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA3
ST2NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA4
ST2NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA5
ST2NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA6
ST2NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA7
ST2NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaSenzorVlagaHIA8
ST2NapakaTSTempTIA1 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA1
ST2NapakaTSTempTIA2 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA2
ST2NapakaTSTempTIA3 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA3
ST2NapakaTSTempTIA4 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA4
ST2NapakaTSTempTIA5 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA5
ST2NapakaTSTempTIA6 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA6
ST2NapakaTSTempTIA7 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA7
ST2NapakaTSTempTIA8 | DIGITAL | IOD_ST2 | ST2:.NapakaTSTempTIA8
ST2NSX1ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMAX
ST2NSX1ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[1].ResetMIN
ST2NSX2ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMAX
ST2NSX2ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[2].ResetMIN
ST2NSX3ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMAX
ST2NSX3ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[3].ResetMIN
ST2NSX4ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMAX
ST2NSX4ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[4].ResetMIN
ST2NSX5ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMAX
ST2NSX5ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[5].ResetMIN
ST2NSX6ResetMAX | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMAX
ST2NSX6ResetMIN | DIGITAL | IOD_ST2 | ST2:.NSX[6].ResetMIN
ST2PLC_SB_IROGSM21_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM21_F2_2_NOT_OK
ST2PLC_SB_IROGSM22_F2_2_NOT_OK | DIGITAL | IOD_ST2 | ST2:.PLC_SB_IROGSM22_F2_2_NOT_OK
ST2PMMQA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QA1_GlStik_IZKLOP_IZPAD
ST2PMMQB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2 | ST2:.PMM.QB1_GlStik_IZKLOP_IZPAD
ST2PMMSkNapaka_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_med60in80
ST2PMMSkNapaka_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapaka_nad80
ST2PMMSkNapakaVirA_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_med60in80
ST2PMMSkNapakaVirA_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirA_nad80
ST2PMMSkNapakaVirB_med60in80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_med60in80
ST2PMMSkNapakaVirB_nad80 | DIGITAL | IOD_ST2 | ST2:.PMM.SkNapakaVirB_nad80
ST2PMMVirA_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirA_NapakaOzemljitve
ST2PMMVirB_NapakaOzemljitve | DIGITAL | IOD_ST2 | ST2:.PMM.VirB_NapakaOzemljitve
ST2PrevisokaTemp | DIGITAL | IOD_ST2 | ST2:.PrevisokaTemp
ST2razlitjeLAH1 | DIGITAL | IOD_ST2 | ST2:.razlitjeLAH1
ST2SetDateTime | DIGITAL | IOD_ST2 | ST2:.SetDateTime
ST2SetDateTimeDemand | DIGITAL | IOD_ST2 | ST2:.SetDateTimeDemand
ST2SetDateTimeError | DIGITAL | IOD_ST2 | ST2:.SetDateTimeError
ST2SetDateTimeFinished | DIGITAL | IOD_ST2 | ST2:.SetDateTimeFinished
ST2SlabaBaterijaPLC | DIGITAL | IOD_ST2 | ST2:.SlabaBaterijaPLC
ST2TIA1_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA1_previs_temp
ST2TIA2_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA2_previs_temp
ST2TIA3_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA3_previs_temp
ST2TIA4_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA4_previs_temp
ST2TIA5_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA5_previs_temp
ST2TIA6_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA6_previs_temp
ST2TIA7_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA7_previs_temp
ST2TIA8_previs_temp | DIGITAL | IOD_ST2 | ST2:.TIA8_previs_temp
ST2ups_alarm | DIGITAL | IOD_ST2 | ST2:.ups_alarm
ST2ups_baterijski_nac | DIGITAL | IOD_ST2 | ST2:.ups_baterijski_nac
ST2ups_polnjenje | DIGITAL | IOD_ST2 | ST2:.ups_polnjenje
ST2UserLoggedIn | DIGITAL | IOD_ST2 | ST2:.UserLoggedIn
ST2XVH_AlarmOn | DIGITAL | IOD_ST2 | ST2:.XVH_AlarmOn
ST2DateTimeDan | INT | IOD_ST2 | ST2:.DateTime.Dan | BYTE
ST2DateTimeLeto | INT | IOD_ST2 | ST2:.DateTime.Leto | BYTE
ST2DateTimeLeto2 | INT | IOD_ST2 | ST2:.DateTime.Leto2
ST2DateTimeMesec | INT | IOD_ST2 | ST2:.DateTime.Mesec | BYTE
ST2DateTimeMinuta | INT | IOD_ST2 | ST2:.DateTime.Minuta | BYTE
ST2DateTimePLC_Dan | INT | IOD_ST2 | ST2:.DateTime.PLC_Dan | BYTE
ST2DateTimePLC_DanVTednu | INT | IOD_ST2 | ST2:.DateTime.PLC_DanVTednu | BYTE
ST2DateTimePLC_Leto | INT | IOD_ST2 | ST2:.DateTime.PLC_Leto | BYTE
ST2DateTimePLC_Mesec | INT | IOD_ST2 | ST2:.DateTime.PLC_Mesec | BYTE
ST2DateTimePLC_Minuta | INT | IOD_ST2 | ST2:.DateTime.PLC_Minuta | BYTE
ST2DateTimePLC_Sekunda | INT | IOD_ST2 | ST2:.DateTime.PLC_Sekunda | BYTE
ST2DateTimePLC_Ura | INT | IOD_ST2 | ST2:.DateTime.PLC_Ura | BYTE
ST2DateTimeSekunda | INT | IOD_ST2 | ST2:.DateTime.Sekunda | BYTE
ST2DateTimeUra | INT | IOD_ST2 | ST2:.DateTime.Ura | BYTE
ST2ErrorComPMM1Status | INT | IOD_ST2 | ST2:.ErrorComPMM[1].Status
ST2HIA1_vlaga_s | INT | IOD_ST2 | ST2:.HIA1_vlaga_s
ST2HIA2_vlaga_s | INT | IOD_ST2 | ST2:.HIA2_vlaga_s
ST2HIA3_vlaga_s | INT | IOD_ST2 | ST2:.HIA3_vlaga_s
ST2HIA4_vlaga_s | INT | IOD_ST2 | ST2:.HIA4_vlaga_s
ST2HIA5_vlaga_s | INT | IOD_ST2 | ST2:.HIA5_vlaga_s
ST2HIA6_vlaga_s | INT | IOD_ST2 | ST2:.HIA6_vlaga_s
ST2HIA7_vlaga_s | INT | IOD_ST2 | ST2:.HIA7_vlaga_s
ST2HIA8_vlaga_s | INT | IOD_ST2 | ST2:.HIA8_vlaga_s
ST2TIA1_alarm | INT | IOD_ST2 | ST2:.TIA1_alarm
ST2TIA1_temp_s | INT | IOD_ST2 | ST2:.TIA1_temp_s
ST2TIA2_alarm | INT | IOD_ST2 | ST2:.TIA2_alarm
ST2TIA2_temp_s | INT | IOD_ST2 | ST2:.TIA2_temp_s
ST2TIA3_alarm | INT | IOD_ST2 | ST2:.TIA3_alarm
ST2TIA3_temp_s | INT | IOD_ST2 | ST2:.TIA3_temp_s
ST2TIA4_alarm | INT | IOD_ST2 | ST2:.TIA4_alarm
ST2TIA4_temp_s | INT | IOD_ST2 | ST2:.TIA4_temp_s
ST2TIA5_alarm | INT | IOD_ST2 | ST2:.TIA5_alarm
ST2TIA5_temp_s | INT | IOD_ST2 | ST2:.TIA5_temp_s
ST2TIA6_alarm | INT | IOD_ST2 | ST2:.TIA6_alarm
ST2TIA6_temp_s | INT | IOD_ST2 | ST2:.TIA6_temp_s
ST2TIA7_alarm | INT | IOD_ST2 | ST2:.TIA7_alarm
ST2TIA7_temp_s | INT | IOD_ST2 | ST2:.TIA7_temp_s
ST2TIA8_alarm | INT | IOD_ST2 | ST2:.TIA8_alarm
ST2TIA8_temp_s | INT | IOD_ST2 | ST2:.TIA8_temp_s
ST2UserCurrentLevel | INT | IOD_ST2 | ST2:.UserCurrentLevel | BYTE
ST2iPMM_VirA_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok1
ST2iPMM_VirA_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok10
ST2iPMM_VirA_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok11
ST2iPMM_VirA_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok12
ST2iPMM_VirA_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok13
ST2iPMM_VirA_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok14
ST2iPMM_VirA_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok15
ST2iPMM_VirA_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok16
ST2iPMM_VirA_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok17
ST2iPMM_VirA_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok18
ST2iPMM_VirA_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok19
ST2iPMM_VirA_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok2
ST2iPMM_VirA_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok20
ST2iPMM_VirA_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok21
ST2iPMM_VirA_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok22
ST2iPMM_VirA_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok23
ST2iPMM_VirA_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok24
ST2iPMM_VirA_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok25
ST2iPMM_VirA_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok26
ST2iPMM_VirA_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok27
ST2iPMM_VirA_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok28
ST2iPMM_VirA_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok29
ST2iPMM_VirA_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok3
ST2iPMM_VirA_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok30
ST2iPMM_VirA_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok31
ST2iPMM_VirA_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok32
ST2iPMM_VirA_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok33
ST2iPMM_VirA_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok34
ST2iPMM_VirA_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok35
ST2iPMM_VirA_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok36
ST2iPMM_VirA_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok37
ST2iPMM_VirA_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok38
ST2iPMM_VirA_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok39
ST2iPMM_VirA_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok4
ST2iPMM_VirA_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok40
ST2iPMM_VirA_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok41
ST2iPMM_VirA_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok42
ST2iPMM_VirA_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok43
ST2iPMM_VirA_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok44
ST2iPMM_VirA_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok5
ST2iPMM_VirA_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok6
ST2iPMM_VirA_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok7
ST2iPMM_VirA_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok8
ST2iPMM_VirA_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirA_Tok9
ST2iPMM_VirB_Tok1 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok1
ST2iPMM_VirB_Tok10 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok10
ST2iPMM_VirB_Tok11 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok11
ST2iPMM_VirB_Tok12 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok12
ST2iPMM_VirB_Tok13 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok13
ST2iPMM_VirB_Tok14 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok14
ST2iPMM_VirB_Tok15 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok15
ST2iPMM_VirB_Tok16 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok16
ST2iPMM_VirB_Tok17 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok17
ST2iPMM_VirB_Tok18 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok18
ST2iPMM_VirB_Tok19 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok19
ST2iPMM_VirB_Tok2 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok2
ST2iPMM_VirB_Tok20 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok20
ST2iPMM_VirB_Tok21 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok21
ST2iPMM_VirB_Tok22 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok22
ST2iPMM_VirB_Tok23 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok23
ST2iPMM_VirB_Tok24 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok24
ST2iPMM_VirB_Tok25 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok25
ST2iPMM_VirB_Tok26 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok26
ST2iPMM_VirB_Tok27 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok27
ST2iPMM_VirB_Tok28 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok28
ST2iPMM_VirB_Tok29 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok29
ST2iPMM_VirB_Tok3 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok3
ST2iPMM_VirB_Tok30 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok30
ST2iPMM_VirB_Tok31 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok31
ST2iPMM_VirB_Tok32 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok32
ST2iPMM_VirB_Tok33 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok33
ST2iPMM_VirB_Tok34 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok34
ST2iPMM_VirB_Tok35 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok35
ST2iPMM_VirB_Tok36 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok36
ST2iPMM_VirB_Tok37 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok37
ST2iPMM_VirB_Tok38 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok38
ST2iPMM_VirB_Tok39 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok39
ST2iPMM_VirB_Tok4 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok4
ST2iPMM_VirB_Tok40 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok40
ST2iPMM_VirB_Tok41 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok41
ST2iPMM_VirB_Tok42 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok42
ST2iPMM_VirB_Tok43 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok43
ST2iPMM_VirB_Tok44 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok44
ST2iPMM_VirB_Tok5 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok5
ST2iPMM_VirB_Tok6 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok6
ST2iPMM_VirB_Tok7 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok7
ST2iPMM_VirB_Tok8 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok8
ST2iPMM_VirB_Tok9 | REAL | IOD_ST2 | ST2:.iPMM_VirB_Tok9
ST2NSX1ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveEnergy_kWh
ST2NSX1ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActiveNegativeEnergy_kWh
ST2NSX1ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].ActivePositiveEnergy_kWh
ST2NSX1ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerDemand_kW
ST2NSX1ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL1_kW
ST2NSX1ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL2_kW
ST2NSX1ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerL3_kW
ST2NSX1ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerMaxDemand_kW
ST2NSX1ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].ActivePowerTotal_kW
ST2NSX1ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[1].ApparentEnergy_kVAh
ST2NSX1ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerDemand_kVA
ST2NSX1ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparentPowerMaxDemand_kVA
ST2NSX1ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL1_kVA
ST2NSX1ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL2_kVA
ST2NSX1ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerL3_kVA
ST2NSX1ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].ApparetnPowerTotal_kVA
ST2NSX1CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL1
ST2NSX1CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL2
ST2NSX1CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].CosFL3
ST2NSX1CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].CosFTotal
ST2NSX1CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulNegativeActiveEnergy_kWh
ST2NSX1CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[1].CumulPositiveActiveEnergy_kWh
ST2NSX1CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentAvgI1I2I3_A
ST2NSX1CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL1_A
ST2NSX1CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL2_A
ST2NSX1CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandL3_A
ST2NSX1CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL1_A
ST2NSX1CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL2_A
ST2NSX1CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxL3_A
ST2NSX1CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandMaxN_A
ST2NSX1CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentDemandN_A
ST2NSX1CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL1_A
ST2NSX1CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL2_A
ST2NSX1CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentL3_A
ST2NSX1CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].CurrentN_A
ST2NSX1CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI1_P
ST2NSX1CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI2_P
ST2NSX1CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbI3_P
ST2NSX1CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[1].CurrentUnbN_P
ST2NSX1DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].DelovnaEnergija_TEMP
ST2NSX1DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL1_kVAr
ST2NSX1DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL2_kVAr
ST2NSX1DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerL3_kVAr
ST2NSX1DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].DistortionPowerTotal_kVAr
ST2NSX1Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].Frequency_Hz
ST2NSX1FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL1_kVAr
ST2NSX1FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL2_kVAr
ST2NSX1FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerL3_kVAr
ST2NSX1FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].FunReactivePowerTotal_kVAr
ST2NSX1MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL1_kW
ST2NSX1MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL2_kW
ST2NSX1MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerL3_kW
ST2NSX1MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ActivePowerTotal_kW
ST2NSX1MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL1_kVA
ST2NSX1MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL2_kVA
ST2NSX1MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerL3_kVA
ST2NSX1MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ApparetnPowerTotal_kVA
ST2NSX1MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL1
ST2NSX1MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL2
ST2NSX1MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFL3
ST2NSX1MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CosFTotal
ST2NSX1MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentAvgI1I2I3_A
ST2NSX1MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL1_A
ST2NSX1MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL2_A
ST2NSX1MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentL3_A
ST2NSX1MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentMaxL1L2L3N_A
ST2NSX1MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MAX_CurrentN_A
ST2NSX1MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL1_kVAr
ST2NSX1MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL2_kVAr
ST2NSX1MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerL3_kVAr
ST2NSX1MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_DistortionPowerTotal_kVAr
ST2NSX1MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MAX_Frequency_Hz
ST2NSX1MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL1_kVAr
ST2NSX1MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL2_kVAr
ST2NSX1MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerL3_kVAr
ST2NSX1MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_FunReactivePowerTotal_kVAr
ST2NSX1MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL1
ST2NSX1MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL2
ST2NSX1MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorL3
ST2NSX1MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MAX_PowerFactorTotal
ST2NSX1MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL1_kVAr
ST2NSX1MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL2_kVAr
ST2NSX1MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerL3_kVAr
ST2NSX1MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MAX_ReactivePowerTotal_kVAr
ST2NSX1MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI1_P
ST2NSX1MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI2_P
ST2NSX1MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDI3_P
ST2NSX1MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV12_P
ST2NSX1MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV1N_P
ST2NSX1MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV23_P
ST2NSX1MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV2N_P
ST2NSX1MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV31_P
ST2NSX1MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_THDV3N_P
ST2NSX1MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToN_V
ST2NSX1MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageAvgPhToPh_V
ST2NSX1MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV12_P
ST2NSX1MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV1N_P
ST2NSX1MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV23_P
ST2NSX1MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV2N_P
ST2NSX1MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV31_P
ST2NSX1MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageUnbV3N_P
ST2NSX1MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV12_V
ST2NSX1MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV1N_V
ST2NSX1MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV23_V
ST2NSX1MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV2N_V
ST2NSX1MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV31_V
ST2NSX1MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MAX_VoltageV3N_V
ST2NSX1MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL1_kW
ST2NSX1MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL2_kW
ST2NSX1MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerL3_kW
ST2NSX1MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ActivePowerTotal_kW
ST2NSX1MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL1_kVA
ST2NSX1MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL2_kVA
ST2NSX1MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerL3_kVA
ST2NSX1MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ApparetnPowerTotal_kVA
ST2NSX1MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL1
ST2NSX1MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL2
ST2NSX1MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFL3
ST2NSX1MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CosFTotal
ST2NSX1MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentAvgI1I2I3_A
ST2NSX1MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL1_A
ST2NSX1MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL2_A
ST2NSX1MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentL3_A
ST2NSX1MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentMaxL1L2L3N_A
ST2NSX1MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[1].MIN_CurrentN_A
ST2NSX1MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL1_kVAr
ST2NSX1MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL2_kVAr
ST2NSX1MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerL3_kVAr
ST2NSX1MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_DistortionPowerTotal_kVAr
ST2NSX1MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[1].MIN_Frequency_Hz
ST2NSX1MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL1_kVAr
ST2NSX1MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL2_kVAr
ST2NSX1MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerL3_kVAr
ST2NSX1MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_FunReactivePowerTotal_kVAr
ST2NSX1MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL1
ST2NSX1MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL2
ST2NSX1MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorL3
ST2NSX1MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].MIN_PowerFactorTotal
ST2NSX1MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL1_kVAr
ST2NSX1MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL2_kVAr
ST2NSX1MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerL3_kVAr
ST2NSX1MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].MIN_ReactivePowerTotal_kVAr
ST2NSX1MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI1_P
ST2NSX1MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI2_P
ST2NSX1MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDI3_P
ST2NSX1MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV12_P
ST2NSX1MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV1N_P
ST2NSX1MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV23_P
ST2NSX1MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV2N_P
ST2NSX1MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV31_P
ST2NSX1MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_THDV3N_P
ST2NSX1MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToN_V
ST2NSX1MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageAvgPhToPh_V
ST2NSX1MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV12_P
ST2NSX1MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV1N_P
ST2NSX1MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV23_P
ST2NSX1MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV2N_P
ST2NSX1MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV31_P
ST2NSX1MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageUnbV3N_P
ST2NSX1MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV12_V
ST2NSX1MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV1N_V
ST2NSX1MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV23_V
ST2NSX1MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV2N_V
ST2NSX1MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV31_V
ST2NSX1MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].MIN_VoltageV3N_V
ST2NSX1PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL1
ST2NSX1PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL2
ST2NSX1PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorL3
ST2NSX1PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[1].PowerFactorTotal
ST2NSX1RazEner_D | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D
ST2NSX1RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_SCADA
ST2NSX1RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_D_TEMP
ST2NSX1RazEner_M | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M
ST2NSX1RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_SCADA
ST2NSX1RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_M_TEMP
ST2NSX1RazEner_T | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T
ST2NSX1RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_SCADA
ST2NSX1RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[1].RazEner_T_TEMP
ST2NSX1ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveEnergy_kVArh
ST2NSX1ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactiveNegativeEnergy_kVArh
ST2NSX1ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePositiveEnergy_kVArh
ST2NSX1ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerDemand_kVAr
ST2NSX1ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL1_kVAr
ST2NSX1ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL2_kVAr
ST2NSX1ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerL3_kVAr
ST2NSX1ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerMaxDemand_kVAr
ST2NSX1ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[1].ReactivePowerTotal_kVAr
ST2NSX1THDI1_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI1_P
ST2NSX1THDI2_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI2_P
ST2NSX1THDI3_P | REAL | IOD_ST2 | ST2:.NSX[1].THDI3_P
ST2NSX1THDV12_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV12_P
ST2NSX1THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV1N_P
ST2NSX1THDV23_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV23_P
ST2NSX1THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV2N_P
ST2NSX1THDV31_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV31_P
ST2NSX1THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].THDV3N_P
ST2NSX1VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToN_V
ST2NSX1VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageAvgPhToPh_V
ST2NSX1VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV12_P
ST2NSX1VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV1N_P
ST2NSX1VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV23_P
ST2NSX1VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV2N_P
ST2NSX1VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV31_P
ST2NSX1VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[1].VoltageUnbV3N_P
ST2NSX1VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV12_V
ST2NSX1VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV1N_V
ST2NSX1VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV23_V
ST2NSX1VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV2N_V
ST2NSX1VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV31_V
ST2NSX1VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[1].VoltageV3N_V
ST2NSX2ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveEnergy_kWh
ST2NSX2ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActiveNegativeEnergy_kWh
ST2NSX2ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].ActivePositiveEnergy_kWh
ST2NSX2ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerDemand_kW
ST2NSX2ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL1_kW
ST2NSX2ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL2_kW
ST2NSX2ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerL3_kW
ST2NSX2ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerMaxDemand_kW
ST2NSX2ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].ActivePowerTotal_kW
ST2NSX2ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[2].ApparentEnergy_kVAh
ST2NSX2ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerDemand_kVA
ST2NSX2ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparentPowerMaxDemand_kVA
ST2NSX2ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL1_kVA
ST2NSX2ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL2_kVA
ST2NSX2ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerL3_kVA
ST2NSX2ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].ApparetnPowerTotal_kVA
ST2NSX2CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL1
ST2NSX2CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL2
ST2NSX2CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].CosFL3
ST2NSX2CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].CosFTotal
ST2NSX2CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulNegativeActiveEnergy_kWh
ST2NSX2CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[2].CumulPositiveActiveEnergy_kWh
ST2NSX2CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentAvgI1I2I3_A
ST2NSX2CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL1_A
ST2NSX2CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL2_A
ST2NSX2CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandL3_A
ST2NSX2CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL1_A
ST2NSX2CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL2_A
ST2NSX2CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxL3_A
ST2NSX2CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandMaxN_A
ST2NSX2CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentDemandN_A
ST2NSX2CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL1_A
ST2NSX2CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL2_A
ST2NSX2CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentL3_A
ST2NSX2CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].CurrentN_A
ST2NSX2CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI1_P
ST2NSX2CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI2_P
ST2NSX2CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbI3_P
ST2NSX2CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[2].CurrentUnbN_P
ST2NSX2DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].DelovnaEnergija_TEMP
ST2NSX2DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL1_kVAr
ST2NSX2DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL2_kVAr
ST2NSX2DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerL3_kVAr
ST2NSX2DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].DistortionPowerTotal_kVAr
ST2NSX2Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].Frequency_Hz
ST2NSX2FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL1_kVAr
ST2NSX2FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL2_kVAr
ST2NSX2FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerL3_kVAr
ST2NSX2FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].FunReactivePowerTotal_kVAr
ST2NSX2MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL1_kW
ST2NSX2MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL2_kW
ST2NSX2MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerL3_kW
ST2NSX2MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ActivePowerTotal_kW
ST2NSX2MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL1_kVA
ST2NSX2MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL2_kVA
ST2NSX2MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerL3_kVA
ST2NSX2MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ApparetnPowerTotal_kVA
ST2NSX2MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL1
ST2NSX2MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL2
ST2NSX2MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFL3
ST2NSX2MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CosFTotal
ST2NSX2MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentAvgI1I2I3_A
ST2NSX2MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL1_A
ST2NSX2MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL2_A
ST2NSX2MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentL3_A
ST2NSX2MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentMaxL1L2L3N_A
ST2NSX2MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MAX_CurrentN_A
ST2NSX2MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL1_kVAr
ST2NSX2MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL2_kVAr
ST2NSX2MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerL3_kVAr
ST2NSX2MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_DistortionPowerTotal_kVAr
ST2NSX2MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MAX_Frequency_Hz
ST2NSX2MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL1_kVAr
ST2NSX2MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL2_kVAr
ST2NSX2MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerL3_kVAr
ST2NSX2MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_FunReactivePowerTotal_kVAr
ST2NSX2MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL1
ST2NSX2MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL2
ST2NSX2MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorL3
ST2NSX2MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MAX_PowerFactorTotal
ST2NSX2MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL1_kVAr
ST2NSX2MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL2_kVAr
ST2NSX2MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerL3_kVAr
ST2NSX2MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MAX_ReactivePowerTotal_kVAr
ST2NSX2MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI1_P
ST2NSX2MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI2_P
ST2NSX2MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDI3_P
ST2NSX2MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV12_P
ST2NSX2MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV1N_P
ST2NSX2MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV23_P
ST2NSX2MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV2N_P
ST2NSX2MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV31_P
ST2NSX2MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_THDV3N_P
ST2NSX2MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToN_V
ST2NSX2MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageAvgPhToPh_V
ST2NSX2MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV12_P
ST2NSX2MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV1N_P
ST2NSX2MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV23_P
ST2NSX2MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV2N_P
ST2NSX2MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV31_P
ST2NSX2MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageUnbV3N_P
ST2NSX2MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV12_V
ST2NSX2MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV1N_V
ST2NSX2MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV23_V
ST2NSX2MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV2N_V
ST2NSX2MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV31_V
ST2NSX2MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MAX_VoltageV3N_V
ST2NSX2MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL1_kW
ST2NSX2MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL2_kW
ST2NSX2MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerL3_kW
ST2NSX2MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ActivePowerTotal_kW
ST2NSX2MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL1_kVA
ST2NSX2MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL2_kVA
ST2NSX2MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerL3_kVA
ST2NSX2MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ApparetnPowerTotal_kVA
ST2NSX2MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL1
ST2NSX2MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL2
ST2NSX2MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFL3
ST2NSX2MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CosFTotal
ST2NSX2MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentAvgI1I2I3_A
ST2NSX2MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL1_A
ST2NSX2MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL2_A
ST2NSX2MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentL3_A
ST2NSX2MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentMaxL1L2L3N_A
ST2NSX2MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[2].MIN_CurrentN_A
ST2NSX2MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL1_kVAr
ST2NSX2MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL2_kVAr
ST2NSX2MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerL3_kVAr
ST2NSX2MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_DistortionPowerTotal_kVAr
ST2NSX2MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[2].MIN_Frequency_Hz
ST2NSX2MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL1_kVAr
ST2NSX2MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL2_kVAr
ST2NSX2MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerL3_kVAr
ST2NSX2MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_FunReactivePowerTotal_kVAr
ST2NSX2MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL1
ST2NSX2MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL2
ST2NSX2MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorL3
ST2NSX2MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].MIN_PowerFactorTotal
ST2NSX2MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL1_kVAr
ST2NSX2MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL2_kVAr
ST2NSX2MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerL3_kVAr
ST2NSX2MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].MIN_ReactivePowerTotal_kVAr
ST2NSX2MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI1_P
ST2NSX2MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI2_P
ST2NSX2MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDI3_P
ST2NSX2MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV12_P
ST2NSX2MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV1N_P
ST2NSX2MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV23_P
ST2NSX2MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV2N_P
ST2NSX2MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV31_P
ST2NSX2MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_THDV3N_P
ST2NSX2MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToN_V
ST2NSX2MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageAvgPhToPh_V
ST2NSX2MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV12_P
ST2NSX2MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV1N_P
ST2NSX2MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV23_P
ST2NSX2MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV2N_P
ST2NSX2MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV31_P
ST2NSX2MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageUnbV3N_P
ST2NSX2MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV12_V
ST2NSX2MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV1N_V
ST2NSX2MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV23_V
ST2NSX2MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV2N_V
ST2NSX2MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV31_V
ST2NSX2MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].MIN_VoltageV3N_V
ST2NSX2PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL1
ST2NSX2PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL2
ST2NSX2PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorL3
ST2NSX2PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[2].PowerFactorTotal
ST2NSX2RazEner_D | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D
ST2NSX2RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_SCADA
ST2NSX2RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_D_TEMP
ST2NSX2RazEner_M | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M
ST2NSX2RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_SCADA
ST2NSX2RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_M_TEMP
ST2NSX2RazEner_T | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T
ST2NSX2RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_SCADA
ST2NSX2RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[2].RazEner_T_TEMP
ST2NSX2ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveEnergy_kVArh
ST2NSX2ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactiveNegativeEnergy_kVArh
ST2NSX2ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePositiveEnergy_kVArh
ST2NSX2ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerDemand_kVAr
ST2NSX2ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL1_kVAr
ST2NSX2ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL2_kVAr
ST2NSX2ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerL3_kVAr
ST2NSX2ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerMaxDemand_kVAr
ST2NSX2ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[2].ReactivePowerTotal_kVAr
ST2NSX2THDI1_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI1_P
ST2NSX2THDI2_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI2_P
ST2NSX2THDI3_P | REAL | IOD_ST2 | ST2:.NSX[2].THDI3_P
ST2NSX2THDV12_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV12_P
ST2NSX2THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV1N_P
ST2NSX2THDV23_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV23_P
ST2NSX2THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV2N_P
ST2NSX2THDV31_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV31_P
ST2NSX2THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].THDV3N_P
ST2NSX2VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToN_V
ST2NSX2VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageAvgPhToPh_V
ST2NSX2VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV12_P
ST2NSX2VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV1N_P
ST2NSX2VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV23_P
ST2NSX2VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV2N_P
ST2NSX2VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV31_P
ST2NSX2VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[2].VoltageUnbV3N_P
ST2NSX2VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV12_V
ST2NSX2VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV1N_V
ST2NSX2VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV23_V
ST2NSX2VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV2N_V
ST2NSX2VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV31_V
ST2NSX2VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[2].VoltageV3N_V
ST2NSX3ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveEnergy_kWh
ST2NSX3ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActiveNegativeEnergy_kWh
ST2NSX3ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].ActivePositiveEnergy_kWh
ST2NSX3ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerDemand_kW
ST2NSX3ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL1_kW
ST2NSX3ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL2_kW
ST2NSX3ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerL3_kW
ST2NSX3ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerMaxDemand_kW
ST2NSX3ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].ActivePowerTotal_kW
ST2NSX3ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[3].ApparentEnergy_kVAh
ST2NSX3ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerDemand_kVA
ST2NSX3ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparentPowerMaxDemand_kVA
ST2NSX3ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL1_kVA
ST2NSX3ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL2_kVA
ST2NSX3ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerL3_kVA
ST2NSX3ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].ApparetnPowerTotal_kVA
ST2NSX3CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL1
ST2NSX3CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL2
ST2NSX3CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].CosFL3
ST2NSX3CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].CosFTotal
ST2NSX3CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulNegativeActiveEnergy_kWh
ST2NSX3CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[3].CumulPositiveActiveEnergy_kWh
ST2NSX3CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentAvgI1I2I3_A
ST2NSX3CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL1_A
ST2NSX3CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL2_A
ST2NSX3CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandL3_A
ST2NSX3CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL1_A
ST2NSX3CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL2_A
ST2NSX3CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxL3_A
ST2NSX3CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandMaxN_A
ST2NSX3CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentDemandN_A
ST2NSX3CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL1_A
ST2NSX3CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL2_A
ST2NSX3CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentL3_A
ST2NSX3CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].CurrentN_A
ST2NSX3CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI1_P
ST2NSX3CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI2_P
ST2NSX3CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbI3_P
ST2NSX3CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[3].CurrentUnbN_P
ST2NSX3DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].DelovnaEnergija_TEMP
ST2NSX3DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL1_kVAr
ST2NSX3DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL2_kVAr
ST2NSX3DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerL3_kVAr
ST2NSX3DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].DistortionPowerTotal_kVAr
ST2NSX3Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].Frequency_Hz
ST2NSX3FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL1_kVAr
ST2NSX3FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL2_kVAr
ST2NSX3FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerL3_kVAr
ST2NSX3FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].FunReactivePowerTotal_kVAr
ST2NSX3MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL1_kW
ST2NSX3MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL2_kW
ST2NSX3MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerL3_kW
ST2NSX3MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ActivePowerTotal_kW
ST2NSX3MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL1_kVA
ST2NSX3MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL2_kVA
ST2NSX3MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerL3_kVA
ST2NSX3MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ApparetnPowerTotal_kVA
ST2NSX3MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL1
ST2NSX3MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL2
ST2NSX3MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFL3
ST2NSX3MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CosFTotal
ST2NSX3MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentAvgI1I2I3_A
ST2NSX3MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL1_A
ST2NSX3MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL2_A
ST2NSX3MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentL3_A
ST2NSX3MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentMaxL1L2L3N_A
ST2NSX3MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MAX_CurrentN_A
ST2NSX3MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL1_kVAr
ST2NSX3MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL2_kVAr
ST2NSX3MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerL3_kVAr
ST2NSX3MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_DistortionPowerTotal_kVAr
ST2NSX3MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MAX_Frequency_Hz
ST2NSX3MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL1_kVAr
ST2NSX3MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL2_kVAr
ST2NSX3MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerL3_kVAr
ST2NSX3MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_FunReactivePowerTotal_kVAr
ST2NSX3MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL1
ST2NSX3MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL2
ST2NSX3MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorL3
ST2NSX3MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MAX_PowerFactorTotal
ST2NSX3MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL1_kVAr
ST2NSX3MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL2_kVAr
ST2NSX3MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerL3_kVAr
ST2NSX3MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MAX_ReactivePowerTotal_kVAr
ST2NSX3MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI1_P
ST2NSX3MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI2_P
ST2NSX3MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDI3_P
ST2NSX3MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV12_P
ST2NSX3MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV1N_P
ST2NSX3MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV23_P
ST2NSX3MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV2N_P
ST2NSX3MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV31_P
ST2NSX3MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_THDV3N_P
ST2NSX3MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToN_V
ST2NSX3MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageAvgPhToPh_V
ST2NSX3MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV12_P
ST2NSX3MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV1N_P
ST2NSX3MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV23_P
ST2NSX3MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV2N_P
ST2NSX3MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV31_P
ST2NSX3MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageUnbV3N_P
ST2NSX3MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV12_V
ST2NSX3MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV1N_V
ST2NSX3MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV23_V
ST2NSX3MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV2N_V
ST2NSX3MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV31_V
ST2NSX3MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MAX_VoltageV3N_V
ST2NSX3MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL1_kW
ST2NSX3MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL2_kW
ST2NSX3MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerL3_kW
ST2NSX3MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ActivePowerTotal_kW
ST2NSX3MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL1_kVA
ST2NSX3MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL2_kVA
ST2NSX3MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerL3_kVA
ST2NSX3MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ApparetnPowerTotal_kVA
ST2NSX3MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL1
ST2NSX3MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL2
ST2NSX3MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFL3
ST2NSX3MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CosFTotal
ST2NSX3MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentAvgI1I2I3_A
ST2NSX3MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL1_A
ST2NSX3MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL2_A
ST2NSX3MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentL3_A
ST2NSX3MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentMaxL1L2L3N_A
ST2NSX3MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[3].MIN_CurrentN_A
ST2NSX3MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL1_kVAr
ST2NSX3MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL2_kVAr
ST2NSX3MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerL3_kVAr
ST2NSX3MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_DistortionPowerTotal_kVAr
ST2NSX3MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[3].MIN_Frequency_Hz
ST2NSX3MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL1_kVAr
ST2NSX3MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL2_kVAr
ST2NSX3MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerL3_kVAr
ST2NSX3MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_FunReactivePowerTotal_kVAr
ST2NSX3MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL1
ST2NSX3MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL2
ST2NSX3MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorL3
ST2NSX3MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].MIN_PowerFactorTotal
ST2NSX3MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL1_kVAr
ST2NSX3MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL2_kVAr
ST2NSX3MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerL3_kVAr
ST2NSX3MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].MIN_ReactivePowerTotal_kVAr
ST2NSX3MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI1_P
ST2NSX3MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI2_P
ST2NSX3MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDI3_P
ST2NSX3MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV12_P
ST2NSX3MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV1N_P
ST2NSX3MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV23_P
ST2NSX3MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV2N_P
ST2NSX3MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV31_P
ST2NSX3MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_THDV3N_P
ST2NSX3MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToN_V
ST2NSX3MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageAvgPhToPh_V
ST2NSX3MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV12_P
ST2NSX3MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV1N_P
ST2NSX3MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV23_P
ST2NSX3MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV2N_P
ST2NSX3MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV31_P
ST2NSX3MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageUnbV3N_P
ST2NSX3MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV12_V
ST2NSX3MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV1N_V
ST2NSX3MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV23_V
ST2NSX3MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV2N_V
ST2NSX3MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV31_V
ST2NSX3MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].MIN_VoltageV3N_V
ST2NSX3PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL1
ST2NSX3PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL2
ST2NSX3PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorL3
ST2NSX3PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[3].PowerFactorTotal
ST2NSX3RazEner_D | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D
ST2NSX3RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_SCADA
ST2NSX3RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_D_TEMP
ST2NSX3RazEner_M | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M
ST2NSX3RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_SCADA
ST2NSX3RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_M_TEMP
ST2NSX3RazEner_T | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T
ST2NSX3RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_SCADA
ST2NSX3RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[3].RazEner_T_TEMP
ST2NSX3ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveEnergy_kVArh
ST2NSX3ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactiveNegativeEnergy_kVArh
ST2NSX3ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePositiveEnergy_kVArh
ST2NSX3ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerDemand_kVAr
ST2NSX3ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL1_kVAr
ST2NSX3ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL2_kVAr
ST2NSX3ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerL3_kVAr
ST2NSX3ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerMaxDemand_kVAr
ST2NSX3ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[3].ReactivePowerTotal_kVAr
ST2NSX3THDI1_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI1_P
ST2NSX3THDI2_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI2_P
ST2NSX3THDI3_P | REAL | IOD_ST2 | ST2:.NSX[3].THDI3_P
ST2NSX3THDV12_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV12_P
ST2NSX3THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV1N_P
ST2NSX3THDV23_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV23_P
ST2NSX3THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV2N_P
ST2NSX3THDV31_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV31_P
ST2NSX3THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].THDV3N_P
ST2NSX3VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToN_V
ST2NSX3VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageAvgPhToPh_V
ST2NSX3VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV12_P
ST2NSX3VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV1N_P
ST2NSX3VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV23_P
ST2NSX3VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV2N_P
ST2NSX3VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV31_P
ST2NSX3VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[3].VoltageUnbV3N_P
ST2NSX3VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV12_V
ST2NSX3VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV1N_V
ST2NSX3VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV23_V
ST2NSX3VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV2N_V
ST2NSX3VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV31_V
ST2NSX3VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[3].VoltageV3N_V
ST2NSX4ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveEnergy_kWh
ST2NSX4ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActiveNegativeEnergy_kWh
ST2NSX4ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].ActivePositiveEnergy_kWh
ST2NSX4ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerDemand_kW
ST2NSX4ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL1_kW
ST2NSX4ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL2_kW
ST2NSX4ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerL3_kW
ST2NSX4ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerMaxDemand_kW
ST2NSX4ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].ActivePowerTotal_kW
ST2NSX4ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[4].ApparentEnergy_kVAh
ST2NSX4ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerDemand_kVA
ST2NSX4ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparentPowerMaxDemand_kVA
ST2NSX4ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL1_kVA
ST2NSX4ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL2_kVA
ST2NSX4ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerL3_kVA
ST2NSX4ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].ApparetnPowerTotal_kVA
ST2NSX4CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL1
ST2NSX4CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL2
ST2NSX4CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].CosFL3
ST2NSX4CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].CosFTotal
ST2NSX4CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulNegativeActiveEnergy_kWh
ST2NSX4CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[4].CumulPositiveActiveEnergy_kWh
ST2NSX4CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentAvgI1I2I3_A
ST2NSX4CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL1_A
ST2NSX4CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL2_A
ST2NSX4CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandL3_A
ST2NSX4CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL1_A
ST2NSX4CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL2_A
ST2NSX4CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxL3_A
ST2NSX4CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandMaxN_A
ST2NSX4CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentDemandN_A
ST2NSX4CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL1_A
ST2NSX4CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL2_A
ST2NSX4CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentL3_A
ST2NSX4CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].CurrentN_A
ST2NSX4CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI1_P
ST2NSX4CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI2_P
ST2NSX4CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbI3_P
ST2NSX4CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[4].CurrentUnbN_P
ST2NSX4DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].DelovnaEnergija_TEMP
ST2NSX4DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL1_kVAr
ST2NSX4DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL2_kVAr
ST2NSX4DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerL3_kVAr
ST2NSX4DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].DistortionPowerTotal_kVAr
ST2NSX4Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].Frequency_Hz
ST2NSX4FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL1_kVAr
ST2NSX4FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL2_kVAr
ST2NSX4FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerL3_kVAr
ST2NSX4FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].FunReactivePowerTotal_kVAr
ST2NSX4MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL1_kW
ST2NSX4MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL2_kW
ST2NSX4MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerL3_kW
ST2NSX4MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ActivePowerTotal_kW
ST2NSX4MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL1_kVA
ST2NSX4MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL2_kVA
ST2NSX4MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerL3_kVA
ST2NSX4MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ApparetnPowerTotal_kVA
ST2NSX4MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL1
ST2NSX4MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL2
ST2NSX4MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFL3
ST2NSX4MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CosFTotal
ST2NSX4MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentAvgI1I2I3_A
ST2NSX4MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL1_A
ST2NSX4MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL2_A
ST2NSX4MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentL3_A
ST2NSX4MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentMaxL1L2L3N_A
ST2NSX4MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MAX_CurrentN_A
ST2NSX4MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL1_kVAr
ST2NSX4MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL2_kVAr
ST2NSX4MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerL3_kVAr
ST2NSX4MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_DistortionPowerTotal_kVAr
ST2NSX4MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MAX_Frequency_Hz
ST2NSX4MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL1_kVAr
ST2NSX4MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL2_kVAr
ST2NSX4MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerL3_kVAr
ST2NSX4MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_FunReactivePowerTotal_kVAr
ST2NSX4MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL1
ST2NSX4MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL2
ST2NSX4MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorL3
ST2NSX4MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MAX_PowerFactorTotal
ST2NSX4MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL1_kVAr
ST2NSX4MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL2_kVAr
ST2NSX4MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerL3_kVAr
ST2NSX4MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MAX_ReactivePowerTotal_kVAr
ST2NSX4MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI1_P
ST2NSX4MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI2_P
ST2NSX4MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDI3_P
ST2NSX4MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV12_P
ST2NSX4MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV1N_P
ST2NSX4MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV23_P
ST2NSX4MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV2N_P
ST2NSX4MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV31_P
ST2NSX4MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_THDV3N_P
ST2NSX4MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToN_V
ST2NSX4MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageAvgPhToPh_V
ST2NSX4MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV12_P
ST2NSX4MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV1N_P
ST2NSX4MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV23_P
ST2NSX4MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV2N_P
ST2NSX4MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV31_P
ST2NSX4MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageUnbV3N_P
ST2NSX4MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV12_V
ST2NSX4MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV1N_V
ST2NSX4MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV23_V
ST2NSX4MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV2N_V
ST2NSX4MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV31_V
ST2NSX4MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MAX_VoltageV3N_V
ST2NSX4MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL1_kW
ST2NSX4MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL2_kW
ST2NSX4MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerL3_kW
ST2NSX4MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ActivePowerTotal_kW
ST2NSX4MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL1_kVA
ST2NSX4MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL2_kVA
ST2NSX4MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerL3_kVA
ST2NSX4MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ApparetnPowerTotal_kVA
ST2NSX4MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL1
ST2NSX4MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL2
ST2NSX4MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFL3
ST2NSX4MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CosFTotal
ST2NSX4MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentAvgI1I2I3_A
ST2NSX4MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL1_A
ST2NSX4MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL2_A
ST2NSX4MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentL3_A
ST2NSX4MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentMaxL1L2L3N_A
ST2NSX4MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[4].MIN_CurrentN_A
ST2NSX4MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL1_kVAr
ST2NSX4MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL2_kVAr
ST2NSX4MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerL3_kVAr
ST2NSX4MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_DistortionPowerTotal_kVAr
ST2NSX4MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[4].MIN_Frequency_Hz
ST2NSX4MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL1_kVAr
ST2NSX4MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL2_kVAr
ST2NSX4MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerL3_kVAr
ST2NSX4MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_FunReactivePowerTotal_kVAr
ST2NSX4MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL1
ST2NSX4MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL2
ST2NSX4MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorL3
ST2NSX4MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].MIN_PowerFactorTotal
ST2NSX4MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL1_kVAr
ST2NSX4MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL2_kVAr
ST2NSX4MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerL3_kVAr
ST2NSX4MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].MIN_ReactivePowerTotal_kVAr
ST2NSX4MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI1_P
ST2NSX4MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI2_P
ST2NSX4MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDI3_P
ST2NSX4MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV12_P
ST2NSX4MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV1N_P
ST2NSX4MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV23_P
ST2NSX4MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV2N_P
ST2NSX4MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV31_P
ST2NSX4MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_THDV3N_P
ST2NSX4MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToN_V
ST2NSX4MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageAvgPhToPh_V
ST2NSX4MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV12_P
ST2NSX4MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV1N_P
ST2NSX4MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV23_P
ST2NSX4MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV2N_P
ST2NSX4MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV31_P
ST2NSX4MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageUnbV3N_P
ST2NSX4MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV12_V
ST2NSX4MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV1N_V
ST2NSX4MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV23_V
ST2NSX4MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV2N_V
ST2NSX4MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV31_V
ST2NSX4MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].MIN_VoltageV3N_V
ST2NSX4PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL1
ST2NSX4PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL2
ST2NSX4PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorL3
ST2NSX4PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[4].PowerFactorTotal
ST2NSX4RazEner_D | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D
ST2NSX4RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_SCADA
ST2NSX4RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_D_TEMP
ST2NSX4RazEner_M | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M
ST2NSX4RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_SCADA
ST2NSX4RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_M_TEMP
ST2NSX4RazEner_T | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T
ST2NSX4RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_SCADA
ST2NSX4RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[4].RazEner_T_TEMP
ST2NSX4ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveEnergy_kVArh
ST2NSX4ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactiveNegativeEnergy_kVArh
ST2NSX4ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePositiveEnergy_kVArh
ST2NSX4ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerDemand_kVAr
ST2NSX4ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL1_kVAr
ST2NSX4ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL2_kVAr
ST2NSX4ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerL3_kVAr
ST2NSX4ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerMaxDemand_kVAr
ST2NSX4ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[4].ReactivePowerTotal_kVAr
ST2NSX4THDI1_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI1_P
ST2NSX4THDI2_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI2_P
ST2NSX4THDI3_P | REAL | IOD_ST2 | ST2:.NSX[4].THDI3_P
ST2NSX4THDV12_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV12_P
ST2NSX4THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV1N_P
ST2NSX4THDV23_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV23_P
ST2NSX4THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV2N_P
ST2NSX4THDV31_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV31_P
ST2NSX4THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].THDV3N_P
ST2NSX4VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToN_V
ST2NSX4VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageAvgPhToPh_V
ST2NSX4VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV12_P
ST2NSX4VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV1N_P
ST2NSX4VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV23_P
ST2NSX4VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV2N_P
ST2NSX4VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV31_P
ST2NSX4VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[4].VoltageUnbV3N_P
ST2NSX4VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV12_V
ST2NSX4VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV1N_V
ST2NSX4VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV23_V
ST2NSX4VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV2N_V
ST2NSX4VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV31_V
ST2NSX4VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[4].VoltageV3N_V
ST2NSX5ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveEnergy_kWh
ST2NSX5ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActiveNegativeEnergy_kWh
ST2NSX5ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].ActivePositiveEnergy_kWh
ST2NSX5ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerDemand_kW
ST2NSX5ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL1_kW
ST2NSX5ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL2_kW
ST2NSX5ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerL3_kW
ST2NSX5ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerMaxDemand_kW
ST2NSX5ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].ActivePowerTotal_kW
ST2NSX5ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[5].ApparentEnergy_kVAh
ST2NSX5ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerDemand_kVA
ST2NSX5ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparentPowerMaxDemand_kVA
ST2NSX5ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL1_kVA
ST2NSX5ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL2_kVA
ST2NSX5ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerL3_kVA
ST2NSX5ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].ApparetnPowerTotal_kVA
ST2NSX5CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL1
ST2NSX5CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL2
ST2NSX5CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].CosFL3
ST2NSX5CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].CosFTotal
ST2NSX5CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulNegativeActiveEnergy_kWh
ST2NSX5CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[5].CumulPositiveActiveEnergy_kWh
ST2NSX5CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentAvgI1I2I3_A
ST2NSX5CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL1_A
ST2NSX5CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL2_A
ST2NSX5CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandL3_A
ST2NSX5CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL1_A
ST2NSX5CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL2_A
ST2NSX5CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxL3_A
ST2NSX5CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandMaxN_A
ST2NSX5CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentDemandN_A
ST2NSX5CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL1_A
ST2NSX5CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL2_A
ST2NSX5CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentL3_A
ST2NSX5CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].CurrentN_A
ST2NSX5CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI1_P
ST2NSX5CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI2_P
ST2NSX5CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbI3_P
ST2NSX5CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[5].CurrentUnbN_P
ST2NSX5DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].DelovnaEnergija_TEMP
ST2NSX5DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL1_kVAr
ST2NSX5DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL2_kVAr
ST2NSX5DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerL3_kVAr
ST2NSX5DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].DistortionPowerTotal_kVAr
ST2NSX5Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].Frequency_Hz
ST2NSX5FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL1_kVAr
ST2NSX5FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL2_kVAr
ST2NSX5FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerL3_kVAr
ST2NSX5FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].FunReactivePowerTotal_kVAr
ST2NSX5MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL1_kW
ST2NSX5MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL2_kW
ST2NSX5MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerL3_kW
ST2NSX5MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ActivePowerTotal_kW
ST2NSX5MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL1_kVA
ST2NSX5MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL2_kVA
ST2NSX5MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerL3_kVA
ST2NSX5MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ApparetnPowerTotal_kVA
ST2NSX5MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL1
ST2NSX5MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL2
ST2NSX5MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFL3
ST2NSX5MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CosFTotal
ST2NSX5MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentAvgI1I2I3_A
ST2NSX5MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL1_A
ST2NSX5MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL2_A
ST2NSX5MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentL3_A
ST2NSX5MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentMaxL1L2L3N_A
ST2NSX5MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MAX_CurrentN_A
ST2NSX5MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL1_kVAr
ST2NSX5MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL2_kVAr
ST2NSX5MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerL3_kVAr
ST2NSX5MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_DistortionPowerTotal_kVAr
ST2NSX5MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MAX_Frequency_Hz
ST2NSX5MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL1_kVAr
ST2NSX5MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL2_kVAr
ST2NSX5MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerL3_kVAr
ST2NSX5MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_FunReactivePowerTotal_kVAr
ST2NSX5MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL1
ST2NSX5MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL2
ST2NSX5MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorL3
ST2NSX5MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MAX_PowerFactorTotal
ST2NSX5MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL1_kVAr
ST2NSX5MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL2_kVAr
ST2NSX5MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerL3_kVAr
ST2NSX5MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MAX_ReactivePowerTotal_kVAr
ST2NSX5MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI1_P
ST2NSX5MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI2_P
ST2NSX5MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDI3_P
ST2NSX5MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV12_P
ST2NSX5MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV1N_P
ST2NSX5MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV23_P
ST2NSX5MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV2N_P
ST2NSX5MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV31_P
ST2NSX5MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_THDV3N_P
ST2NSX5MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToN_V
ST2NSX5MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageAvgPhToPh_V
ST2NSX5MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV12_P
ST2NSX5MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV1N_P
ST2NSX5MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV23_P
ST2NSX5MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV2N_P
ST2NSX5MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV31_P
ST2NSX5MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageUnbV3N_P
ST2NSX5MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV12_V
ST2NSX5MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV1N_V
ST2NSX5MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV23_V
ST2NSX5MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV2N_V
ST2NSX5MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV31_V
ST2NSX5MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MAX_VoltageV3N_V
ST2NSX5MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL1_kW
ST2NSX5MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL2_kW
ST2NSX5MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerL3_kW
ST2NSX5MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ActivePowerTotal_kW
ST2NSX5MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL1_kVA
ST2NSX5MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL2_kVA
ST2NSX5MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerL3_kVA
ST2NSX5MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ApparetnPowerTotal_kVA
ST2NSX5MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL1
ST2NSX5MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL2
ST2NSX5MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFL3
ST2NSX5MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CosFTotal
ST2NSX5MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentAvgI1I2I3_A
ST2NSX5MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL1_A
ST2NSX5MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL2_A
ST2NSX5MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentL3_A
ST2NSX5MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentMaxL1L2L3N_A
ST2NSX5MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[5].MIN_CurrentN_A
ST2NSX5MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL1_kVAr
ST2NSX5MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL2_kVAr
ST2NSX5MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerL3_kVAr
ST2NSX5MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_DistortionPowerTotal_kVAr
ST2NSX5MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[5].MIN_Frequency_Hz
ST2NSX5MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL1_kVAr
ST2NSX5MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL2_kVAr
ST2NSX5MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerL3_kVAr
ST2NSX5MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_FunReactivePowerTotal_kVAr
ST2NSX5MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL1
ST2NSX5MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL2
ST2NSX5MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorL3
ST2NSX5MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].MIN_PowerFactorTotal
ST2NSX5MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL1_kVAr
ST2NSX5MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL2_kVAr
ST2NSX5MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerL3_kVAr
ST2NSX5MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].MIN_ReactivePowerTotal_kVAr
ST2NSX5MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI1_P
ST2NSX5MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI2_P
ST2NSX5MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDI3_P
ST2NSX5MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV12_P
ST2NSX5MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV1N_P
ST2NSX5MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV23_P
ST2NSX5MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV2N_P
ST2NSX5MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV31_P
ST2NSX5MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_THDV3N_P
ST2NSX5MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToN_V
ST2NSX5MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageAvgPhToPh_V
ST2NSX5MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV12_P
ST2NSX5MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV1N_P
ST2NSX5MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV23_P
ST2NSX5MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV2N_P
ST2NSX5MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV31_P
ST2NSX5MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageUnbV3N_P
ST2NSX5MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV12_V
ST2NSX5MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV1N_V
ST2NSX5MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV23_V
ST2NSX5MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV2N_V
ST2NSX5MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV31_V
ST2NSX5MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].MIN_VoltageV3N_V
ST2NSX5PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL1
ST2NSX5PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL2
ST2NSX5PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorL3
ST2NSX5PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[5].PowerFactorTotal
ST2NSX5RazEner_D | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D
ST2NSX5RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_SCADA
ST2NSX5RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_D_TEMP
ST2NSX5RazEner_M | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M
ST2NSX5RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_SCADA
ST2NSX5RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_M_TEMP
ST2NSX5RazEner_T | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T
ST2NSX5RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_SCADA
ST2NSX5RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[5].RazEner_T_TEMP
ST2NSX5ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveEnergy_kVArh
ST2NSX5ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactiveNegativeEnergy_kVArh
ST2NSX5ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePositiveEnergy_kVArh
ST2NSX5ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerDemand_kVAr
ST2NSX5ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL1_kVAr
ST2NSX5ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL2_kVAr
ST2NSX5ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerL3_kVAr
ST2NSX5ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerMaxDemand_kVAr
ST2NSX5ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[5].ReactivePowerTotal_kVAr
ST2NSX5THDI1_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI1_P
ST2NSX5THDI2_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI2_P
ST2NSX5THDI3_P | REAL | IOD_ST2 | ST2:.NSX[5].THDI3_P
ST2NSX5THDV12_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV12_P
ST2NSX5THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV1N_P
ST2NSX5THDV23_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV23_P
ST2NSX5THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV2N_P
ST2NSX5THDV31_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV31_P
ST2NSX5THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].THDV3N_P
ST2NSX5VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToN_V
ST2NSX5VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageAvgPhToPh_V
ST2NSX5VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV12_P
ST2NSX5VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV1N_P
ST2NSX5VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV23_P
ST2NSX5VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV2N_P
ST2NSX5VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV31_P
ST2NSX5VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[5].VoltageUnbV3N_P
ST2NSX5VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV12_V
ST2NSX5VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV1N_V
ST2NSX5VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV23_V
ST2NSX5VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV2N_V
ST2NSX5VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV31_V
ST2NSX5VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[5].VoltageV3N_V
ST2NSX6ActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveEnergy_kWh
ST2NSX6ActiveNegativeEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActiveNegativeEnergy_kWh
ST2NSX6ActivePositiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].ActivePositiveEnergy_kWh
ST2NSX6ActivePowerDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerDemand_kW
ST2NSX6ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL1_kW
ST2NSX6ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL2_kW
ST2NSX6ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerL3_kW
ST2NSX6ActivePowerMaxDemand_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerMaxDemand_kW
ST2NSX6ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].ActivePowerTotal_kW
ST2NSX6ApparentEnergy_kVAh | REAL | IOD_ST2 | ST2:.NSX[6].ApparentEnergy_kVAh
ST2NSX6ApparentPowerDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerDemand_kVA
ST2NSX6ApparentPowerMaxDemand_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparentPowerMaxDemand_kVA
ST2NSX6ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL1_kVA
ST2NSX6ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL2_kVA
ST2NSX6ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerL3_kVA
ST2NSX6ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].ApparetnPowerTotal_kVA
ST2NSX6CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL1
ST2NSX6CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL2
ST2NSX6CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].CosFL3
ST2NSX6CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].CosFTotal
ST2NSX6CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulNegativeActiveEnergy_kWh
ST2NSX6CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2 | ST2:.NSX[6].CumulPositiveActiveEnergy_kWh
ST2NSX6CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentAvgI1I2I3_A
ST2NSX6CurrentDemandL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL1_A
ST2NSX6CurrentDemandL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL2_A
ST2NSX6CurrentDemandL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandL3_A
ST2NSX6CurrentDemandMaxL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL1_A
ST2NSX6CurrentDemandMaxL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL2_A
ST2NSX6CurrentDemandMaxL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxL3_A
ST2NSX6CurrentDemandMaxN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandMaxN_A
ST2NSX6CurrentDemandN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentDemandN_A
ST2NSX6CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL1_A
ST2NSX6CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL2_A
ST2NSX6CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentL3_A
ST2NSX6CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].CurrentN_A
ST2NSX6CurrentUnbI1_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI1_P
ST2NSX6CurrentUnbI2_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI2_P
ST2NSX6CurrentUnbI3_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbI3_P
ST2NSX6CurrentUnbN_P | REAL | IOD_ST2 | ST2:.NSX[6].CurrentUnbN_P
ST2NSX6DelovnaEnergija_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].DelovnaEnergija_TEMP
ST2NSX6DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL1_kVAr
ST2NSX6DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL2_kVAr
ST2NSX6DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerL3_kVAr
ST2NSX6DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].DistortionPowerTotal_kVAr
ST2NSX6Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].Frequency_Hz
ST2NSX6FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL1_kVAr
ST2NSX6FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL2_kVAr
ST2NSX6FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerL3_kVAr
ST2NSX6FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].FunReactivePowerTotal_kVAr
ST2NSX6MAX_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL1_kW
ST2NSX6MAX_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL2_kW
ST2NSX6MAX_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerL3_kW
ST2NSX6MAX_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ActivePowerTotal_kW
ST2NSX6MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL1_kVA
ST2NSX6MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL2_kVA
ST2NSX6MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerL3_kVA
ST2NSX6MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ApparetnPowerTotal_kVA
ST2NSX6MAX_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL1
ST2NSX6MAX_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL2
ST2NSX6MAX_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFL3
ST2NSX6MAX_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CosFTotal
ST2NSX6MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentAvgI1I2I3_A
ST2NSX6MAX_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL1_A
ST2NSX6MAX_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL2_A
ST2NSX6MAX_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentL3_A
ST2NSX6MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentMaxL1L2L3N_A
ST2NSX6MAX_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MAX_CurrentN_A
ST2NSX6MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL1_kVAr
ST2NSX6MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL2_kVAr
ST2NSX6MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerL3_kVAr
ST2NSX6MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_DistortionPowerTotal_kVAr
ST2NSX6MAX_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MAX_Frequency_Hz
ST2NSX6MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL1_kVAr
ST2NSX6MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL2_kVAr
ST2NSX6MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerL3_kVAr
ST2NSX6MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_FunReactivePowerTotal_kVAr
ST2NSX6MAX_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL1
ST2NSX6MAX_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL2
ST2NSX6MAX_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorL3
ST2NSX6MAX_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MAX_PowerFactorTotal
ST2NSX6MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL1_kVAr
ST2NSX6MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL2_kVAr
ST2NSX6MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerL3_kVAr
ST2NSX6MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MAX_ReactivePowerTotal_kVAr
ST2NSX6MAX_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI1_P
ST2NSX6MAX_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI2_P
ST2NSX6MAX_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDI3_P
ST2NSX6MAX_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV12_P
ST2NSX6MAX_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV1N_P
ST2NSX6MAX_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV23_P
ST2NSX6MAX_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV2N_P
ST2NSX6MAX_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV31_P
ST2NSX6MAX_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_THDV3N_P
ST2NSX6MAX_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToN_V
ST2NSX6MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageAvgPhToPh_V
ST2NSX6MAX_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV12_P
ST2NSX6MAX_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV1N_P
ST2NSX6MAX_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV23_P
ST2NSX6MAX_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV2N_P
ST2NSX6MAX_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV31_P
ST2NSX6MAX_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageUnbV3N_P
ST2NSX6MAX_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV12_V
ST2NSX6MAX_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV1N_V
ST2NSX6MAX_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV23_V
ST2NSX6MAX_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV2N_V
ST2NSX6MAX_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV31_V
ST2NSX6MAX_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MAX_VoltageV3N_V
ST2NSX6MIN_ActivePowerL1_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL1_kW
ST2NSX6MIN_ActivePowerL2_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL2_kW
ST2NSX6MIN_ActivePowerL3_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerL3_kW
ST2NSX6MIN_ActivePowerTotal_kW | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ActivePowerTotal_kW
ST2NSX6MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL1_kVA
ST2NSX6MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL2_kVA
ST2NSX6MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerL3_kVA
ST2NSX6MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ApparetnPowerTotal_kVA
ST2NSX6MIN_CosFL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL1
ST2NSX6MIN_CosFL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL2
ST2NSX6MIN_CosFL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFL3
ST2NSX6MIN_CosFTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CosFTotal
ST2NSX6MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentAvgI1I2I3_A
ST2NSX6MIN_CurrentL1_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL1_A
ST2NSX6MIN_CurrentL2_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL2_A
ST2NSX6MIN_CurrentL3_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentL3_A
ST2NSX6MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentMaxL1L2L3N_A
ST2NSX6MIN_CurrentN_A | REAL | IOD_ST2 | ST2:.NSX[6].MIN_CurrentN_A
ST2NSX6MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL1_kVAr
ST2NSX6MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL2_kVAr
ST2NSX6MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerL3_kVAr
ST2NSX6MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_DistortionPowerTotal_kVAr
ST2NSX6MIN_Frequency_Hz | REAL | IOD_ST2 | ST2:.NSX[6].MIN_Frequency_Hz
ST2NSX6MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL1_kVAr
ST2NSX6MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL2_kVAr
ST2NSX6MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerL3_kVAr
ST2NSX6MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_FunReactivePowerTotal_kVAr
ST2NSX6MIN_PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL1
ST2NSX6MIN_PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL2
ST2NSX6MIN_PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorL3
ST2NSX6MIN_PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].MIN_PowerFactorTotal
ST2NSX6MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL1_kVAr
ST2NSX6MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL2_kVAr
ST2NSX6MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerL3_kVAr
ST2NSX6MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].MIN_ReactivePowerTotal_kVAr
ST2NSX6MIN_THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI1_P
ST2NSX6MIN_THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI2_P
ST2NSX6MIN_THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDI3_P
ST2NSX6MIN_THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV12_P
ST2NSX6MIN_THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV1N_P
ST2NSX6MIN_THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV23_P
ST2NSX6MIN_THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV2N_P
ST2NSX6MIN_THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV31_P
ST2NSX6MIN_THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_THDV3N_P
ST2NSX6MIN_VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToN_V
ST2NSX6MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageAvgPhToPh_V
ST2NSX6MIN_VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV12_P
ST2NSX6MIN_VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV1N_P
ST2NSX6MIN_VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV23_P
ST2NSX6MIN_VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV2N_P
ST2NSX6MIN_VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV31_P
ST2NSX6MIN_VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageUnbV3N_P
ST2NSX6MIN_VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV12_V
ST2NSX6MIN_VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV1N_V
ST2NSX6MIN_VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV23_V
ST2NSX6MIN_VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV2N_V
ST2NSX6MIN_VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV31_V
ST2NSX6MIN_VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].MIN_VoltageV3N_V
ST2NSX6PowerFactorL1 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL1
ST2NSX6PowerFactorL2 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL2
ST2NSX6PowerFactorL3 | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorL3
ST2NSX6PowerFactorTotal | REAL | IOD_ST2 | ST2:.NSX[6].PowerFactorTotal
ST2NSX6RazEner_D | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D
ST2NSX6RazEner_D_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_SCADA
ST2NSX6RazEner_D_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_D_TEMP
ST2NSX6RazEner_M | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M
ST2NSX6RazEner_M_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_SCADA
ST2NSX6RazEner_M_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_M_TEMP
ST2NSX6RazEner_T | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T
ST2NSX6RazEner_T_SCADA | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_SCADA
ST2NSX6RazEner_T_TEMP | REAL | IOD_ST2 | ST2:.NSX[6].RazEner_T_TEMP
ST2NSX6ReactiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveEnergy_kVArh
ST2NSX6ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactiveNegativeEnergy_kVArh
ST2NSX6ReactivePositiveEnergy_kVArh | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePositiveEnergy_kVArh
ST2NSX6ReactivePowerDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerDemand_kVAr
ST2NSX6ReactivePowerL1_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL1_kVAr
ST2NSX6ReactivePowerL2_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL2_kVAr
ST2NSX6ReactivePowerL3_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerL3_kVAr
ST2NSX6ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerMaxDemand_kVAr
ST2NSX6ReactivePowerTotal_kVAr | REAL | IOD_ST2 | ST2:.NSX[6].ReactivePowerTotal_kVAr
ST2NSX6THDI1_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI1_P
ST2NSX6THDI2_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI2_P
ST2NSX6THDI3_P | REAL | IOD_ST2 | ST2:.NSX[6].THDI3_P
ST2NSX6THDV12_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV12_P
ST2NSX6THDV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV1N_P
ST2NSX6THDV23_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV23_P
ST2NSX6THDV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV2N_P
ST2NSX6THDV31_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV31_P
ST2NSX6THDV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].THDV3N_P
ST2NSX6VoltageAvgPhToN_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToN_V
ST2NSX6VoltageAvgPhToPh_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageAvgPhToPh_V
ST2NSX6VoltageUnbV12_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV12_P
ST2NSX6VoltageUnbV1N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV1N_P
ST2NSX6VoltageUnbV23_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV23_P
ST2NSX6VoltageUnbV2N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV2N_P
ST2NSX6VoltageUnbV31_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV31_P
ST2NSX6VoltageUnbV3N_P | REAL | IOD_ST2 | ST2:.NSX[6].VoltageUnbV3N_P
ST2NSX6VoltageV12_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV12_V
ST2NSX6VoltageV1N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV1N_V
ST2NSX6VoltageV23_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV23_V
ST2NSX6VoltageV2N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV2N_V
ST2NSX6VoltageV31_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV31_V
ST2NSX6VoltageV3N_V | REAL | IOD_ST2 | ST2:.NSX[6].VoltageV3N_V
ST2PMMVirACurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[10]
ST2PMMVirACurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[11]
ST2PMMVirACurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[12]
ST2PMMVirACurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[13]
ST2PMMVirACurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[14]
ST2PMMVirACurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[15]
ST2PMMVirACurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[16]
ST2PMMVirACurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[17]
ST2PMMVirACurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[18]
ST2PMMVirACurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[19]
ST2PMMVirACurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[1]
ST2PMMVirACurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[20]
ST2PMMVirACurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[21]
ST2PMMVirACurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[22]
ST2PMMVirACurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[23]
ST2PMMVirACurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[24]
ST2PMMVirACurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[25]
ST2PMMVirACurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[26]
ST2PMMVirACurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[27]
ST2PMMVirACurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[28]
ST2PMMVirACurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[29]
ST2PMMVirACurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[2]
ST2PMMVirACurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[30]
ST2PMMVirACurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[31]
ST2PMMVirACurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[32]
ST2PMMVirACurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[33]
ST2PMMVirACurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[34]
ST2PMMVirACurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[35]
ST2PMMVirACurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[36]
ST2PMMVirACurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[37]
ST2PMMVirACurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[38]
ST2PMMVirACurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[39]
ST2PMMVirACurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[3]
ST2PMMVirACurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[40]
ST2PMMVirACurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[41]
ST2PMMVirACurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[42]
ST2PMMVirACurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[43]
ST2PMMVirACurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[44]
ST2PMMVirACurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[4]
ST2PMMVirACurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[5]
ST2PMMVirACurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[6]
ST2PMMVirACurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[7]
ST2PMMVirACurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[8]
ST2PMMVirACurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirA.Current[9]
ST2PMMVirA_fsys | REAL | IOD_ST2 | ST2:.PMM.VirA_fsys
ST2PMMVirA_Isys | REAL | IOD_ST2 | ST2:.PMM.VirA_Isys
ST2PMMVirA_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirA_PFsys
ST2PMMVirA_Psys | REAL | IOD_ST2 | ST2:.PMM.VirA_Psys
ST2PMMVirA_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirA_Qsys
ST2PMMVirA_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirA_Ssys
ST2PMMVirA_Usys | REAL | IOD_ST2 | ST2:.PMM.VirA_Usys
ST2PMMVirAActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirAActiveEnergyConsumed_kWh
ST2PMMVirAActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseA_kW
ST2PMMVirAActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseB_kW
ST2PMMVirAActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirAActivePowerPhaseC_kW
ST2PMMVirAAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseA
ST2PMMVirAAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseB
ST2PMMVirAAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAAparentPowerPhaseC
ST2PMMVirACurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseA_A
ST2PMMVirACurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseB_A
ST2PMMVirACurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirACurrentInPhaseC_A
ST2PMMVirAReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirAReactiveEnergyConsumed_kVARh
ST2PMMVirAReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseA
ST2PMMVirAReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseB
ST2PMMVirAReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirAReactivePowerPhaseC
ST2PMMVirAVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAB_V
ST2PMMVirAVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseAN_V
ST2PMMVirAVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBC_V
ST2PMMVirAVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseBN_V
ST2PMMVirAVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCA_V
ST2PMMVirAVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirAVoltageBetweenPhaseCN_V
ST2PMMVirBCurrent10 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[10]
ST2PMMVirBCurrent11 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[11]
ST2PMMVirBCurrent12 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[12]
ST2PMMVirBCurrent13 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[13]
ST2PMMVirBCurrent14 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[14]
ST2PMMVirBCurrent15 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[15]
ST2PMMVirBCurrent16 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[16]
ST2PMMVirBCurrent17 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[17]
ST2PMMVirBCurrent18 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[18]
ST2PMMVirBCurrent19 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[19]
ST2PMMVirBCurrent1 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[1]
ST2PMMVirBCurrent20 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[20]
ST2PMMVirBCurrent21 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[21]
ST2PMMVirBCurrent22 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[22]
ST2PMMVirBCurrent23 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[23]
ST2PMMVirBCurrent24 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[24]
ST2PMMVirBCurrent25 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[25]
ST2PMMVirBCurrent26 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[26]
ST2PMMVirBCurrent27 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[27]
ST2PMMVirBCurrent28 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[28]
ST2PMMVirBCurrent29 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[29]
ST2PMMVirBCurrent2 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[2]
ST2PMMVirBCurrent30 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[30]
ST2PMMVirBCurrent31 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[31]
ST2PMMVirBCurrent32 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[32]
ST2PMMVirBCurrent33 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[33]
ST2PMMVirBCurrent34 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[34]
ST2PMMVirBCurrent35 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[35]
ST2PMMVirBCurrent36 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[36]
ST2PMMVirBCurrent37 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[37]
ST2PMMVirBCurrent38 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[38]
ST2PMMVirBCurrent39 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[39]
ST2PMMVirBCurrent3 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[3]
ST2PMMVirBCurrent40 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[40]
ST2PMMVirBCurrent41 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[41]
ST2PMMVirBCurrent42 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[42]
ST2PMMVirBCurrent43 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[43]
ST2PMMVirBCurrent44 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[44]
ST2PMMVirBCurrent4 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[4]
ST2PMMVirBCurrent5 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[5]
ST2PMMVirBCurrent6 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[6]
ST2PMMVirBCurrent7 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[7]
ST2PMMVirBCurrent8 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[8]
ST2PMMVirBCurrent9 | REAL | IOD_ST2 | ST2:.PMM.VirB.Current[9]
ST2PMMVirB_fsys | REAL | IOD_ST2 | ST2:.PMM.VirB_fsys
ST2PMMVirB_Isys | REAL | IOD_ST2 | ST2:.PMM.VirB_Isys
ST2PMMVirB_PFsys | REAL | IOD_ST2 | ST2:.PMM.VirB_PFsys
ST2PMMVirB_Psys | REAL | IOD_ST2 | ST2:.PMM.VirB_Psys
ST2PMMVirB_Qsys | REAL | IOD_ST2 | ST2:.PMM.VirB_Qsys
ST2PMMVirB_Ssys | REAL | IOD_ST2 | ST2:.PMM.VirB_Ssys
ST2PMMVirB_Usys | REAL | IOD_ST2 | ST2:.PMM.VirB_Usys
ST2PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_ST2 | ST2:.PMM.VirBActiveEnergyConsumed_kWh
ST2PMMVirBActivePowerPhaseA_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseA_kW
ST2PMMVirBActivePowerPhaseB_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseB_kW
ST2PMMVirBActivePowerPhaseC_kW | REAL | IOD_ST2 | ST2:.PMM.VirBActivePowerPhaseC_kW
ST2PMMVirBAparentPowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseA
ST2PMMVirBAparentPowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseB
ST2PMMVirBAparentPowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBAparentPowerPhaseC
ST2PMMVirBCurrentInPhaseA_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseA_A
ST2PMMVirBCurrentInPhaseB_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseB_A
ST2PMMVirBCurrentInPhaseC_A | REAL | IOD_ST2 | ST2:.PMM.VirBCurrentInPhaseC_A
ST2PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_ST2 | ST2:.PMM.VirBReactiveEnergyConsumed_kVARh
ST2PMMVirBReactivePowerPhaseA | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseA
ST2PMMVirBReactivePowerPhaseB | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseB
ST2PMMVirBReactivePowerPhaseC | REAL | IOD_ST2 | ST2:.PMM.VirBReactivePowerPhaseC
ST2PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAB_V
ST2PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseAN_V
ST2PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBC_V
ST2PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseBN_V
ST2PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCA_V
ST2PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_ST2 | ST2:.PMM.VirBVoltageBetweenPhaseCN_V
ST2Date_Time0 | STRING | IOD_ST2 | ST2:.Date_Time[0]
ST2Date_Time1 | STRING | IOD_ST2 | ST2:.Date_Time[1]
ST2Date_Time2 | STRING | IOD_ST2 | ST2:.Date_Time[2]
ST2Date_Time3 | STRING | IOD_ST2 | ST2:.Date_Time[3]
ST2kom_nast_cas_izpada | STRING | IOD_ST2 | ST2:.kom_nast_cas_izpada
ST2UserCurrentName | STRING | IOD_ST2 | ST2:.UserCurrentName
ST2UserDisplay | STRING | IOD_ST2 | ST2:.UserDisplay
ST2NSX1StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[1].StatusSwitch
ST2NSX2StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[2].StatusSwitch
ST2NSX3StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[3].StatusSwitch
ST2NSX4StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[4].StatusSwitch
ST2NSX5StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[5].StatusSwitch
ST2NSX6StatusSwitch | UINT | IOD_ST2 | ST2:.NSX[6].StatusSwitch
ST2PMMVirAAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_60to80
ST2PMMVirAAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C01_16_over80
ST2PMMVirAAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_60to80
ST2PMMVirAAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C17_32_over80
ST2PMMVirAAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_60to80
ST2PMMVirAAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirAAlarmPhase.C33_44_over80
ST2PMMVirBAlarmPhase_C01_16_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_60to80
ST2PMMVirBAlarmPhase_C01_16_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C01_16_over80
ST2PMMVirBAlarmPhase_C17_32_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_60to80
ST2PMMVirBAlarmPhase_C17_32_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C17_32_over80
ST2PMMVirBAlarmPhase_C33_44_60to80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_60to80
ST2PMMVirBAlarmPhase_C33_44_over80 | UINT | IOD_ST2 | ST2:.PMM.VirBAlarmPhase.C33_44_over80

## variable_3
ST2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_ST2_TCP | 1 | 00001 | Circ_Vpis_Dnevne_energija_scada1
ST2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_ST2_TCP | 2 | 00002 | Circ_Vpis_Dnevne_energija_scada2
ST2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_ST2_TCP | 3 | 00003 | Circ_Vpis_Mesecna_energija_scada1
ST2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_ST2_TCP | 4 | 00004 | Circ_Vpis_Mesecna_energija_scada2
ST2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_ST2_TCP | 5 | 00005 | Circ_Vpis_Tedenska_energija_scada1
ST2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_ST2_TCP | 6 | 00006 | Circ_Vpis_Tedenska_energija_scada2
ST2ComError | DIGITAL | IOD_ST2_TCP | 7 | 00007 | ComError
ST2ComSCADA | DIGITAL | IOD_ST2_TCP | 8 | 00008 | ComSCADA
ST2ComSCADA1 | DIGITAL | IOD_ST2_TCP | 9 | 00009 | ComSCADA1
ST2ComSCADA2 | DIGITAL | IOD_ST2_TCP | 10 | 00010 | ComSCADA2
ST2ComSCADA3 | DIGITAL | IOD_ST2_TCP | 11 | 00011 | ComSCADA3
ST2DI2_I10_Rezerva3 | DIGITAL | IOD_ST2_TCP | 12 | 00012 | DI2_I10_Rezerva3
ST2DI2_I11_Rezerva4 | DIGITAL | IOD_ST2_TCP | 13 | 00013 | DI2_I11_Rezerva4
ST2DI2_I12_Rezerva5 | DIGITAL | IOD_ST2_TCP | 14 | 00014 | DI2_I12_Rezerva5
ST2DI2_I13_Rezerva6 | DIGITAL | IOD_ST2_TCP | 15 | 00015 | DI2_I13_Rezerva6
ST2DI2_I8_Rezerva1 | DIGITAL | IOD_ST2_TCP | 16 | 00016 | DI2_I8_Rezerva1
ST2DI2_I9_Rezerva2 | DIGITAL | IOD_ST2_TCP | 17 | 00017 | DI2_I9_Rezerva2
ST2DI_SB_IROGSM21_Q0_Izkljucen | DIGITAL | IOD_ST2_TCP | 18 | 00018 | DI_SB_IROGSM21_Q0_Izkljucen
ST2DI_SB_IROGSM21_Q0_Vkljucen | DIGITAL | IOD_ST2_TCP | 19 | 00019 | DI_SB_IROGSM21_Q0_Vkljucen
ST2DI_SB_IROGSM21_Q11_Izkljucen | DIGITAL | IOD_ST2_TCP | 20 | 00020 | DI_SB_IROGSM21_Q11_Izkljucen
ST2DI_SB_IROGSM21_Q11_Vkljucen | DIGITAL | IOD_ST2_TCP | 21 | 00021 | DI_SB_IROGSM21_Q11_Vkljucen
ST2DI_SB_IROGSM21_Q12_Izkljucen | DIGITAL | IOD_ST2_TCP | 22 | 00022 | DI_SB_IROGSM21_Q12_Izkljucen
ST2DI_SB_IROGSM21_Q12_Vkljucen | DIGITAL | IOD_ST2_TCP | 23 | 00023 | DI_SB_IROGSM21_Q12_Vkljucen
ST2DI_SB_IROGSM21_Q13_Izpad | DIGITAL | IOD_ST2_TCP | 24 | 00024 | DI_SB_IROGSM21_Q13_Izpad
ST2DI_SB_IROGSM21_Q13_Vkljucen | DIGITAL | IOD_ST2_TCP | 25 | 00025 | DI_SB_IROGSM21_Q13_Vkljucen
ST2DI_SB_IROGSM21_Q14_Izpad | DIGITAL | IOD_ST2_TCP | 26 | 00026 | DI_SB_IROGSM21_Q14_Izpad
ST2DI_SB_IROGSM21_Q14_Vkljucen | DIGITAL | IOD_ST2_TCP | 27 | 00027 | DI_SB_IROGSM21_Q14_Vkljucen
ST2DI_SB_IROGSM21_Q15_Izpad | DIGITAL | IOD_ST2_TCP | 28 | 00028 | DI_SB_IROGSM21_Q15_Izpad
ST2DI_SB_IROGSM21_Q15_Vkljucen | DIGITAL | IOD_ST2_TCP | 29 | 00029 | DI_SB_IROGSM21_Q15_Vkljucen
ST2DI_SB_IROGSM21_SkupnaNapaka | DIGITAL | IOD_ST2_TCP | 30 | 00030 | DI_SB_IROGSM21_SkupnaNapaka
ST2DI_SB_IROGSM22_Q0_Izkljucen | DIGITAL | IOD_ST2_TCP | 31 | 00031 | DI_SB_IROGSM22_Q0_Izkljucen
ST2DI_SB_IROGSM22_Q0_Vkljucen | DIGITAL | IOD_ST2_TCP | 32 | 00032 | DI_SB_IROGSM22_Q0_Vkljucen
ST2DI_SB_IROGSM22_Q11_Izkljucen | DIGITAL | IOD_ST2_TCP | 33 | 00033 | DI_SB_IROGSM22_Q11_Izkljucen
ST2DI_SB_IROGSM22_Q11_Vkljucen | DIGITAL | IOD_ST2_TCP | 34 | 00034 | DI_SB_IROGSM22_Q11_Vkljucen
ST2DI_SB_IROGSM22_Q12_Izkljucen | DIGITAL | IOD_ST2_TCP | 35 | 00035 | DI_SB_IROGSM22_Q12_Izkljucen
ST2DI_SB_IROGSM22_Q12_Vkljucen | DIGITAL | IOD_ST2_TCP | 36 | 00036 | DI_SB_IROGSM22_Q12_Vkljucen
ST2DI_SB_IROGSM22_Q13_Izpad | DIGITAL | IOD_ST2_TCP | 37 | 00037 | DI_SB_IROGSM22_Q13_Izpad
ST2DI_SB_IROGSM22_Q13_Vkljucen | DIGITAL | IOD_ST2_TCP | 38 | 00038 | DI_SB_IROGSM22_Q13_Vkljucen
ST2DI_SB_IROGSM22_Q14_Izpad | DIGITAL | IOD_ST2_TCP | 39 | 00039 | DI_SB_IROGSM22_Q14_Izpad
ST2DI_SB_IROGSM22_Q14_Vkljucen | DIGITAL | IOD_ST2_TCP | 40 | 00040 | DI_SB_IROGSM22_Q14_Vkljucen
ST2DI_SB_IROGSM22_Q15_Izpad | DIGITAL | IOD_ST2_TCP | 41 | 00041 | DI_SB_IROGSM22_Q15_Izpad
ST2DI_SB_IROGSM22_Q15_Vkljucen | DIGITAL | IOD_ST2_TCP | 42 | 00042 | DI_SB_IROGSM22_Q15_Vkljucen
ST2DI_SB_IROGSM22_SkupnaNapaka | DIGITAL | IOD_ST2_TCP | 43 | 00043 | DI_SB_IROGSM22_SkupnaNapaka
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_ST2_TCP | 44 | 00044 | DI_SBi_RAZS_AA_Izolacija_NOT_OK
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_ST2_TCP | 45 | 00045 | DI_SBi_RAZS_AB_Izolacija_NOT_OK
ST2ErrComNSX1 | DIGITAL | IOD_ST2_TCP | 46 | 00046 | ErrComNSX[1]
ST2ErrComNSX2 | DIGITAL | IOD_ST2_TCP | 47 | 00047 | ErrComNSX[2]
ST2ErrComNSX3 | DIGITAL | IOD_ST2_TCP | 48 | 00048 | ErrComNSX[3]
ST2ErrComNSX4 | DIGITAL | IOD_ST2_TCP | 49 | 00049 | ErrComNSX[4]
ST2ErrComNSX5 | DIGITAL | IOD_ST2_TCP | 50 | 00050 | ErrComNSX[5]
ST2ErrComNSX6 | DIGITAL | IOD_ST2_TCP | 51 | 00051 | ErrComNSX[6]
ST2ErrComPMM1 | DIGITAL | IOD_ST2_TCP | 52 | 00052 | ErrComPMM[1]
ST2ErrComPort2 | DIGITAL | IOD_ST2_TCP | 53 | 00053 | ErrComPort2
ST2ErrorComPMM1Error | DIGITAL | IOD_ST2_TCP | 54 | 00054 | ErrorComPMM[1].Error
ST2napaka_kom_panel | DIGITAL | IOD_ST2_TCP | 55 | 00055 | napaka_kom_panel
ST2napaka_kom_scada | DIGITAL | IOD_ST2_TCP | 56 | 00056 | napaka_kom_scada
ST2napaka_kom_scada2 | DIGITAL | IOD_ST2_TCP | 57 | 00057 | napaka_kom_scada2
ST2NapakaSenzorSkupno | DIGITAL | IOD_ST2_TCP | 58 | 00058 | NapakaSenzorSkupno
ST2NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST2_TCP | 59 | 00059 | NapakaSenzorVlagaHIA1
ST2NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST2_TCP | 60 | 00060 | NapakaSenzorVlagaHIA2
ST2NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST2_TCP | 61 | 00061 | NapakaSenzorVlagaHIA3
ST2NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST2_TCP | 62 | 00062 | NapakaSenzorVlagaHIA4
ST2NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST2_TCP | 63 | 00063 | NapakaSenzorVlagaHIA5
ST2NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST2_TCP | 64 | 00064 | NapakaSenzorVlagaHIA6
ST2NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST2_TCP | 65 | 00065 | NapakaSenzorVlagaHIA7
ST2NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST2_TCP | 66 | 00066 | NapakaSenzorVlagaHIA8
ST2NapakaTSTempTIA1 | DIGITAL | IOD_ST2_TCP | 67 | 00067 | NapakaTSTempTIA1
ST2NapakaTSTempTIA2 | DIGITAL | IOD_ST2_TCP | 68 | 00068 | NapakaTSTempTIA2
ST2NapakaTSTempTIA3 | DIGITAL | IOD_ST2_TCP | 69 | 00069 | NapakaTSTempTIA3
ST2NapakaTSTempTIA4 | DIGITAL | IOD_ST2_TCP | 70 | 00070 | NapakaTSTempTIA4
ST2NapakaTSTempTIA5 | DIGITAL | IOD_ST2_TCP | 71 | 00071 | NapakaTSTempTIA5
ST2NapakaTSTempTIA6 | DIGITAL | IOD_ST2_TCP | 72 | 00072 | NapakaTSTempTIA6
ST2NapakaTSTempTIA7 | DIGITAL | IOD_ST2_TCP | 73 | 00073 | NapakaTSTempTIA7
ST2NapakaTSTempTIA8 | DIGITAL | IOD_ST2_TCP | 74 | 00074 | NapakaTSTempTIA8
ST2NSX1ResetMAX | DIGITAL | IOD_ST2_TCP | 75 | 00075 | NSX[1].ResetMAX
ST2NSX1ResetMIN | DIGITAL | IOD_ST2_TCP | 76 | 00076 | NSX[1].ResetMIN
ST2NSX2ResetMAX | DIGITAL | IOD_ST2_TCP | 77 | 00077 | NSX[2].ResetMAX
ST2NSX2ResetMIN | DIGITAL | IOD_ST2_TCP | 78 | 00078 | NSX[2].ResetMIN
ST2NSX3ResetMAX | DIGITAL | IOD_ST2_TCP | 79 | 00079 | NSX[3].ResetMAX
ST2NSX3ResetMIN | DIGITAL | IOD_ST2_TCP | 80 | 00080 | NSX[3].ResetMIN
ST2NSX4ResetMAX | DIGITAL | IOD_ST2_TCP | 81 | 00081 | NSX[4].ResetMAX
ST2NSX4ResetMIN | DIGITAL | IOD_ST2_TCP | 82 | 00082 | NSX[4].ResetMIN
ST2NSX5ResetMAX | DIGITAL | IOD_ST2_TCP | 83 | 00083 | NSX[5].ResetMAX
ST2NSX5ResetMIN | DIGITAL | IOD_ST2_TCP | 84 | 00084 | NSX[5].ResetMIN
ST2NSX6ResetMAX | DIGITAL | IOD_ST2_TCP | 85 | 00085 | NSX[6].ResetMAX
ST2NSX6ResetMIN | DIGITAL | IOD_ST2_TCP | 86 | 00086 | NSX[6].ResetMIN
ST2PLC_SB_IROGSM21_F2_2_NOT_OK | DIGITAL | IOD_ST2_TCP | 87 | 00087 | PLC_SB_IROGSM21_F2_2_NOT_OK
ST2PLC_SB_IROGSM22_F2_2_NOT_OK | DIGITAL | IOD_ST2_TCP | 88 | 00088 | PLC_SB_IROGSM22_F2_2_NOT_OK
ST2PMMQA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2_TCP | 89 | 00089 | PMM.QA1_GlStik_IZKLOP_IZPAD
ST2PMMQB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2_TCP | 90 | 00090 | PMM.QB1_GlStik_IZKLOP_IZPAD
ST2PMMSkNapaka_med60in80 | DIGITAL | IOD_ST2_TCP | 91 | 00091 | PMM.SkNapaka_med60in80
ST2PMMSkNapaka_nad80 | DIGITAL | IOD_ST2_TCP | 92 | 00092 | PMM.SkNapaka_nad80
ST2PMMSkNapakaVirA_med60in80 | DIGITAL | IOD_ST2_TCP | 93 | 00093 | PMM.SkNapakaVirA_med60in80
ST2PMMSkNapakaVirA_nad80 | DIGITAL | IOD_ST2_TCP | 94 | 00094 | PMM.SkNapakaVirA_nad80
ST2PMMSkNapakaVirB_med60in80 | DIGITAL | IOD_ST2_TCP | 95 | 00095 | PMM.SkNapakaVirB_med60in80
ST2PMMSkNapakaVirB_nad80 | DIGITAL | IOD_ST2_TCP | 96 | 00096 | PMM.SkNapakaVirB_nad80
ST2PMMVirA_NapakaOzemljitve | DIGITAL | IOD_ST2_TCP | 97 | 00097 | PMM.VirA_NapakaOzemljitve
ST2PMMVirB_NapakaOzemljitve | DIGITAL | IOD_ST2_TCP | 98 | 00098 | PMM.VirB_NapakaOzemljitve
ST2PrevisokaTemp | DIGITAL | IOD_ST2_TCP | 99 | 00099 | PrevisokaTemp
ST2razlitjeLAH1 | DIGITAL | IOD_ST2_TCP | 100 | 00100 | razlitjeLAH1
ST2SetDateTime | DIGITAL | IOD_ST2_TCP | 101 | 00101 | SetDateTime
ST2SetDateTimeDemand | DIGITAL | IOD_ST2_TCP | 102 | 00102 | SetDateTimeDemand
ST2SetDateTimeError | DIGITAL | IOD_ST2_TCP | 103 | 00103 | SetDateTimeError
ST2SetDateTimeFinished | DIGITAL | IOD_ST2_TCP | 104 | 00104 | SetDateTimeFinished
ST2SlabaBaterijaPLC | DIGITAL | IOD_ST2_TCP | 105 | 00105 | SlabaBaterijaPLC
ST2TIA1_previs_temp | DIGITAL | IOD_ST2_TCP | 106 | 00106 | TIA1_previs_temp
ST2TIA2_previs_temp | DIGITAL | IOD_ST2_TCP | 107 | 00107 | TIA2_previs_temp
ST2TIA3_previs_temp | DIGITAL | IOD_ST2_TCP | 108 | 00108 | TIA3_previs_temp
ST2TIA4_previs_temp | DIGITAL | IOD_ST2_TCP | 109 | 00109 | TIA4_previs_temp
ST2TIA5_previs_temp | DIGITAL | IOD_ST2_TCP | 110 | 00110 | TIA5_previs_temp
ST2TIA6_previs_temp | DIGITAL | IOD_ST2_TCP | 111 | 00111 | TIA6_previs_temp
ST2TIA7_previs_temp | DIGITAL | IOD_ST2_TCP | 112 | 00112 | TIA7_previs_temp
ST2TIA8_previs_temp | DIGITAL | IOD_ST2_TCP | 113 | 00113 | TIA8_previs_temp
ST2ups_alarm | DIGITAL | IOD_ST2_TCP | 114 | 00114 | ups_alarm
ST2ups_baterijski_nac | DIGITAL | IOD_ST2_TCP | 115 | 00115 | ups_baterijski_nac
ST2ups_polnjenje | DIGITAL | IOD_ST2_TCP | 116 | 00116 | ups_polnjenje
ST2UserLoggedIn | DIGITAL | IOD_ST2_TCP | 117 | 00117 | UserLoggedIn
ST2XVH_AlarmOn | DIGITAL | IOD_ST2_TCP | 118 | 00118 | XVH_AlarmOn
ST2DateTimeDan | INT | IOD_ST2_TCP | 1 | 40001 | DateTime.Dan | BYTE
ST2DateTimeLeto | INT | IOD_ST2_TCP | 2 | 40002 | DateTime.Leto | BYTE
ST2DateTimeLeto2 | INT | IOD_ST2_TCP | 3 | 40003 | DateTime.Leto2
ST2DateTimeMesec | INT | IOD_ST2_TCP | 4 | 40004 | DateTime.Mesec | BYTE
ST2DateTimeMinuta | INT | IOD_ST2_TCP | 5 | 40005 | DateTime.Minuta | BYTE
ST2DateTimePLC_Dan | INT | IOD_ST2_TCP | 6 | 40006 | DateTime.PLC_Dan | BYTE
ST2DateTimePLC_DanVTednu | INT | IOD_ST2_TCP | 7 | 40007 | DateTime.PLC_DanVTednu | BYTE
ST2DateTimePLC_Leto | INT | IOD_ST2_TCP | 8 | 40008 | DateTime.PLC_Leto | BYTE
ST2DateTimePLC_Mesec | INT | IOD_ST2_TCP | 9 | 40009 | DateTime.PLC_Mesec | BYTE
ST2DateTimePLC_Minuta | INT | IOD_ST2_TCP | 10 | 40010 | DateTime.PLC_Minuta | BYTE
ST2DateTimePLC_Sekunda | INT | IOD_ST2_TCP | 11 | 40011 | DateTime.PLC_Sekunda | BYTE
ST2DateTimePLC_Ura | INT | IOD_ST2_TCP | 12 | 40012 | DateTime.PLC_Ura | BYTE
ST2DateTimeSekunda | INT | IOD_ST2_TCP | 13 | 40013 | DateTime.Sekunda | BYTE
ST2DateTimeUra | INT | IOD_ST2_TCP | 14 | 40014 | DateTime.Ura | BYTE
ST2ErrorComPMM1Status | INT | IOD_ST2_TCP | 15 | 40015 | ErrorComPMM[1].Status
ST2HIA1_vlaga_s | INT | IOD_ST2_TCP | 16 | 40016 | HIA1_vlaga_s
ST2HIA2_vlaga_s | INT | IOD_ST2_TCP | 17 | 40017 | HIA2_vlaga_s
ST2HIA3_vlaga_s | INT | IOD_ST2_TCP | 18 | 40018 | HIA3_vlaga_s
ST2HIA4_vlaga_s | INT | IOD_ST2_TCP | 19 | 40019 | HIA4_vlaga_s
ST2HIA5_vlaga_s | INT | IOD_ST2_TCP | 20 | 40020 | HIA5_vlaga_s
ST2HIA6_vlaga_s | INT | IOD_ST2_TCP | 21 | 40021 | HIA6_vlaga_s
ST2HIA7_vlaga_s | INT | IOD_ST2_TCP | 22 | 40022 | HIA7_vlaga_s
ST2HIA8_vlaga_s | INT | IOD_ST2_TCP | 23 | 40023 | HIA8_vlaga_s
ST2TIA1_alarm | INT | IOD_ST2_TCP | 24 | 40024 | TIA1_alarm
ST2TIA1_temp_s | INT | IOD_ST2_TCP | 25 | 40025 | TIA1_temp_s
ST2TIA2_alarm | INT | IOD_ST2_TCP | 26 | 40026 | TIA2_alarm
ST2TIA2_temp_s | INT | IOD_ST2_TCP | 27 | 40027 | TIA2_temp_s
ST2TIA3_alarm | INT | IOD_ST2_TCP | 28 | 40028 | TIA3_alarm
ST2TIA3_temp_s | INT | IOD_ST2_TCP | 29 | 40029 | TIA3_temp_s
ST2TIA4_alarm | INT | IOD_ST2_TCP | 30 | 40030 | TIA4_alarm
ST2TIA4_temp_s | INT | IOD_ST2_TCP | 31 | 40031 | TIA4_temp_s
ST2TIA5_alarm | INT | IOD_ST2_TCP | 32 | 40032 | TIA5_alarm
ST2TIA5_temp_s | INT | IOD_ST2_TCP | 33 | 40033 | TIA5_temp_s
ST2TIA6_alarm | INT | IOD_ST2_TCP | 34 | 40034 | TIA6_alarm
ST2TIA6_temp_s | INT | IOD_ST2_TCP | 35 | 40035 | TIA6_temp_s
ST2TIA7_alarm | INT | IOD_ST2_TCP | 36 | 40036 | TIA7_alarm
ST2TIA7_temp_s | INT | IOD_ST2_TCP | 37 | 40037 | TIA7_temp_s
ST2TIA8_alarm | INT | IOD_ST2_TCP | 38 | 40038 | TIA8_alarm
ST2TIA8_temp_s | INT | IOD_ST2_TCP | 39 | 40039 | TIA8_temp_s
ST2UserCurrentLevel | INT | IOD_ST2_TCP | 40 | 40040 | UserCurrentLevel | BYTE
ST2iPMM_VirA_Tok1 | REAL | IOD_ST2_TCP | 4001 | 44001 | iPMM_VirA_Tok1
ST2iPMM_VirA_Tok10 | REAL | IOD_ST2_TCP | 4003 | 44003 | iPMM_VirA_Tok10
ST2iPMM_VirA_Tok11 | REAL | IOD_ST2_TCP | 4005 | 44005 | iPMM_VirA_Tok11
ST2iPMM_VirA_Tok12 | REAL | IOD_ST2_TCP | 4007 | 44007 | iPMM_VirA_Tok12
ST2iPMM_VirA_Tok13 | REAL | IOD_ST2_TCP | 4009 | 44009 | iPMM_VirA_Tok13
ST2iPMM_VirA_Tok14 | REAL | IOD_ST2_TCP | 4011 | 44011 | iPMM_VirA_Tok14
ST2iPMM_VirA_Tok15 | REAL | IOD_ST2_TCP | 4013 | 44013 | iPMM_VirA_Tok15
ST2iPMM_VirA_Tok16 | REAL | IOD_ST2_TCP | 4015 | 44015 | iPMM_VirA_Tok16
ST2iPMM_VirA_Tok17 | REAL | IOD_ST2_TCP | 4017 | 44017 | iPMM_VirA_Tok17
ST2iPMM_VirA_Tok18 | REAL | IOD_ST2_TCP | 4019 | 44019 | iPMM_VirA_Tok18
ST2iPMM_VirA_Tok19 | REAL | IOD_ST2_TCP | 4021 | 44021 | iPMM_VirA_Tok19
ST2iPMM_VirA_Tok2 | REAL | IOD_ST2_TCP | 4023 | 44023 | iPMM_VirA_Tok2
ST2iPMM_VirA_Tok20 | REAL | IOD_ST2_TCP | 4025 | 44025 | iPMM_VirA_Tok20
ST2iPMM_VirA_Tok21 | REAL | IOD_ST2_TCP | 4027 | 44027 | iPMM_VirA_Tok21
ST2iPMM_VirA_Tok22 | REAL | IOD_ST2_TCP | 4029 | 44029 | iPMM_VirA_Tok22
ST2iPMM_VirA_Tok23 | REAL | IOD_ST2_TCP | 4031 | 44031 | iPMM_VirA_Tok23
ST2iPMM_VirA_Tok24 | REAL | IOD_ST2_TCP | 4033 | 44033 | iPMM_VirA_Tok24
ST2iPMM_VirA_Tok25 | REAL | IOD_ST2_TCP | 4035 | 44035 | iPMM_VirA_Tok25
ST2iPMM_VirA_Tok26 | REAL | IOD_ST2_TCP | 4037 | 44037 | iPMM_VirA_Tok26
ST2iPMM_VirA_Tok27 | REAL | IOD_ST2_TCP | 4039 | 44039 | iPMM_VirA_Tok27
ST2iPMM_VirA_Tok28 | REAL | IOD_ST2_TCP | 4041 | 44041 | iPMM_VirA_Tok28
ST2iPMM_VirA_Tok29 | REAL | IOD_ST2_TCP | 4043 | 44043 | iPMM_VirA_Tok29
ST2iPMM_VirA_Tok3 | REAL | IOD_ST2_TCP | 4045 | 44045 | iPMM_VirA_Tok3
ST2iPMM_VirA_Tok30 | REAL | IOD_ST2_TCP | 4047 | 44047 | iPMM_VirA_Tok30
ST2iPMM_VirA_Tok31 | REAL | IOD_ST2_TCP | 4049 | 44049 | iPMM_VirA_Tok31
ST2iPMM_VirA_Tok32 | REAL | IOD_ST2_TCP | 4051 | 44051 | iPMM_VirA_Tok32
ST2iPMM_VirA_Tok33 | REAL | IOD_ST2_TCP | 4053 | 44053 | iPMM_VirA_Tok33
ST2iPMM_VirA_Tok34 | REAL | IOD_ST2_TCP | 4055 | 44055 | iPMM_VirA_Tok34
ST2iPMM_VirA_Tok35 | REAL | IOD_ST2_TCP | 4057 | 44057 | iPMM_VirA_Tok35
ST2iPMM_VirA_Tok36 | REAL | IOD_ST2_TCP | 4059 | 44059 | iPMM_VirA_Tok36
ST2iPMM_VirA_Tok37 | REAL | IOD_ST2_TCP | 4061 | 44061 | iPMM_VirA_Tok37
ST2iPMM_VirA_Tok38 | REAL | IOD_ST2_TCP | 4063 | 44063 | iPMM_VirA_Tok38
ST2iPMM_VirA_Tok39 | REAL | IOD_ST2_TCP | 4065 | 44065 | iPMM_VirA_Tok39
ST2iPMM_VirA_Tok4 | REAL | IOD_ST2_TCP | 4067 | 44067 | iPMM_VirA_Tok4
ST2iPMM_VirA_Tok40 | REAL | IOD_ST2_TCP | 4069 | 44069 | iPMM_VirA_Tok40
ST2iPMM_VirA_Tok41 | REAL | IOD_ST2_TCP | 4071 | 44071 | iPMM_VirA_Tok41
ST2iPMM_VirA_Tok42 | REAL | IOD_ST2_TCP | 4073 | 44073 | iPMM_VirA_Tok42
ST2iPMM_VirA_Tok43 | REAL | IOD_ST2_TCP | 4075 | 44075 | iPMM_VirA_Tok43
ST2iPMM_VirA_Tok44 | REAL | IOD_ST2_TCP | 4077 | 44077 | iPMM_VirA_Tok44
ST2iPMM_VirA_Tok5 | REAL | IOD_ST2_TCP | 4079 | 44079 | iPMM_VirA_Tok5
ST2iPMM_VirA_Tok6 | REAL | IOD_ST2_TCP | 4081 | 44081 | iPMM_VirA_Tok6
ST2iPMM_VirA_Tok7 | REAL | IOD_ST2_TCP | 4083 | 44083 | iPMM_VirA_Tok7
ST2iPMM_VirA_Tok8 | REAL | IOD_ST2_TCP | 4085 | 44085 | iPMM_VirA_Tok8
ST2iPMM_VirA_Tok9 | REAL | IOD_ST2_TCP | 4087 | 44087 | iPMM_VirA_Tok9
ST2iPMM_VirB_Tok1 | REAL | IOD_ST2_TCP | 4089 | 44089 | iPMM_VirB_Tok1
ST2iPMM_VirB_Tok10 | REAL | IOD_ST2_TCP | 4091 | 44091 | iPMM_VirB_Tok10
ST2iPMM_VirB_Tok11 | REAL | IOD_ST2_TCP | 4093 | 44093 | iPMM_VirB_Tok11
ST2iPMM_VirB_Tok12 | REAL | IOD_ST2_TCP | 4095 | 44095 | iPMM_VirB_Tok12
ST2iPMM_VirB_Tok13 | REAL | IOD_ST2_TCP | 4097 | 44097 | iPMM_VirB_Tok13
ST2iPMM_VirB_Tok14 | REAL | IOD_ST2_TCP | 4099 | 44099 | iPMM_VirB_Tok14
ST2iPMM_VirB_Tok15 | REAL | IOD_ST2_TCP | 4101 | 44101 | iPMM_VirB_Tok15
ST2iPMM_VirB_Tok16 | REAL | IOD_ST2_TCP | 4103 | 44103 | iPMM_VirB_Tok16
ST2iPMM_VirB_Tok17 | REAL | IOD_ST2_TCP | 4105 | 44105 | iPMM_VirB_Tok17
ST2iPMM_VirB_Tok18 | REAL | IOD_ST2_TCP | 4107 | 44107 | iPMM_VirB_Tok18
ST2iPMM_VirB_Tok19 | REAL | IOD_ST2_TCP | 4109 | 44109 | iPMM_VirB_Tok19
ST2iPMM_VirB_Tok2 | REAL | IOD_ST2_TCP | 4111 | 44111 | iPMM_VirB_Tok2
ST2iPMM_VirB_Tok20 | REAL | IOD_ST2_TCP | 4113 | 44113 | iPMM_VirB_Tok20
ST2iPMM_VirB_Tok21 | REAL | IOD_ST2_TCP | 4115 | 44115 | iPMM_VirB_Tok21
ST2iPMM_VirB_Tok22 | REAL | IOD_ST2_TCP | 4117 | 44117 | iPMM_VirB_Tok22
ST2iPMM_VirB_Tok23 | REAL | IOD_ST2_TCP | 4119 | 44119 | iPMM_VirB_Tok23
ST2iPMM_VirB_Tok24 | REAL | IOD_ST2_TCP | 4121 | 44121 | iPMM_VirB_Tok24
ST2iPMM_VirB_Tok25 | REAL | IOD_ST2_TCP | 4123 | 44123 | iPMM_VirB_Tok25
ST2iPMM_VirB_Tok26 | REAL | IOD_ST2_TCP | 4125 | 44125 | iPMM_VirB_Tok26
ST2iPMM_VirB_Tok27 | REAL | IOD_ST2_TCP | 4127 | 44127 | iPMM_VirB_Tok27
ST2iPMM_VirB_Tok28 | REAL | IOD_ST2_TCP | 4129 | 44129 | iPMM_VirB_Tok28
ST2iPMM_VirB_Tok29 | REAL | IOD_ST2_TCP | 4131 | 44131 | iPMM_VirB_Tok29
ST2iPMM_VirB_Tok3 | REAL | IOD_ST2_TCP | 4133 | 44133 | iPMM_VirB_Tok3
ST2iPMM_VirB_Tok30 | REAL | IOD_ST2_TCP | 4135 | 44135 | iPMM_VirB_Tok30
ST2iPMM_VirB_Tok31 | REAL | IOD_ST2_TCP | 4137 | 44137 | iPMM_VirB_Tok31
ST2iPMM_VirB_Tok32 | REAL | IOD_ST2_TCP | 4139 | 44139 | iPMM_VirB_Tok32
ST2iPMM_VirB_Tok33 | REAL | IOD_ST2_TCP | 4141 | 44141 | iPMM_VirB_Tok33
ST2iPMM_VirB_Tok34 | REAL | IOD_ST2_TCP | 4143 | 44143 | iPMM_VirB_Tok34
ST2iPMM_VirB_Tok35 | REAL | IOD_ST2_TCP | 4145 | 44145 | iPMM_VirB_Tok35
ST2iPMM_VirB_Tok36 | REAL | IOD_ST2_TCP | 4147 | 44147 | iPMM_VirB_Tok36
ST2iPMM_VirB_Tok37 | REAL | IOD_ST2_TCP | 4149 | 44149 | iPMM_VirB_Tok37
ST2iPMM_VirB_Tok38 | REAL | IOD_ST2_TCP | 4151 | 44151 | iPMM_VirB_Tok38
ST2iPMM_VirB_Tok39 | REAL | IOD_ST2_TCP | 4153 | 44153 | iPMM_VirB_Tok39
ST2iPMM_VirB_Tok4 | REAL | IOD_ST2_TCP | 4155 | 44155 | iPMM_VirB_Tok4
ST2iPMM_VirB_Tok40 | REAL | IOD_ST2_TCP | 4157 | 44157 | iPMM_VirB_Tok40
ST2iPMM_VirB_Tok41 | REAL | IOD_ST2_TCP | 4159 | 44159 | iPMM_VirB_Tok41
ST2iPMM_VirB_Tok42 | REAL | IOD_ST2_TCP | 4161 | 44161 | iPMM_VirB_Tok42
ST2iPMM_VirB_Tok43 | REAL | IOD_ST2_TCP | 4163 | 44163 | iPMM_VirB_Tok43
ST2iPMM_VirB_Tok44 | REAL | IOD_ST2_TCP | 4165 | 44165 | iPMM_VirB_Tok44
ST2iPMM_VirB_Tok5 | REAL | IOD_ST2_TCP | 4167 | 44167 | iPMM_VirB_Tok5
ST2iPMM_VirB_Tok6 | REAL | IOD_ST2_TCP | 4169 | 44169 | iPMM_VirB_Tok6
ST2iPMM_VirB_Tok7 | REAL | IOD_ST2_TCP | 4171 | 44171 | iPMM_VirB_Tok7
ST2iPMM_VirB_Tok8 | REAL | IOD_ST2_TCP | 4173 | 44173 | iPMM_VirB_Tok8
ST2iPMM_VirB_Tok9 | REAL | IOD_ST2_TCP | 4175 | 44175 | iPMM_VirB_Tok9
ST2NSX1ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4177 | 44177 | NSX[1].ActiveEnergy_kWh
ST2NSX1ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 4179 | 44179 | NSX[1].ActiveNegativeEnergy_kWh
ST2NSX1ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 4181 | 44181 | NSX[1].ActivePositiveEnergy_kWh
ST2NSX1ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 4183 | 44183 | NSX[1].ActivePowerDemand_kW
ST2NSX1ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4185 | 44185 | NSX[1].ActivePowerL1_kW
ST2NSX1ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4187 | 44187 | NSX[1].ActivePowerL2_kW
ST2NSX1ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4189 | 44189 | NSX[1].ActivePowerL3_kW
ST2NSX1ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 4191 | 44191 | NSX[1].ActivePowerMaxDemand_kW
ST2NSX1ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4193 | 44193 | NSX[1].ActivePowerTotal_kW
ST2NSX1ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 4195 | 44195 | NSX[1].ApparentEnergy_kVAh
ST2NSX1ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 4197 | 44197 | NSX[1].ApparentPowerDemand_kVA
ST2NSX1ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 4199 | 44199 | NSX[1].ApparentPowerMaxDemand_kVA
ST2NSX1ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4201 | 44201 | NSX[1].ApparetnPowerL1_kVA
ST2NSX1ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4203 | 44203 | NSX[1].ApparetnPowerL2_kVA
ST2NSX1ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4205 | 44205 | NSX[1].ApparetnPowerL3_kVA
ST2NSX1ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4207 | 44207 | NSX[1].ApparetnPowerTotal_kVA
ST2NSX1CosFL1 | REAL | IOD_ST2_TCP | 4209 | 44209 | NSX[1].CosFL1
ST2NSX1CosFL2 | REAL | IOD_ST2_TCP | 4211 | 44211 | NSX[1].CosFL2
ST2NSX1CosFL3 | REAL | IOD_ST2_TCP | 4213 | 44213 | NSX[1].CosFL3
ST2NSX1CosFTotal | REAL | IOD_ST2_TCP | 4215 | 44215 | NSX[1].CosFTotal
ST2NSX1CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4217 | 44217 | NSX[1].CumulNegativeActiveEnergy_kWh
ST2NSX1CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4219 | 44219 | NSX[1].CumulPositiveActiveEnergy_kWh
ST2NSX1CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4221 | 44221 | NSX[1].CurrentAvgI1I2I3_A
ST2NSX1CurrentDemandL1_A | REAL | IOD_ST2_TCP | 4223 | 44223 | NSX[1].CurrentDemandL1_A
ST2NSX1CurrentDemandL2_A | REAL | IOD_ST2_TCP | 4225 | 44225 | NSX[1].CurrentDemandL2_A
ST2NSX1CurrentDemandL3_A | REAL | IOD_ST2_TCP | 4227 | 44227 | NSX[1].CurrentDemandL3_A
ST2NSX1CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 4229 | 44229 | NSX[1].CurrentDemandMaxL1_A
ST2NSX1CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 4231 | 44231 | NSX[1].CurrentDemandMaxL2_A
ST2NSX1CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 4233 | 44233 | NSX[1].CurrentDemandMaxL3_A
ST2NSX1CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 4235 | 44235 | NSX[1].CurrentDemandMaxN_A
ST2NSX1CurrentDemandN_A | REAL | IOD_ST2_TCP | 4237 | 44237 | NSX[1].CurrentDemandN_A
ST2NSX1CurrentL1_A | REAL | IOD_ST2_TCP | 4239 | 44239 | NSX[1].CurrentL1_A
ST2NSX1CurrentL2_A | REAL | IOD_ST2_TCP | 4241 | 44241 | NSX[1].CurrentL2_A
ST2NSX1CurrentL3_A | REAL | IOD_ST2_TCP | 4243 | 44243 | NSX[1].CurrentL3_A
ST2NSX1CurrentN_A | REAL | IOD_ST2_TCP | 4245 | 44245 | NSX[1].CurrentN_A
ST2NSX1CurrentUnbI1_P | REAL | IOD_ST2_TCP | 4247 | 44247 | NSX[1].CurrentUnbI1_P
ST2NSX1CurrentUnbI2_P | REAL | IOD_ST2_TCP | 4249 | 44249 | NSX[1].CurrentUnbI2_P
ST2NSX1CurrentUnbI3_P | REAL | IOD_ST2_TCP | 4251 | 44251 | NSX[1].CurrentUnbI3_P
ST2NSX1CurrentUnbN_P | REAL | IOD_ST2_TCP | 4253 | 44253 | NSX[1].CurrentUnbN_P
ST2NSX1DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 4255 | 44255 | NSX[1].DelovnaEnergija_TEMP
ST2NSX1DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4257 | 44257 | NSX[1].DistortionPowerL1_kVAr
ST2NSX1DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4259 | 44259 | NSX[1].DistortionPowerL2_kVAr
ST2NSX1DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4261 | 44261 | NSX[1].DistortionPowerL3_kVAr
ST2NSX1DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4263 | 44263 | NSX[1].DistortionPowerTotal_kVAr
ST2NSX1Frequency_Hz | REAL | IOD_ST2_TCP | 4265 | 44265 | NSX[1].Frequency_Hz
ST2NSX1FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4267 | 44267 | NSX[1].FunReactivePowerL1_kVAr
ST2NSX1FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4269 | 44269 | NSX[1].FunReactivePowerL2_kVAr
ST2NSX1FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4271 | 44271 | NSX[1].FunReactivePowerL3_kVAr
ST2NSX1FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4273 | 44273 | NSX[1].FunReactivePowerTotal_kVAr
ST2NSX1MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4275 | 44275 | NSX[1].MAX_ActivePowerL1_kW
ST2NSX1MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4277 | 44277 | NSX[1].MAX_ActivePowerL2_kW
ST2NSX1MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4279 | 44279 | NSX[1].MAX_ActivePowerL3_kW
ST2NSX1MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4281 | 44281 | NSX[1].MAX_ActivePowerTotal_kW
ST2NSX1MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4283 | 44283 | NSX[1].MAX_ApparetnPowerL1_kVA
ST2NSX1MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4285 | 44285 | NSX[1].MAX_ApparetnPowerL2_kVA
ST2NSX1MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4287 | 44287 | NSX[1].MAX_ApparetnPowerL3_kVA
ST2NSX1MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4289 | 44289 | NSX[1].MAX_ApparetnPowerTotal_kVA
ST2NSX1MAX_CosFL1 | REAL | IOD_ST2_TCP | 4291 | 44291 | NSX[1].MAX_CosFL1
ST2NSX1MAX_CosFL2 | REAL | IOD_ST2_TCP | 4293 | 44293 | NSX[1].MAX_CosFL2
ST2NSX1MAX_CosFL3 | REAL | IOD_ST2_TCP | 4295 | 44295 | NSX[1].MAX_CosFL3
ST2NSX1MAX_CosFTotal | REAL | IOD_ST2_TCP | 4297 | 44297 | NSX[1].MAX_CosFTotal
ST2NSX1MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4299 | 44299 | NSX[1].MAX_CurrentAvgI1I2I3_A
ST2NSX1MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 4301 | 44301 | NSX[1].MAX_CurrentL1_A
ST2NSX1MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 4303 | 44303 | NSX[1].MAX_CurrentL2_A
ST2NSX1MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 4305 | 44305 | NSX[1].MAX_CurrentL3_A
ST2NSX1MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 4307 | 44307 | NSX[1].MAX_CurrentMaxL1L2L3N_A
ST2NSX1MAX_CurrentN_A | REAL | IOD_ST2_TCP | 4309 | 44309 | NSX[1].MAX_CurrentN_A
ST2NSX1MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4311 | 44311 | NSX[1].MAX_DistortionPowerL1_kVAr
ST2NSX1MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4313 | 44313 | NSX[1].MAX_DistortionPowerL2_kVAr
ST2NSX1MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4315 | 44315 | NSX[1].MAX_DistortionPowerL3_kVAr
ST2NSX1MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4317 | 44317 | NSX[1].MAX_DistortionPowerTotal_kVAr
ST2NSX1MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 4319 | 44319 | NSX[1].MAX_Frequency_Hz
ST2NSX1MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4321 | 44321 | NSX[1].MAX_FunReactivePowerL1_kVAr
ST2NSX1MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4323 | 44323 | NSX[1].MAX_FunReactivePowerL2_kVAr
ST2NSX1MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4325 | 44325 | NSX[1].MAX_FunReactivePowerL3_kVAr
ST2NSX1MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4327 | 44327 | NSX[1].MAX_FunReactivePowerTotal_kVAr
ST2NSX1MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 4329 | 44329 | NSX[1].MAX_PowerFactorL1
ST2NSX1MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 4331 | 44331 | NSX[1].MAX_PowerFactorL2
ST2NSX1MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 4333 | 44333 | NSX[1].MAX_PowerFactorL3
ST2NSX1MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 4335 | 44335 | NSX[1].MAX_PowerFactorTotal
ST2NSX1MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4337 | 44337 | NSX[1].MAX_ReactivePowerL1_kVAr
ST2NSX1MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4339 | 44339 | NSX[1].MAX_ReactivePowerL2_kVAr
ST2NSX1MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4341 | 44341 | NSX[1].MAX_ReactivePowerL3_kVAr
ST2NSX1MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4343 | 44343 | NSX[1].MAX_ReactivePowerTotal_kVAr
ST2NSX1MAX_THDI1_P | REAL | IOD_ST2_TCP | 4345 | 44345 | NSX[1].MAX_THDI1_P
ST2NSX1MAX_THDI2_P | REAL | IOD_ST2_TCP | 4347 | 44347 | NSX[1].MAX_THDI2_P
ST2NSX1MAX_THDI3_P | REAL | IOD_ST2_TCP | 4349 | 44349 | NSX[1].MAX_THDI3_P
ST2NSX1MAX_THDV12_P | REAL | IOD_ST2_TCP | 4351 | 44351 | NSX[1].MAX_THDV12_P
ST2NSX1MAX_THDV1N_P | REAL | IOD_ST2_TCP | 4353 | 44353 | NSX[1].MAX_THDV1N_P
ST2NSX1MAX_THDV23_P | REAL | IOD_ST2_TCP | 4355 | 44355 | NSX[1].MAX_THDV23_P
ST2NSX1MAX_THDV2N_P | REAL | IOD_ST2_TCP | 4357 | 44357 | NSX[1].MAX_THDV2N_P
ST2NSX1MAX_THDV31_P | REAL | IOD_ST2_TCP | 4359 | 44359 | NSX[1].MAX_THDV31_P
ST2NSX1MAX_THDV3N_P | REAL | IOD_ST2_TCP | 4361 | 44361 | NSX[1].MAX_THDV3N_P
ST2NSX1MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4363 | 44363 | NSX[1].MAX_VoltageAvgPhToN_V
ST2NSX1MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4365 | 44365 | NSX[1].MAX_VoltageAvgPhToPh_V
ST2NSX1MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4367 | 44367 | NSX[1].MAX_VoltageUnbV12_P
ST2NSX1MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4369 | 44369 | NSX[1].MAX_VoltageUnbV1N_P
ST2NSX1MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4371 | 44371 | NSX[1].MAX_VoltageUnbV23_P
ST2NSX1MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4373 | 44373 | NSX[1].MAX_VoltageUnbV2N_P
ST2NSX1MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 4375 | 44375 | NSX[1].MAX_VoltageUnbV31_P
ST2NSX1MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 4377 | 44377 | NSX[1].MAX_VoltageUnbV3N_P
ST2NSX1MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 4379 | 44379 | NSX[1].MAX_VoltageV12_V
ST2NSX1MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 4381 | 44381 | NSX[1].MAX_VoltageV1N_V
ST2NSX1MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 4383 | 44383 | NSX[1].MAX_VoltageV23_V
ST2NSX1MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 4385 | 44385 | NSX[1].MAX_VoltageV2N_V
ST2NSX1MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 4387 | 44387 | NSX[1].MAX_VoltageV31_V
ST2NSX1MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 4389 | 44389 | NSX[1].MAX_VoltageV3N_V
ST2NSX1MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4391 | 44391 | NSX[1].MIN_ActivePowerL1_kW
ST2NSX1MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4393 | 44393 | NSX[1].MIN_ActivePowerL2_kW
ST2NSX1MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4395 | 44395 | NSX[1].MIN_ActivePowerL3_kW
ST2NSX1MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4397 | 44397 | NSX[1].MIN_ActivePowerTotal_kW
ST2NSX1MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4399 | 44399 | NSX[1].MIN_ApparetnPowerL1_kVA
ST2NSX1MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4401 | 44401 | NSX[1].MIN_ApparetnPowerL2_kVA
ST2NSX1MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4403 | 44403 | NSX[1].MIN_ApparetnPowerL3_kVA
ST2NSX1MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4405 | 44405 | NSX[1].MIN_ApparetnPowerTotal_kVA
ST2NSX1MIN_CosFL1 | REAL | IOD_ST2_TCP | 4407 | 44407 | NSX[1].MIN_CosFL1
ST2NSX1MIN_CosFL2 | REAL | IOD_ST2_TCP | 4409 | 44409 | NSX[1].MIN_CosFL2
ST2NSX1MIN_CosFL3 | REAL | IOD_ST2_TCP | 4411 | 44411 | NSX[1].MIN_CosFL3
ST2NSX1MIN_CosFTotal | REAL | IOD_ST2_TCP | 4413 | 44413 | NSX[1].MIN_CosFTotal
ST2NSX1MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4415 | 44415 | NSX[1].MIN_CurrentAvgI1I2I3_A
ST2NSX1MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 4417 | 44417 | NSX[1].MIN_CurrentL1_A
ST2NSX1MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 4419 | 44419 | NSX[1].MIN_CurrentL2_A
ST2NSX1MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 4421 | 44421 | NSX[1].MIN_CurrentL3_A
ST2NSX1MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 4423 | 44423 | NSX[1].MIN_CurrentMaxL1L2L3N_A
ST2NSX1MIN_CurrentN_A | REAL | IOD_ST2_TCP | 4425 | 44425 | NSX[1].MIN_CurrentN_A
ST2NSX1MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4427 | 44427 | NSX[1].MIN_DistortionPowerL1_kVAr
ST2NSX1MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4429 | 44429 | NSX[1].MIN_DistortionPowerL2_kVAr
ST2NSX1MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4431 | 44431 | NSX[1].MIN_DistortionPowerL3_kVAr
ST2NSX1MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4433 | 44433 | NSX[1].MIN_DistortionPowerTotal_kVAr
ST2NSX1MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 4435 | 44435 | NSX[1].MIN_Frequency_Hz
ST2NSX1MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4437 | 44437 | NSX[1].MIN_FunReactivePowerL1_kVAr
ST2NSX1MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4439 | 44439 | NSX[1].MIN_FunReactivePowerL2_kVAr
ST2NSX1MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4441 | 44441 | NSX[1].MIN_FunReactivePowerL3_kVAr
ST2NSX1MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4443 | 44443 | NSX[1].MIN_FunReactivePowerTotal_kVAr
ST2NSX1MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 4445 | 44445 | NSX[1].MIN_PowerFactorL1
ST2NSX1MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 4447 | 44447 | NSX[1].MIN_PowerFactorL2
ST2NSX1MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 4449 | 44449 | NSX[1].MIN_PowerFactorL3
ST2NSX1MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 4451 | 44451 | NSX[1].MIN_PowerFactorTotal
ST2NSX1MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4453 | 44453 | NSX[1].MIN_ReactivePowerL1_kVAr
ST2NSX1MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4455 | 44455 | NSX[1].MIN_ReactivePowerL2_kVAr
ST2NSX1MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4457 | 44457 | NSX[1].MIN_ReactivePowerL3_kVAr
ST2NSX1MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4459 | 44459 | NSX[1].MIN_ReactivePowerTotal_kVAr
ST2NSX1MIN_THDI1_P | REAL | IOD_ST2_TCP | 4461 | 44461 | NSX[1].MIN_THDI1_P
ST2NSX1MIN_THDI2_P | REAL | IOD_ST2_TCP | 4463 | 44463 | NSX[1].MIN_THDI2_P
ST2NSX1MIN_THDI3_P | REAL | IOD_ST2_TCP | 4465 | 44465 | NSX[1].MIN_THDI3_P
ST2NSX1MIN_THDV12_P | REAL | IOD_ST2_TCP | 4467 | 44467 | NSX[1].MIN_THDV12_P
ST2NSX1MIN_THDV1N_P | REAL | IOD_ST2_TCP | 4469 | 44469 | NSX[1].MIN_THDV1N_P
ST2NSX1MIN_THDV23_P | REAL | IOD_ST2_TCP | 4471 | 44471 | NSX[1].MIN_THDV23_P
ST2NSX1MIN_THDV2N_P | REAL | IOD_ST2_TCP | 4473 | 44473 | NSX[1].MIN_THDV2N_P
ST2NSX1MIN_THDV31_P | REAL | IOD_ST2_TCP | 4475 | 44475 | NSX[1].MIN_THDV31_P
ST2NSX1MIN_THDV3N_P | REAL | IOD_ST2_TCP | 4477 | 44477 | NSX[1].MIN_THDV3N_P
ST2NSX1MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4479 | 44479 | NSX[1].MIN_VoltageAvgPhToN_V
ST2NSX1MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4481 | 44481 | NSX[1].MIN_VoltageAvgPhToPh_V
ST2NSX1MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4483 | 44483 | NSX[1].MIN_VoltageUnbV12_P
ST2NSX1MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4485 | 44485 | NSX[1].MIN_VoltageUnbV1N_P
ST2NSX1MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4487 | 44487 | NSX[1].MIN_VoltageUnbV23_P
ST2NSX1MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4489 | 44489 | NSX[1].MIN_VoltageUnbV2N_P
ST2NSX1MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 4491 | 44491 | NSX[1].MIN_VoltageUnbV31_P
ST2NSX1MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 4493 | 44493 | NSX[1].MIN_VoltageUnbV3N_P
ST2NSX1MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 4495 | 44495 | NSX[1].MIN_VoltageV12_V
ST2NSX1MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 4497 | 44497 | NSX[1].MIN_VoltageV1N_V
ST2NSX1MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 4499 | 44499 | NSX[1].MIN_VoltageV23_V
ST2NSX1MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 4501 | 44501 | NSX[1].MIN_VoltageV2N_V
ST2NSX1MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 4503 | 44503 | NSX[1].MIN_VoltageV31_V
ST2NSX1MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 4505 | 44505 | NSX[1].MIN_VoltageV3N_V
ST2NSX1PowerFactorL1 | REAL | IOD_ST2_TCP | 4507 | 44507 | NSX[1].PowerFactorL1
ST2NSX1PowerFactorL2 | REAL | IOD_ST2_TCP | 4509 | 44509 | NSX[1].PowerFactorL2
ST2NSX1PowerFactorL3 | REAL | IOD_ST2_TCP | 4511 | 44511 | NSX[1].PowerFactorL3
ST2NSX1PowerFactorTotal | REAL | IOD_ST2_TCP | 4513 | 44513 | NSX[1].PowerFactorTotal
ST2NSX1RazEner_D | REAL | IOD_ST2_TCP | 4515 | 44515 | NSX[1].RazEner_D
ST2NSX1RazEner_D_SCADA | REAL | IOD_ST2_TCP | 4517 | 44517 | NSX[1].RazEner_D_SCADA
ST2NSX1RazEner_D_TEMP | REAL | IOD_ST2_TCP | 4519 | 44519 | NSX[1].RazEner_D_TEMP
ST2NSX1RazEner_M | REAL | IOD_ST2_TCP | 4521 | 44521 | NSX[1].RazEner_M
ST2NSX1RazEner_M_SCADA | REAL | IOD_ST2_TCP | 4523 | 44523 | NSX[1].RazEner_M_SCADA
ST2NSX1RazEner_M_TEMP | REAL | IOD_ST2_TCP | 4525 | 44525 | NSX[1].RazEner_M_TEMP
ST2NSX1RazEner_T | REAL | IOD_ST2_TCP | 4527 | 44527 | NSX[1].RazEner_T
ST2NSX1RazEner_T_SCADA | REAL | IOD_ST2_TCP | 4529 | 44529 | NSX[1].RazEner_T_SCADA
ST2NSX1RazEner_T_TEMP | REAL | IOD_ST2_TCP | 4531 | 44531 | NSX[1].RazEner_T_TEMP
ST2NSX1ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 4533 | 44533 | NSX[1].ReactiveEnergy_kVArh
ST2NSX1ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 4535 | 44535 | NSX[1].ReactiveNegativeEnergy_kVArh
ST2NSX1ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 4537 | 44537 | NSX[1].ReactivePositiveEnergy_kVArh
ST2NSX1ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 4539 | 44539 | NSX[1].ReactivePowerDemand_kVAr
ST2NSX1ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4541 | 44541 | NSX[1].ReactivePowerL1_kVAr
ST2NSX1ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4543 | 44543 | NSX[1].ReactivePowerL2_kVAr
ST2NSX1ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4545 | 44545 | NSX[1].ReactivePowerL3_kVAr
ST2NSX1ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 4547 | 44547 | NSX[1].ReactivePowerMaxDemand_kVAr
ST2NSX1ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4549 | 44549 | NSX[1].ReactivePowerTotal_kVAr
ST2NSX1THDI1_P | REAL | IOD_ST2_TCP | 4551 | 44551 | NSX[1].THDI1_P
ST2NSX1THDI2_P | REAL | IOD_ST2_TCP | 4553 | 44553 | NSX[1].THDI2_P
ST2NSX1THDI3_P | REAL | IOD_ST2_TCP | 4555 | 44555 | NSX[1].THDI3_P
ST2NSX1THDV12_P | REAL | IOD_ST2_TCP | 4557 | 44557 | NSX[1].THDV12_P
ST2NSX1THDV1N_P | REAL | IOD_ST2_TCP | 4559 | 44559 | NSX[1].THDV1N_P
ST2NSX1THDV23_P | REAL | IOD_ST2_TCP | 4561 | 44561 | NSX[1].THDV23_P
ST2NSX1THDV2N_P | REAL | IOD_ST2_TCP | 4563 | 44563 | NSX[1].THDV2N_P
ST2NSX1THDV31_P | REAL | IOD_ST2_TCP | 4565 | 44565 | NSX[1].THDV31_P
ST2NSX1THDV3N_P | REAL | IOD_ST2_TCP | 4567 | 44567 | NSX[1].THDV3N_P
ST2NSX1VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4569 | 44569 | NSX[1].VoltageAvgPhToN_V
ST2NSX1VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4571 | 44571 | NSX[1].VoltageAvgPhToPh_V
ST2NSX1VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4573 | 44573 | NSX[1].VoltageUnbV12_P
ST2NSX1VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4575 | 44575 | NSX[1].VoltageUnbV1N_P
ST2NSX1VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4577 | 44577 | NSX[1].VoltageUnbV23_P
ST2NSX1VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4579 | 44579 | NSX[1].VoltageUnbV2N_P
ST2NSX1VoltageUnbV31_P | REAL | IOD_ST2_TCP | 4581 | 44581 | NSX[1].VoltageUnbV31_P
ST2NSX1VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 4583 | 44583 | NSX[1].VoltageUnbV3N_P
ST2NSX1VoltageV12_V | REAL | IOD_ST2_TCP | 4585 | 44585 | NSX[1].VoltageV12_V
ST2NSX1VoltageV1N_V | REAL | IOD_ST2_TCP | 4587 | 44587 | NSX[1].VoltageV1N_V
ST2NSX1VoltageV23_V | REAL | IOD_ST2_TCP | 4589 | 44589 | NSX[1].VoltageV23_V
ST2NSX1VoltageV2N_V | REAL | IOD_ST2_TCP | 4591 | 44591 | NSX[1].VoltageV2N_V
ST2NSX1VoltageV31_V | REAL | IOD_ST2_TCP | 4593 | 44593 | NSX[1].VoltageV31_V
ST2NSX1VoltageV3N_V | REAL | IOD_ST2_TCP | 4595 | 44595 | NSX[1].VoltageV3N_V
ST2NSX2ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4597 | 44597 | NSX[2].ActiveEnergy_kWh
ST2NSX2ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 4599 | 44599 | NSX[2].ActiveNegativeEnergy_kWh
ST2NSX2ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 4601 | 44601 | NSX[2].ActivePositiveEnergy_kWh
ST2NSX2ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 4603 | 44603 | NSX[2].ActivePowerDemand_kW
ST2NSX2ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4605 | 44605 | NSX[2].ActivePowerL1_kW
ST2NSX2ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4607 | 44607 | NSX[2].ActivePowerL2_kW
ST2NSX2ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4609 | 44609 | NSX[2].ActivePowerL3_kW
ST2NSX2ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 4611 | 44611 | NSX[2].ActivePowerMaxDemand_kW
ST2NSX2ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4613 | 44613 | NSX[2].ActivePowerTotal_kW
ST2NSX2ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 4615 | 44615 | NSX[2].ApparentEnergy_kVAh
ST2NSX2ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 4617 | 44617 | NSX[2].ApparentPowerDemand_kVA
ST2NSX2ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 4619 | 44619 | NSX[2].ApparentPowerMaxDemand_kVA
ST2NSX2ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4621 | 44621 | NSX[2].ApparetnPowerL1_kVA
ST2NSX2ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4623 | 44623 | NSX[2].ApparetnPowerL2_kVA
ST2NSX2ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4625 | 44625 | NSX[2].ApparetnPowerL3_kVA
ST2NSX2ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4627 | 44627 | NSX[2].ApparetnPowerTotal_kVA
ST2NSX2CosFL1 | REAL | IOD_ST2_TCP | 4629 | 44629 | NSX[2].CosFL1
ST2NSX2CosFL2 | REAL | IOD_ST2_TCP | 4631 | 44631 | NSX[2].CosFL2
ST2NSX2CosFL3 | REAL | IOD_ST2_TCP | 4633 | 44633 | NSX[2].CosFL3
ST2NSX2CosFTotal | REAL | IOD_ST2_TCP | 4635 | 44635 | NSX[2].CosFTotal
ST2NSX2CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4637 | 44637 | NSX[2].CumulNegativeActiveEnergy_kWh
ST2NSX2CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 4639 | 44639 | NSX[2].CumulPositiveActiveEnergy_kWh
ST2NSX2CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4641 | 44641 | NSX[2].CurrentAvgI1I2I3_A
ST2NSX2CurrentDemandL1_A | REAL | IOD_ST2_TCP | 4643 | 44643 | NSX[2].CurrentDemandL1_A
ST2NSX2CurrentDemandL2_A | REAL | IOD_ST2_TCP | 4645 | 44645 | NSX[2].CurrentDemandL2_A
ST2NSX2CurrentDemandL3_A | REAL | IOD_ST2_TCP | 4647 | 44647 | NSX[2].CurrentDemandL3_A
ST2NSX2CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 4649 | 44649 | NSX[2].CurrentDemandMaxL1_A
ST2NSX2CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 4651 | 44651 | NSX[2].CurrentDemandMaxL2_A
ST2NSX2CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 4653 | 44653 | NSX[2].CurrentDemandMaxL3_A
ST2NSX2CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 4655 | 44655 | NSX[2].CurrentDemandMaxN_A
ST2NSX2CurrentDemandN_A | REAL | IOD_ST2_TCP | 4657 | 44657 | NSX[2].CurrentDemandN_A
ST2NSX2CurrentL1_A | REAL | IOD_ST2_TCP | 4659 | 44659 | NSX[2].CurrentL1_A
ST2NSX2CurrentL2_A | REAL | IOD_ST2_TCP | 4661 | 44661 | NSX[2].CurrentL2_A
ST2NSX2CurrentL3_A | REAL | IOD_ST2_TCP | 4663 | 44663 | NSX[2].CurrentL3_A
ST2NSX2CurrentN_A | REAL | IOD_ST2_TCP | 4665 | 44665 | NSX[2].CurrentN_A
ST2NSX2CurrentUnbI1_P | REAL | IOD_ST2_TCP | 4667 | 44667 | NSX[2].CurrentUnbI1_P
ST2NSX2CurrentUnbI2_P | REAL | IOD_ST2_TCP | 4669 | 44669 | NSX[2].CurrentUnbI2_P
ST2NSX2CurrentUnbI3_P | REAL | IOD_ST2_TCP | 4671 | 44671 | NSX[2].CurrentUnbI3_P
ST2NSX2CurrentUnbN_P | REAL | IOD_ST2_TCP | 4673 | 44673 | NSX[2].CurrentUnbN_P
ST2NSX2DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 4675 | 44675 | NSX[2].DelovnaEnergija_TEMP
ST2NSX2DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4677 | 44677 | NSX[2].DistortionPowerL1_kVAr
ST2NSX2DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4679 | 44679 | NSX[2].DistortionPowerL2_kVAr
ST2NSX2DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4681 | 44681 | NSX[2].DistortionPowerL3_kVAr
ST2NSX2DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4683 | 44683 | NSX[2].DistortionPowerTotal_kVAr
ST2NSX2Frequency_Hz | REAL | IOD_ST2_TCP | 4685 | 44685 | NSX[2].Frequency_Hz
ST2NSX2FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4687 | 44687 | NSX[2].FunReactivePowerL1_kVAr
ST2NSX2FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4689 | 44689 | NSX[2].FunReactivePowerL2_kVAr
ST2NSX2FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4691 | 44691 | NSX[2].FunReactivePowerL3_kVAr
ST2NSX2FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4693 | 44693 | NSX[2].FunReactivePowerTotal_kVAr
ST2NSX2MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4695 | 44695 | NSX[2].MAX_ActivePowerL1_kW
ST2NSX2MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4697 | 44697 | NSX[2].MAX_ActivePowerL2_kW
ST2NSX2MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4699 | 44699 | NSX[2].MAX_ActivePowerL3_kW
ST2NSX2MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4701 | 44701 | NSX[2].MAX_ActivePowerTotal_kW
ST2NSX2MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4703 | 44703 | NSX[2].MAX_ApparetnPowerL1_kVA
ST2NSX2MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4705 | 44705 | NSX[2].MAX_ApparetnPowerL2_kVA
ST2NSX2MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4707 | 44707 | NSX[2].MAX_ApparetnPowerL3_kVA
ST2NSX2MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4709 | 44709 | NSX[2].MAX_ApparetnPowerTotal_kVA
ST2NSX2MAX_CosFL1 | REAL | IOD_ST2_TCP | 4711 | 44711 | NSX[2].MAX_CosFL1
ST2NSX2MAX_CosFL2 | REAL | IOD_ST2_TCP | 4713 | 44713 | NSX[2].MAX_CosFL2
ST2NSX2MAX_CosFL3 | REAL | IOD_ST2_TCP | 4715 | 44715 | NSX[2].MAX_CosFL3
ST2NSX2MAX_CosFTotal | REAL | IOD_ST2_TCP | 4717 | 44717 | NSX[2].MAX_CosFTotal
ST2NSX2MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4719 | 44719 | NSX[2].MAX_CurrentAvgI1I2I3_A
ST2NSX2MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 4721 | 44721 | NSX[2].MAX_CurrentL1_A
ST2NSX2MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 4723 | 44723 | NSX[2].MAX_CurrentL2_A
ST2NSX2MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 4725 | 44725 | NSX[2].MAX_CurrentL3_A
ST2NSX2MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 4727 | 44727 | NSX[2].MAX_CurrentMaxL1L2L3N_A
ST2NSX2MAX_CurrentN_A | REAL | IOD_ST2_TCP | 4729 | 44729 | NSX[2].MAX_CurrentN_A
ST2NSX2MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4731 | 44731 | NSX[2].MAX_DistortionPowerL1_kVAr
ST2NSX2MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4733 | 44733 | NSX[2].MAX_DistortionPowerL2_kVAr
ST2NSX2MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4735 | 44735 | NSX[2].MAX_DistortionPowerL3_kVAr
ST2NSX2MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4737 | 44737 | NSX[2].MAX_DistortionPowerTotal_kVAr
ST2NSX2MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 4739 | 44739 | NSX[2].MAX_Frequency_Hz
ST2NSX2MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4741 | 44741 | NSX[2].MAX_FunReactivePowerL1_kVAr
ST2NSX2MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4743 | 44743 | NSX[2].MAX_FunReactivePowerL2_kVAr
ST2NSX2MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4745 | 44745 | NSX[2].MAX_FunReactivePowerL3_kVAr
ST2NSX2MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4747 | 44747 | NSX[2].MAX_FunReactivePowerTotal_kVAr
ST2NSX2MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 4749 | 44749 | NSX[2].MAX_PowerFactorL1
ST2NSX2MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 4751 | 44751 | NSX[2].MAX_PowerFactorL2
ST2NSX2MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 4753 | 44753 | NSX[2].MAX_PowerFactorL3
ST2NSX2MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 4755 | 44755 | NSX[2].MAX_PowerFactorTotal
ST2NSX2MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4757 | 44757 | NSX[2].MAX_ReactivePowerL1_kVAr
ST2NSX2MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4759 | 44759 | NSX[2].MAX_ReactivePowerL2_kVAr
ST2NSX2MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4761 | 44761 | NSX[2].MAX_ReactivePowerL3_kVAr
ST2NSX2MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4763 | 44763 | NSX[2].MAX_ReactivePowerTotal_kVAr
ST2NSX2MAX_THDI1_P | REAL | IOD_ST2_TCP | 4765 | 44765 | NSX[2].MAX_THDI1_P
ST2NSX2MAX_THDI2_P | REAL | IOD_ST2_TCP | 4767 | 44767 | NSX[2].MAX_THDI2_P
ST2NSX2MAX_THDI3_P | REAL | IOD_ST2_TCP | 4769 | 44769 | NSX[2].MAX_THDI3_P
ST2NSX2MAX_THDV12_P | REAL | IOD_ST2_TCP | 4771 | 44771 | NSX[2].MAX_THDV12_P
ST2NSX2MAX_THDV1N_P | REAL | IOD_ST2_TCP | 4773 | 44773 | NSX[2].MAX_THDV1N_P
ST2NSX2MAX_THDV23_P | REAL | IOD_ST2_TCP | 4775 | 44775 | NSX[2].MAX_THDV23_P
ST2NSX2MAX_THDV2N_P | REAL | IOD_ST2_TCP | 4777 | 44777 | NSX[2].MAX_THDV2N_P
ST2NSX2MAX_THDV31_P | REAL | IOD_ST2_TCP | 4779 | 44779 | NSX[2].MAX_THDV31_P
ST2NSX2MAX_THDV3N_P | REAL | IOD_ST2_TCP | 4781 | 44781 | NSX[2].MAX_THDV3N_P
ST2NSX2MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4783 | 44783 | NSX[2].MAX_VoltageAvgPhToN_V
ST2NSX2MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4785 | 44785 | NSX[2].MAX_VoltageAvgPhToPh_V
ST2NSX2MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4787 | 44787 | NSX[2].MAX_VoltageUnbV12_P
ST2NSX2MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4789 | 44789 | NSX[2].MAX_VoltageUnbV1N_P
ST2NSX2MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4791 | 44791 | NSX[2].MAX_VoltageUnbV23_P
ST2NSX2MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4793 | 44793 | NSX[2].MAX_VoltageUnbV2N_P
ST2NSX2MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 4795 | 44795 | NSX[2].MAX_VoltageUnbV31_P
ST2NSX2MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 4797 | 44797 | NSX[2].MAX_VoltageUnbV3N_P
ST2NSX2MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 4799 | 44799 | NSX[2].MAX_VoltageV12_V
ST2NSX2MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 4801 | 44801 | NSX[2].MAX_VoltageV1N_V
ST2NSX2MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 4803 | 44803 | NSX[2].MAX_VoltageV23_V
ST2NSX2MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 4805 | 44805 | NSX[2].MAX_VoltageV2N_V
ST2NSX2MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 4807 | 44807 | NSX[2].MAX_VoltageV31_V
ST2NSX2MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 4809 | 44809 | NSX[2].MAX_VoltageV3N_V
ST2NSX2MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 4811 | 44811 | NSX[2].MIN_ActivePowerL1_kW
ST2NSX2MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 4813 | 44813 | NSX[2].MIN_ActivePowerL2_kW
ST2NSX2MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 4815 | 44815 | NSX[2].MIN_ActivePowerL3_kW
ST2NSX2MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 4817 | 44817 | NSX[2].MIN_ActivePowerTotal_kW
ST2NSX2MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 4819 | 44819 | NSX[2].MIN_ApparetnPowerL1_kVA
ST2NSX2MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 4821 | 44821 | NSX[2].MIN_ApparetnPowerL2_kVA
ST2NSX2MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 4823 | 44823 | NSX[2].MIN_ApparetnPowerL3_kVA
ST2NSX2MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 4825 | 44825 | NSX[2].MIN_ApparetnPowerTotal_kVA
ST2NSX2MIN_CosFL1 | REAL | IOD_ST2_TCP | 4827 | 44827 | NSX[2].MIN_CosFL1
ST2NSX2MIN_CosFL2 | REAL | IOD_ST2_TCP | 4829 | 44829 | NSX[2].MIN_CosFL2
ST2NSX2MIN_CosFL3 | REAL | IOD_ST2_TCP | 4831 | 44831 | NSX[2].MIN_CosFL3
ST2NSX2MIN_CosFTotal | REAL | IOD_ST2_TCP | 4833 | 44833 | NSX[2].MIN_CosFTotal
ST2NSX2MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 4835 | 44835 | NSX[2].MIN_CurrentAvgI1I2I3_A
ST2NSX2MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 4837 | 44837 | NSX[2].MIN_CurrentL1_A
ST2NSX2MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 4839 | 44839 | NSX[2].MIN_CurrentL2_A
ST2NSX2MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 4841 | 44841 | NSX[2].MIN_CurrentL3_A
ST2NSX2MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 4843 | 44843 | NSX[2].MIN_CurrentMaxL1L2L3N_A
ST2NSX2MIN_CurrentN_A | REAL | IOD_ST2_TCP | 4845 | 44845 | NSX[2].MIN_CurrentN_A
ST2NSX2MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 4847 | 44847 | NSX[2].MIN_DistortionPowerL1_kVAr
ST2NSX2MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 4849 | 44849 | NSX[2].MIN_DistortionPowerL2_kVAr
ST2NSX2MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 4851 | 44851 | NSX[2].MIN_DistortionPowerL3_kVAr
ST2NSX2MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 4853 | 44853 | NSX[2].MIN_DistortionPowerTotal_kVAr
ST2NSX2MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 4855 | 44855 | NSX[2].MIN_Frequency_Hz
ST2NSX2MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4857 | 44857 | NSX[2].MIN_FunReactivePowerL1_kVAr
ST2NSX2MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4859 | 44859 | NSX[2].MIN_FunReactivePowerL2_kVAr
ST2NSX2MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4861 | 44861 | NSX[2].MIN_FunReactivePowerL3_kVAr
ST2NSX2MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4863 | 44863 | NSX[2].MIN_FunReactivePowerTotal_kVAr
ST2NSX2MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 4865 | 44865 | NSX[2].MIN_PowerFactorL1
ST2NSX2MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 4867 | 44867 | NSX[2].MIN_PowerFactorL2
ST2NSX2MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 4869 | 44869 | NSX[2].MIN_PowerFactorL3
ST2NSX2MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 4871 | 44871 | NSX[2].MIN_PowerFactorTotal
ST2NSX2MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4873 | 44873 | NSX[2].MIN_ReactivePowerL1_kVAr
ST2NSX2MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4875 | 44875 | NSX[2].MIN_ReactivePowerL2_kVAr
ST2NSX2MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4877 | 44877 | NSX[2].MIN_ReactivePowerL3_kVAr
ST2NSX2MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4879 | 44879 | NSX[2].MIN_ReactivePowerTotal_kVAr
ST2NSX2MIN_THDI1_P | REAL | IOD_ST2_TCP | 4881 | 44881 | NSX[2].MIN_THDI1_P
ST2NSX2MIN_THDI2_P | REAL | IOD_ST2_TCP | 4883 | 44883 | NSX[2].MIN_THDI2_P
ST2NSX2MIN_THDI3_P | REAL | IOD_ST2_TCP | 4885 | 44885 | NSX[2].MIN_THDI3_P
ST2NSX2MIN_THDV12_P | REAL | IOD_ST2_TCP | 4887 | 44887 | NSX[2].MIN_THDV12_P
ST2NSX2MIN_THDV1N_P | REAL | IOD_ST2_TCP | 4889 | 44889 | NSX[2].MIN_THDV1N_P
ST2NSX2MIN_THDV23_P | REAL | IOD_ST2_TCP | 4891 | 44891 | NSX[2].MIN_THDV23_P
ST2NSX2MIN_THDV2N_P | REAL | IOD_ST2_TCP | 4893 | 44893 | NSX[2].MIN_THDV2N_P
ST2NSX2MIN_THDV31_P | REAL | IOD_ST2_TCP | 4895 | 44895 | NSX[2].MIN_THDV31_P
ST2NSX2MIN_THDV3N_P | REAL | IOD_ST2_TCP | 4897 | 44897 | NSX[2].MIN_THDV3N_P
ST2NSX2MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4899 | 44899 | NSX[2].MIN_VoltageAvgPhToN_V
ST2NSX2MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4901 | 44901 | NSX[2].MIN_VoltageAvgPhToPh_V
ST2NSX2MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4903 | 44903 | NSX[2].MIN_VoltageUnbV12_P
ST2NSX2MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4905 | 44905 | NSX[2].MIN_VoltageUnbV1N_P
ST2NSX2MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4907 | 44907 | NSX[2].MIN_VoltageUnbV23_P
ST2NSX2MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4909 | 44909 | NSX[2].MIN_VoltageUnbV2N_P
ST2NSX2MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 4911 | 44911 | NSX[2].MIN_VoltageUnbV31_P
ST2NSX2MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 4913 | 44913 | NSX[2].MIN_VoltageUnbV3N_P
ST2NSX2MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 4915 | 44915 | NSX[2].MIN_VoltageV12_V
ST2NSX2MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 4917 | 44917 | NSX[2].MIN_VoltageV1N_V
ST2NSX2MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 4919 | 44919 | NSX[2].MIN_VoltageV23_V
ST2NSX2MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 4921 | 44921 | NSX[2].MIN_VoltageV2N_V
ST2NSX2MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 4923 | 44923 | NSX[2].MIN_VoltageV31_V
ST2NSX2MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 4925 | 44925 | NSX[2].MIN_VoltageV3N_V
ST2NSX2PowerFactorL1 | REAL | IOD_ST2_TCP | 4927 | 44927 | NSX[2].PowerFactorL1
ST2NSX2PowerFactorL2 | REAL | IOD_ST2_TCP | 4929 | 44929 | NSX[2].PowerFactorL2
ST2NSX2PowerFactorL3 | REAL | IOD_ST2_TCP | 4931 | 44931 | NSX[2].PowerFactorL3
ST2NSX2PowerFactorTotal | REAL | IOD_ST2_TCP | 4933 | 44933 | NSX[2].PowerFactorTotal
ST2NSX2RazEner_D | REAL | IOD_ST2_TCP | 4935 | 44935 | NSX[2].RazEner_D
ST2NSX2RazEner_D_SCADA | REAL | IOD_ST2_TCP | 4937 | 44937 | NSX[2].RazEner_D_SCADA
ST2NSX2RazEner_D_TEMP | REAL | IOD_ST2_TCP | 4939 | 44939 | NSX[2].RazEner_D_TEMP
ST2NSX2RazEner_M | REAL | IOD_ST2_TCP | 4941 | 44941 | NSX[2].RazEner_M
ST2NSX2RazEner_M_SCADA | REAL | IOD_ST2_TCP | 4943 | 44943 | NSX[2].RazEner_M_SCADA
ST2NSX2RazEner_M_TEMP | REAL | IOD_ST2_TCP | 4945 | 44945 | NSX[2].RazEner_M_TEMP
ST2NSX2RazEner_T | REAL | IOD_ST2_TCP | 4947 | 44947 | NSX[2].RazEner_T
ST2NSX2RazEner_T_SCADA | REAL | IOD_ST2_TCP | 4949 | 44949 | NSX[2].RazEner_T_SCADA
ST2NSX2RazEner_T_TEMP | REAL | IOD_ST2_TCP | 4951 | 44951 | NSX[2].RazEner_T_TEMP
ST2NSX2ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 4953 | 44953 | NSX[2].ReactiveEnergy_kVArh
ST2NSX2ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 4955 | 44955 | NSX[2].ReactiveNegativeEnergy_kVArh
ST2NSX2ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 4957 | 44957 | NSX[2].ReactivePositiveEnergy_kVArh
ST2NSX2ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 4959 | 44959 | NSX[2].ReactivePowerDemand_kVAr
ST2NSX2ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 4961 | 44961 | NSX[2].ReactivePowerL1_kVAr
ST2NSX2ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 4963 | 44963 | NSX[2].ReactivePowerL2_kVAr
ST2NSX2ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 4965 | 44965 | NSX[2].ReactivePowerL3_kVAr
ST2NSX2ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 4967 | 44967 | NSX[2].ReactivePowerMaxDemand_kVAr
ST2NSX2ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 4969 | 44969 | NSX[2].ReactivePowerTotal_kVAr
ST2NSX2THDI1_P | REAL | IOD_ST2_TCP | 4971 | 44971 | NSX[2].THDI1_P
ST2NSX2THDI2_P | REAL | IOD_ST2_TCP | 4973 | 44973 | NSX[2].THDI2_P
ST2NSX2THDI3_P | REAL | IOD_ST2_TCP | 4975 | 44975 | NSX[2].THDI3_P
ST2NSX2THDV12_P | REAL | IOD_ST2_TCP | 4977 | 44977 | NSX[2].THDV12_P
ST2NSX2THDV1N_P | REAL | IOD_ST2_TCP | 4979 | 44979 | NSX[2].THDV1N_P
ST2NSX2THDV23_P | REAL | IOD_ST2_TCP | 4981 | 44981 | NSX[2].THDV23_P
ST2NSX2THDV2N_P | REAL | IOD_ST2_TCP | 4983 | 44983 | NSX[2].THDV2N_P
ST2NSX2THDV31_P | REAL | IOD_ST2_TCP | 4985 | 44985 | NSX[2].THDV31_P
ST2NSX2THDV3N_P | REAL | IOD_ST2_TCP | 4987 | 44987 | NSX[2].THDV3N_P
ST2NSX2VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 4989 | 44989 | NSX[2].VoltageAvgPhToN_V
ST2NSX2VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 4991 | 44991 | NSX[2].VoltageAvgPhToPh_V
ST2NSX2VoltageUnbV12_P | REAL | IOD_ST2_TCP | 4993 | 44993 | NSX[2].VoltageUnbV12_P
ST2NSX2VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 4995 | 44995 | NSX[2].VoltageUnbV1N_P
ST2NSX2VoltageUnbV23_P | REAL | IOD_ST2_TCP | 4997 | 44997 | NSX[2].VoltageUnbV23_P
ST2NSX2VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 4999 | 44999 | NSX[2].VoltageUnbV2N_P
ST2NSX2VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5001 | 45001 | NSX[2].VoltageUnbV31_P
ST2NSX2VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5003 | 45003 | NSX[2].VoltageUnbV3N_P
ST2NSX2VoltageV12_V | REAL | IOD_ST2_TCP | 5005 | 45005 | NSX[2].VoltageV12_V
ST2NSX2VoltageV1N_V | REAL | IOD_ST2_TCP | 5007 | 45007 | NSX[2].VoltageV1N_V
ST2NSX2VoltageV23_V | REAL | IOD_ST2_TCP | 5009 | 45009 | NSX[2].VoltageV23_V
ST2NSX2VoltageV2N_V | REAL | IOD_ST2_TCP | 5011 | 45011 | NSX[2].VoltageV2N_V
ST2NSX2VoltageV31_V | REAL | IOD_ST2_TCP | 5013 | 45013 | NSX[2].VoltageV31_V
ST2NSX2VoltageV3N_V | REAL | IOD_ST2_TCP | 5015 | 45015 | NSX[2].VoltageV3N_V
ST2NSX3ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5017 | 45017 | NSX[3].ActiveEnergy_kWh
ST2NSX3ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 5019 | 45019 | NSX[3].ActiveNegativeEnergy_kWh
ST2NSX3ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 5021 | 45021 | NSX[3].ActivePositiveEnergy_kWh
ST2NSX3ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 5023 | 45023 | NSX[3].ActivePowerDemand_kW
ST2NSX3ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5025 | 45025 | NSX[3].ActivePowerL1_kW
ST2NSX3ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5027 | 45027 | NSX[3].ActivePowerL2_kW
ST2NSX3ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5029 | 45029 | NSX[3].ActivePowerL3_kW
ST2NSX3ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 5031 | 45031 | NSX[3].ActivePowerMaxDemand_kW
ST2NSX3ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5033 | 45033 | NSX[3].ActivePowerTotal_kW
ST2NSX3ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 5035 | 45035 | NSX[3].ApparentEnergy_kVAh
ST2NSX3ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 5037 | 45037 | NSX[3].ApparentPowerDemand_kVA
ST2NSX3ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 5039 | 45039 | NSX[3].ApparentPowerMaxDemand_kVA
ST2NSX3ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5041 | 45041 | NSX[3].ApparetnPowerL1_kVA
ST2NSX3ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5043 | 45043 | NSX[3].ApparetnPowerL2_kVA
ST2NSX3ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5045 | 45045 | NSX[3].ApparetnPowerL3_kVA
ST2NSX3ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5047 | 45047 | NSX[3].ApparetnPowerTotal_kVA
ST2NSX3CosFL1 | REAL | IOD_ST2_TCP | 5049 | 45049 | NSX[3].CosFL1
ST2NSX3CosFL2 | REAL | IOD_ST2_TCP | 5051 | 45051 | NSX[3].CosFL2
ST2NSX3CosFL3 | REAL | IOD_ST2_TCP | 5053 | 45053 | NSX[3].CosFL3
ST2NSX3CosFTotal | REAL | IOD_ST2_TCP | 5055 | 45055 | NSX[3].CosFTotal
ST2NSX3CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5057 | 45057 | NSX[3].CumulNegativeActiveEnergy_kWh
ST2NSX3CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5059 | 45059 | NSX[3].CumulPositiveActiveEnergy_kWh
ST2NSX3CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5061 | 45061 | NSX[3].CurrentAvgI1I2I3_A
ST2NSX3CurrentDemandL1_A | REAL | IOD_ST2_TCP | 5063 | 45063 | NSX[3].CurrentDemandL1_A
ST2NSX3CurrentDemandL2_A | REAL | IOD_ST2_TCP | 5065 | 45065 | NSX[3].CurrentDemandL2_A
ST2NSX3CurrentDemandL3_A | REAL | IOD_ST2_TCP | 5067 | 45067 | NSX[3].CurrentDemandL3_A
ST2NSX3CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 5069 | 45069 | NSX[3].CurrentDemandMaxL1_A
ST2NSX3CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 5071 | 45071 | NSX[3].CurrentDemandMaxL2_A
ST2NSX3CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 5073 | 45073 | NSX[3].CurrentDemandMaxL3_A
ST2NSX3CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 5075 | 45075 | NSX[3].CurrentDemandMaxN_A
ST2NSX3CurrentDemandN_A | REAL | IOD_ST2_TCP | 5077 | 45077 | NSX[3].CurrentDemandN_A
ST2NSX3CurrentL1_A | REAL | IOD_ST2_TCP | 5079 | 45079 | NSX[3].CurrentL1_A
ST2NSX3CurrentL2_A | REAL | IOD_ST2_TCP | 5081 | 45081 | NSX[3].CurrentL2_A
ST2NSX3CurrentL3_A | REAL | IOD_ST2_TCP | 5083 | 45083 | NSX[3].CurrentL3_A
ST2NSX3CurrentN_A | REAL | IOD_ST2_TCP | 5085 | 45085 | NSX[3].CurrentN_A
ST2NSX3CurrentUnbI1_P | REAL | IOD_ST2_TCP | 5087 | 45087 | NSX[3].CurrentUnbI1_P
ST2NSX3CurrentUnbI2_P | REAL | IOD_ST2_TCP | 5089 | 45089 | NSX[3].CurrentUnbI2_P
ST2NSX3CurrentUnbI3_P | REAL | IOD_ST2_TCP | 5091 | 45091 | NSX[3].CurrentUnbI3_P
ST2NSX3CurrentUnbN_P | REAL | IOD_ST2_TCP | 5093 | 45093 | NSX[3].CurrentUnbN_P
ST2NSX3DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 5095 | 45095 | NSX[3].DelovnaEnergija_TEMP
ST2NSX3DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5097 | 45097 | NSX[3].DistortionPowerL1_kVAr
ST2NSX3DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5099 | 45099 | NSX[3].DistortionPowerL2_kVAr
ST2NSX3DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5101 | 45101 | NSX[3].DistortionPowerL3_kVAr
ST2NSX3DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5103 | 45103 | NSX[3].DistortionPowerTotal_kVAr
ST2NSX3Frequency_Hz | REAL | IOD_ST2_TCP | 5105 | 45105 | NSX[3].Frequency_Hz
ST2NSX3FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5107 | 45107 | NSX[3].FunReactivePowerL1_kVAr
ST2NSX3FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5109 | 45109 | NSX[3].FunReactivePowerL2_kVAr
ST2NSX3FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5111 | 45111 | NSX[3].FunReactivePowerL3_kVAr
ST2NSX3FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5113 | 45113 | NSX[3].FunReactivePowerTotal_kVAr
ST2NSX3MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5115 | 45115 | NSX[3].MAX_ActivePowerL1_kW
ST2NSX3MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5117 | 45117 | NSX[3].MAX_ActivePowerL2_kW
ST2NSX3MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5119 | 45119 | NSX[3].MAX_ActivePowerL3_kW
ST2NSX3MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5121 | 45121 | NSX[3].MAX_ActivePowerTotal_kW
ST2NSX3MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5123 | 45123 | NSX[3].MAX_ApparetnPowerL1_kVA
ST2NSX3MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5125 | 45125 | NSX[3].MAX_ApparetnPowerL2_kVA
ST2NSX3MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5127 | 45127 | NSX[3].MAX_ApparetnPowerL3_kVA
ST2NSX3MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5129 | 45129 | NSX[3].MAX_ApparetnPowerTotal_kVA
ST2NSX3MAX_CosFL1 | REAL | IOD_ST2_TCP | 5131 | 45131 | NSX[3].MAX_CosFL1
ST2NSX3MAX_CosFL2 | REAL | IOD_ST2_TCP | 5133 | 45133 | NSX[3].MAX_CosFL2
ST2NSX3MAX_CosFL3 | REAL | IOD_ST2_TCP | 5135 | 45135 | NSX[3].MAX_CosFL3
ST2NSX3MAX_CosFTotal | REAL | IOD_ST2_TCP | 5137 | 45137 | NSX[3].MAX_CosFTotal
ST2NSX3MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5139 | 45139 | NSX[3].MAX_CurrentAvgI1I2I3_A
ST2NSX3MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 5141 | 45141 | NSX[3].MAX_CurrentL1_A
ST2NSX3MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 5143 | 45143 | NSX[3].MAX_CurrentL2_A
ST2NSX3MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 5145 | 45145 | NSX[3].MAX_CurrentL3_A
ST2NSX3MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 5147 | 45147 | NSX[3].MAX_CurrentMaxL1L2L3N_A
ST2NSX3MAX_CurrentN_A | REAL | IOD_ST2_TCP | 5149 | 45149 | NSX[3].MAX_CurrentN_A
ST2NSX3MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5151 | 45151 | NSX[3].MAX_DistortionPowerL1_kVAr
ST2NSX3MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5153 | 45153 | NSX[3].MAX_DistortionPowerL2_kVAr
ST2NSX3MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5155 | 45155 | NSX[3].MAX_DistortionPowerL3_kVAr
ST2NSX3MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5157 | 45157 | NSX[3].MAX_DistortionPowerTotal_kVAr
ST2NSX3MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 5159 | 45159 | NSX[3].MAX_Frequency_Hz
ST2NSX3MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5161 | 45161 | NSX[3].MAX_FunReactivePowerL1_kVAr
ST2NSX3MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5163 | 45163 | NSX[3].MAX_FunReactivePowerL2_kVAr
ST2NSX3MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5165 | 45165 | NSX[3].MAX_FunReactivePowerL3_kVAr
ST2NSX3MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5167 | 45167 | NSX[3].MAX_FunReactivePowerTotal_kVAr
ST2NSX3MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 5169 | 45169 | NSX[3].MAX_PowerFactorL1
ST2NSX3MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 5171 | 45171 | NSX[3].MAX_PowerFactorL2
ST2NSX3MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 5173 | 45173 | NSX[3].MAX_PowerFactorL3
ST2NSX3MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 5175 | 45175 | NSX[3].MAX_PowerFactorTotal
ST2NSX3MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5177 | 45177 | NSX[3].MAX_ReactivePowerL1_kVAr
ST2NSX3MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5179 | 45179 | NSX[3].MAX_ReactivePowerL2_kVAr
ST2NSX3MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5181 | 45181 | NSX[3].MAX_ReactivePowerL3_kVAr
ST2NSX3MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5183 | 45183 | NSX[3].MAX_ReactivePowerTotal_kVAr
ST2NSX3MAX_THDI1_P | REAL | IOD_ST2_TCP | 5185 | 45185 | NSX[3].MAX_THDI1_P
ST2NSX3MAX_THDI2_P | REAL | IOD_ST2_TCP | 5187 | 45187 | NSX[3].MAX_THDI2_P
ST2NSX3MAX_THDI3_P | REAL | IOD_ST2_TCP | 5189 | 45189 | NSX[3].MAX_THDI3_P
ST2NSX3MAX_THDV12_P | REAL | IOD_ST2_TCP | 5191 | 45191 | NSX[3].MAX_THDV12_P
ST2NSX3MAX_THDV1N_P | REAL | IOD_ST2_TCP | 5193 | 45193 | NSX[3].MAX_THDV1N_P
ST2NSX3MAX_THDV23_P | REAL | IOD_ST2_TCP | 5195 | 45195 | NSX[3].MAX_THDV23_P
ST2NSX3MAX_THDV2N_P | REAL | IOD_ST2_TCP | 5197 | 45197 | NSX[3].MAX_THDV2N_P
ST2NSX3MAX_THDV31_P | REAL | IOD_ST2_TCP | 5199 | 45199 | NSX[3].MAX_THDV31_P
ST2NSX3MAX_THDV3N_P | REAL | IOD_ST2_TCP | 5201 | 45201 | NSX[3].MAX_THDV3N_P
ST2NSX3MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5203 | 45203 | NSX[3].MAX_VoltageAvgPhToN_V
ST2NSX3MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5205 | 45205 | NSX[3].MAX_VoltageAvgPhToPh_V
ST2NSX3MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5207 | 45207 | NSX[3].MAX_VoltageUnbV12_P
ST2NSX3MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5209 | 45209 | NSX[3].MAX_VoltageUnbV1N_P
ST2NSX3MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5211 | 45211 | NSX[3].MAX_VoltageUnbV23_P
ST2NSX3MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5213 | 45213 | NSX[3].MAX_VoltageUnbV2N_P
ST2NSX3MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5215 | 45215 | NSX[3].MAX_VoltageUnbV31_P
ST2NSX3MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5217 | 45217 | NSX[3].MAX_VoltageUnbV3N_P
ST2NSX3MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 5219 | 45219 | NSX[3].MAX_VoltageV12_V
ST2NSX3MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 5221 | 45221 | NSX[3].MAX_VoltageV1N_V
ST2NSX3MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 5223 | 45223 | NSX[3].MAX_VoltageV23_V
ST2NSX3MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 5225 | 45225 | NSX[3].MAX_VoltageV2N_V
ST2NSX3MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 5227 | 45227 | NSX[3].MAX_VoltageV31_V
ST2NSX3MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 5229 | 45229 | NSX[3].MAX_VoltageV3N_V
ST2NSX3MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5231 | 45231 | NSX[3].MIN_ActivePowerL1_kW
ST2NSX3MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5233 | 45233 | NSX[3].MIN_ActivePowerL2_kW
ST2NSX3MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5235 | 45235 | NSX[3].MIN_ActivePowerL3_kW
ST2NSX3MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5237 | 45237 | NSX[3].MIN_ActivePowerTotal_kW
ST2NSX3MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5239 | 45239 | NSX[3].MIN_ApparetnPowerL1_kVA
ST2NSX3MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5241 | 45241 | NSX[3].MIN_ApparetnPowerL2_kVA
ST2NSX3MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5243 | 45243 | NSX[3].MIN_ApparetnPowerL3_kVA
ST2NSX3MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5245 | 45245 | NSX[3].MIN_ApparetnPowerTotal_kVA
ST2NSX3MIN_CosFL1 | REAL | IOD_ST2_TCP | 5247 | 45247 | NSX[3].MIN_CosFL1
ST2NSX3MIN_CosFL2 | REAL | IOD_ST2_TCP | 5249 | 45249 | NSX[3].MIN_CosFL2
ST2NSX3MIN_CosFL3 | REAL | IOD_ST2_TCP | 5251 | 45251 | NSX[3].MIN_CosFL3
ST2NSX3MIN_CosFTotal | REAL | IOD_ST2_TCP | 5253 | 45253 | NSX[3].MIN_CosFTotal
ST2NSX3MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5255 | 45255 | NSX[3].MIN_CurrentAvgI1I2I3_A
ST2NSX3MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 5257 | 45257 | NSX[3].MIN_CurrentL1_A
ST2NSX3MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 5259 | 45259 | NSX[3].MIN_CurrentL2_A
ST2NSX3MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 5261 | 45261 | NSX[3].MIN_CurrentL3_A
ST2NSX3MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 5263 | 45263 | NSX[3].MIN_CurrentMaxL1L2L3N_A
ST2NSX3MIN_CurrentN_A | REAL | IOD_ST2_TCP | 5265 | 45265 | NSX[3].MIN_CurrentN_A
ST2NSX3MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5267 | 45267 | NSX[3].MIN_DistortionPowerL1_kVAr
ST2NSX3MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5269 | 45269 | NSX[3].MIN_DistortionPowerL2_kVAr
ST2NSX3MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5271 | 45271 | NSX[3].MIN_DistortionPowerL3_kVAr
ST2NSX3MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5273 | 45273 | NSX[3].MIN_DistortionPowerTotal_kVAr
ST2NSX3MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 5275 | 45275 | NSX[3].MIN_Frequency_Hz
ST2NSX3MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5277 | 45277 | NSX[3].MIN_FunReactivePowerL1_kVAr
ST2NSX3MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5279 | 45279 | NSX[3].MIN_FunReactivePowerL2_kVAr
ST2NSX3MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5281 | 45281 | NSX[3].MIN_FunReactivePowerL3_kVAr
ST2NSX3MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5283 | 45283 | NSX[3].MIN_FunReactivePowerTotal_kVAr
ST2NSX3MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 5285 | 45285 | NSX[3].MIN_PowerFactorL1
ST2NSX3MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 5287 | 45287 | NSX[3].MIN_PowerFactorL2
ST2NSX3MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 5289 | 45289 | NSX[3].MIN_PowerFactorL3
ST2NSX3MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 5291 | 45291 | NSX[3].MIN_PowerFactorTotal
ST2NSX3MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5293 | 45293 | NSX[3].MIN_ReactivePowerL1_kVAr
ST2NSX3MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5295 | 45295 | NSX[3].MIN_ReactivePowerL2_kVAr
ST2NSX3MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5297 | 45297 | NSX[3].MIN_ReactivePowerL3_kVAr
ST2NSX3MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5299 | 45299 | NSX[3].MIN_ReactivePowerTotal_kVAr
ST2NSX3MIN_THDI1_P | REAL | IOD_ST2_TCP | 5301 | 45301 | NSX[3].MIN_THDI1_P
ST2NSX3MIN_THDI2_P | REAL | IOD_ST2_TCP | 5303 | 45303 | NSX[3].MIN_THDI2_P
ST2NSX3MIN_THDI3_P | REAL | IOD_ST2_TCP | 5305 | 45305 | NSX[3].MIN_THDI3_P
ST2NSX3MIN_THDV12_P | REAL | IOD_ST2_TCP | 5307 | 45307 | NSX[3].MIN_THDV12_P
ST2NSX3MIN_THDV1N_P | REAL | IOD_ST2_TCP | 5309 | 45309 | NSX[3].MIN_THDV1N_P
ST2NSX3MIN_THDV23_P | REAL | IOD_ST2_TCP | 5311 | 45311 | NSX[3].MIN_THDV23_P
ST2NSX3MIN_THDV2N_P | REAL | IOD_ST2_TCP | 5313 | 45313 | NSX[3].MIN_THDV2N_P
ST2NSX3MIN_THDV31_P | REAL | IOD_ST2_TCP | 5315 | 45315 | NSX[3].MIN_THDV31_P
ST2NSX3MIN_THDV3N_P | REAL | IOD_ST2_TCP | 5317 | 45317 | NSX[3].MIN_THDV3N_P
ST2NSX3MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5319 | 45319 | NSX[3].MIN_VoltageAvgPhToN_V
ST2NSX3MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5321 | 45321 | NSX[3].MIN_VoltageAvgPhToPh_V
ST2NSX3MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5323 | 45323 | NSX[3].MIN_VoltageUnbV12_P
ST2NSX3MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5325 | 45325 | NSX[3].MIN_VoltageUnbV1N_P
ST2NSX3MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5327 | 45327 | NSX[3].MIN_VoltageUnbV23_P
ST2NSX3MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5329 | 45329 | NSX[3].MIN_VoltageUnbV2N_P
ST2NSX3MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5331 | 45331 | NSX[3].MIN_VoltageUnbV31_P
ST2NSX3MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5333 | 45333 | NSX[3].MIN_VoltageUnbV3N_P
ST2NSX3MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 5335 | 45335 | NSX[3].MIN_VoltageV12_V
ST2NSX3MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 5337 | 45337 | NSX[3].MIN_VoltageV1N_V
ST2NSX3MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 5339 | 45339 | NSX[3].MIN_VoltageV23_V
ST2NSX3MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 5341 | 45341 | NSX[3].MIN_VoltageV2N_V
ST2NSX3MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 5343 | 45343 | NSX[3].MIN_VoltageV31_V
ST2NSX3MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 5345 | 45345 | NSX[3].MIN_VoltageV3N_V
ST2NSX3PowerFactorL1 | REAL | IOD_ST2_TCP | 5347 | 45347 | NSX[3].PowerFactorL1
ST2NSX3PowerFactorL2 | REAL | IOD_ST2_TCP | 5349 | 45349 | NSX[3].PowerFactorL2
ST2NSX3PowerFactorL3 | REAL | IOD_ST2_TCP | 5351 | 45351 | NSX[3].PowerFactorL3
ST2NSX3PowerFactorTotal | REAL | IOD_ST2_TCP | 5353 | 45353 | NSX[3].PowerFactorTotal
ST2NSX3RazEner_D | REAL | IOD_ST2_TCP | 5355 | 45355 | NSX[3].RazEner_D
ST2NSX3RazEner_D_SCADA | REAL | IOD_ST2_TCP | 5357 | 45357 | NSX[3].RazEner_D_SCADA
ST2NSX3RazEner_D_TEMP | REAL | IOD_ST2_TCP | 5359 | 45359 | NSX[3].RazEner_D_TEMP
ST2NSX3RazEner_M | REAL | IOD_ST2_TCP | 5361 | 45361 | NSX[3].RazEner_M
ST2NSX3RazEner_M_SCADA | REAL | IOD_ST2_TCP | 5363 | 45363 | NSX[3].RazEner_M_SCADA
ST2NSX3RazEner_M_TEMP | REAL | IOD_ST2_TCP | 5365 | 45365 | NSX[3].RazEner_M_TEMP
ST2NSX3RazEner_T | REAL | IOD_ST2_TCP | 5367 | 45367 | NSX[3].RazEner_T
ST2NSX3RazEner_T_SCADA | REAL | IOD_ST2_TCP | 5369 | 45369 | NSX[3].RazEner_T_SCADA
ST2NSX3RazEner_T_TEMP | REAL | IOD_ST2_TCP | 5371 | 45371 | NSX[3].RazEner_T_TEMP
ST2NSX3ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 5373 | 45373 | NSX[3].ReactiveEnergy_kVArh
ST2NSX3ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 5375 | 45375 | NSX[3].ReactiveNegativeEnergy_kVArh
ST2NSX3ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 5377 | 45377 | NSX[3].ReactivePositiveEnergy_kVArh
ST2NSX3ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 5379 | 45379 | NSX[3].ReactivePowerDemand_kVAr
ST2NSX3ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5381 | 45381 | NSX[3].ReactivePowerL1_kVAr
ST2NSX3ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5383 | 45383 | NSX[3].ReactivePowerL2_kVAr
ST2NSX3ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5385 | 45385 | NSX[3].ReactivePowerL3_kVAr
ST2NSX3ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 5387 | 45387 | NSX[3].ReactivePowerMaxDemand_kVAr
ST2NSX3ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5389 | 45389 | NSX[3].ReactivePowerTotal_kVAr
ST2NSX3THDI1_P | REAL | IOD_ST2_TCP | 5391 | 45391 | NSX[3].THDI1_P
ST2NSX3THDI2_P | REAL | IOD_ST2_TCP | 5393 | 45393 | NSX[3].THDI2_P
ST2NSX3THDI3_P | REAL | IOD_ST2_TCP | 5395 | 45395 | NSX[3].THDI3_P
ST2NSX3THDV12_P | REAL | IOD_ST2_TCP | 5397 | 45397 | NSX[3].THDV12_P
ST2NSX3THDV1N_P | REAL | IOD_ST2_TCP | 5399 | 45399 | NSX[3].THDV1N_P
ST2NSX3THDV23_P | REAL | IOD_ST2_TCP | 5401 | 45401 | NSX[3].THDV23_P
ST2NSX3THDV2N_P | REAL | IOD_ST2_TCP | 5403 | 45403 | NSX[3].THDV2N_P
ST2NSX3THDV31_P | REAL | IOD_ST2_TCP | 5405 | 45405 | NSX[3].THDV31_P
ST2NSX3THDV3N_P | REAL | IOD_ST2_TCP | 5407 | 45407 | NSX[3].THDV3N_P
ST2NSX3VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5409 | 45409 | NSX[3].VoltageAvgPhToN_V
ST2NSX3VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5411 | 45411 | NSX[3].VoltageAvgPhToPh_V
ST2NSX3VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5413 | 45413 | NSX[3].VoltageUnbV12_P
ST2NSX3VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5415 | 45415 | NSX[3].VoltageUnbV1N_P
ST2NSX3VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5417 | 45417 | NSX[3].VoltageUnbV23_P
ST2NSX3VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5419 | 45419 | NSX[3].VoltageUnbV2N_P
ST2NSX3VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5421 | 45421 | NSX[3].VoltageUnbV31_P
ST2NSX3VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5423 | 45423 | NSX[3].VoltageUnbV3N_P
ST2NSX3VoltageV12_V | REAL | IOD_ST2_TCP | 5425 | 45425 | NSX[3].VoltageV12_V
ST2NSX3VoltageV1N_V | REAL | IOD_ST2_TCP | 5427 | 45427 | NSX[3].VoltageV1N_V
ST2NSX3VoltageV23_V | REAL | IOD_ST2_TCP | 5429 | 45429 | NSX[3].VoltageV23_V
ST2NSX3VoltageV2N_V | REAL | IOD_ST2_TCP | 5431 | 45431 | NSX[3].VoltageV2N_V
ST2NSX3VoltageV31_V | REAL | IOD_ST2_TCP | 5433 | 45433 | NSX[3].VoltageV31_V
ST2NSX3VoltageV3N_V | REAL | IOD_ST2_TCP | 5435 | 45435 | NSX[3].VoltageV3N_V
ST2NSX4ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5437 | 45437 | NSX[4].ActiveEnergy_kWh
ST2NSX4ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 5439 | 45439 | NSX[4].ActiveNegativeEnergy_kWh
ST2NSX4ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 5441 | 45441 | NSX[4].ActivePositiveEnergy_kWh
ST2NSX4ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 5443 | 45443 | NSX[4].ActivePowerDemand_kW
ST2NSX4ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5445 | 45445 | NSX[4].ActivePowerL1_kW
ST2NSX4ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5447 | 45447 | NSX[4].ActivePowerL2_kW
ST2NSX4ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5449 | 45449 | NSX[4].ActivePowerL3_kW
ST2NSX4ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 5451 | 45451 | NSX[4].ActivePowerMaxDemand_kW
ST2NSX4ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5453 | 45453 | NSX[4].ActivePowerTotal_kW
ST2NSX4ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 5455 | 45455 | NSX[4].ApparentEnergy_kVAh
ST2NSX4ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 5457 | 45457 | NSX[4].ApparentPowerDemand_kVA
ST2NSX4ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 5459 | 45459 | NSX[4].ApparentPowerMaxDemand_kVA
ST2NSX4ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5461 | 45461 | NSX[4].ApparetnPowerL1_kVA
ST2NSX4ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5463 | 45463 | NSX[4].ApparetnPowerL2_kVA
ST2NSX4ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5465 | 45465 | NSX[4].ApparetnPowerL3_kVA
ST2NSX4ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5467 | 45467 | NSX[4].ApparetnPowerTotal_kVA
ST2NSX4CosFL1 | REAL | IOD_ST2_TCP | 5469 | 45469 | NSX[4].CosFL1
ST2NSX4CosFL2 | REAL | IOD_ST2_TCP | 5471 | 45471 | NSX[4].CosFL2
ST2NSX4CosFL3 | REAL | IOD_ST2_TCP | 5473 | 45473 | NSX[4].CosFL3
ST2NSX4CosFTotal | REAL | IOD_ST2_TCP | 5475 | 45475 | NSX[4].CosFTotal
ST2NSX4CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5477 | 45477 | NSX[4].CumulNegativeActiveEnergy_kWh
ST2NSX4CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5479 | 45479 | NSX[4].CumulPositiveActiveEnergy_kWh
ST2NSX4CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5481 | 45481 | NSX[4].CurrentAvgI1I2I3_A
ST2NSX4CurrentDemandL1_A | REAL | IOD_ST2_TCP | 5483 | 45483 | NSX[4].CurrentDemandL1_A
ST2NSX4CurrentDemandL2_A | REAL | IOD_ST2_TCP | 5485 | 45485 | NSX[4].CurrentDemandL2_A
ST2NSX4CurrentDemandL3_A | REAL | IOD_ST2_TCP | 5487 | 45487 | NSX[4].CurrentDemandL3_A
ST2NSX4CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 5489 | 45489 | NSX[4].CurrentDemandMaxL1_A
ST2NSX4CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 5491 | 45491 | NSX[4].CurrentDemandMaxL2_A
ST2NSX4CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 5493 | 45493 | NSX[4].CurrentDemandMaxL3_A
ST2NSX4CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 5495 | 45495 | NSX[4].CurrentDemandMaxN_A
ST2NSX4CurrentDemandN_A | REAL | IOD_ST2_TCP | 5497 | 45497 | NSX[4].CurrentDemandN_A
ST2NSX4CurrentL1_A | REAL | IOD_ST2_TCP | 5499 | 45499 | NSX[4].CurrentL1_A
ST2NSX4CurrentL2_A | REAL | IOD_ST2_TCP | 5501 | 45501 | NSX[4].CurrentL2_A
ST2NSX4CurrentL3_A | REAL | IOD_ST2_TCP | 5503 | 45503 | NSX[4].CurrentL3_A
ST2NSX4CurrentN_A | REAL | IOD_ST2_TCP | 5505 | 45505 | NSX[4].CurrentN_A
ST2NSX4CurrentUnbI1_P | REAL | IOD_ST2_TCP | 5507 | 45507 | NSX[4].CurrentUnbI1_P
ST2NSX4CurrentUnbI2_P | REAL | IOD_ST2_TCP | 5509 | 45509 | NSX[4].CurrentUnbI2_P
ST2NSX4CurrentUnbI3_P | REAL | IOD_ST2_TCP | 5511 | 45511 | NSX[4].CurrentUnbI3_P
ST2NSX4CurrentUnbN_P | REAL | IOD_ST2_TCP | 5513 | 45513 | NSX[4].CurrentUnbN_P
ST2NSX4DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 5515 | 45515 | NSX[4].DelovnaEnergija_TEMP
ST2NSX4DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5517 | 45517 | NSX[4].DistortionPowerL1_kVAr
ST2NSX4DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5519 | 45519 | NSX[4].DistortionPowerL2_kVAr
ST2NSX4DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5521 | 45521 | NSX[4].DistortionPowerL3_kVAr
ST2NSX4DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5523 | 45523 | NSX[4].DistortionPowerTotal_kVAr
ST2NSX4Frequency_Hz | REAL | IOD_ST2_TCP | 5525 | 45525 | NSX[4].Frequency_Hz
ST2NSX4FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5527 | 45527 | NSX[4].FunReactivePowerL1_kVAr
ST2NSX4FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5529 | 45529 | NSX[4].FunReactivePowerL2_kVAr
ST2NSX4FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5531 | 45531 | NSX[4].FunReactivePowerL3_kVAr
ST2NSX4FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5533 | 45533 | NSX[4].FunReactivePowerTotal_kVAr
ST2NSX4MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5535 | 45535 | NSX[4].MAX_ActivePowerL1_kW
ST2NSX4MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5537 | 45537 | NSX[4].MAX_ActivePowerL2_kW
ST2NSX4MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5539 | 45539 | NSX[4].MAX_ActivePowerL3_kW
ST2NSX4MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5541 | 45541 | NSX[4].MAX_ActivePowerTotal_kW
ST2NSX4MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5543 | 45543 | NSX[4].MAX_ApparetnPowerL1_kVA
ST2NSX4MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5545 | 45545 | NSX[4].MAX_ApparetnPowerL2_kVA
ST2NSX4MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5547 | 45547 | NSX[4].MAX_ApparetnPowerL3_kVA
ST2NSX4MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5549 | 45549 | NSX[4].MAX_ApparetnPowerTotal_kVA
ST2NSX4MAX_CosFL1 | REAL | IOD_ST2_TCP | 5551 | 45551 | NSX[4].MAX_CosFL1
ST2NSX4MAX_CosFL2 | REAL | IOD_ST2_TCP | 5553 | 45553 | NSX[4].MAX_CosFL2
ST2NSX4MAX_CosFL3 | REAL | IOD_ST2_TCP | 5555 | 45555 | NSX[4].MAX_CosFL3
ST2NSX4MAX_CosFTotal | REAL | IOD_ST2_TCP | 5557 | 45557 | NSX[4].MAX_CosFTotal
ST2NSX4MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5559 | 45559 | NSX[4].MAX_CurrentAvgI1I2I3_A
ST2NSX4MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 5561 | 45561 | NSX[4].MAX_CurrentL1_A
ST2NSX4MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 5563 | 45563 | NSX[4].MAX_CurrentL2_A
ST2NSX4MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 5565 | 45565 | NSX[4].MAX_CurrentL3_A
ST2NSX4MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 5567 | 45567 | NSX[4].MAX_CurrentMaxL1L2L3N_A
ST2NSX4MAX_CurrentN_A | REAL | IOD_ST2_TCP | 5569 | 45569 | NSX[4].MAX_CurrentN_A
ST2NSX4MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5571 | 45571 | NSX[4].MAX_DistortionPowerL1_kVAr
ST2NSX4MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5573 | 45573 | NSX[4].MAX_DistortionPowerL2_kVAr
ST2NSX4MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5575 | 45575 | NSX[4].MAX_DistortionPowerL3_kVAr
ST2NSX4MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5577 | 45577 | NSX[4].MAX_DistortionPowerTotal_kVAr
ST2NSX4MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 5579 | 45579 | NSX[4].MAX_Frequency_Hz
ST2NSX4MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5581 | 45581 | NSX[4].MAX_FunReactivePowerL1_kVAr
ST2NSX4MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5583 | 45583 | NSX[4].MAX_FunReactivePowerL2_kVAr
ST2NSX4MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5585 | 45585 | NSX[4].MAX_FunReactivePowerL3_kVAr
ST2NSX4MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5587 | 45587 | NSX[4].MAX_FunReactivePowerTotal_kVAr
ST2NSX4MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 5589 | 45589 | NSX[4].MAX_PowerFactorL1
ST2NSX4MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 5591 | 45591 | NSX[4].MAX_PowerFactorL2
ST2NSX4MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 5593 | 45593 | NSX[4].MAX_PowerFactorL3
ST2NSX4MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 5595 | 45595 | NSX[4].MAX_PowerFactorTotal
ST2NSX4MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5597 | 45597 | NSX[4].MAX_ReactivePowerL1_kVAr
ST2NSX4MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5599 | 45599 | NSX[4].MAX_ReactivePowerL2_kVAr
ST2NSX4MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5601 | 45601 | NSX[4].MAX_ReactivePowerL3_kVAr
ST2NSX4MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5603 | 45603 | NSX[4].MAX_ReactivePowerTotal_kVAr
ST2NSX4MAX_THDI1_P | REAL | IOD_ST2_TCP | 5605 | 45605 | NSX[4].MAX_THDI1_P
ST2NSX4MAX_THDI2_P | REAL | IOD_ST2_TCP | 5607 | 45607 | NSX[4].MAX_THDI2_P
ST2NSX4MAX_THDI3_P | REAL | IOD_ST2_TCP | 5609 | 45609 | NSX[4].MAX_THDI3_P
ST2NSX4MAX_THDV12_P | REAL | IOD_ST2_TCP | 5611 | 45611 | NSX[4].MAX_THDV12_P
ST2NSX4MAX_THDV1N_P | REAL | IOD_ST2_TCP | 5613 | 45613 | NSX[4].MAX_THDV1N_P
ST2NSX4MAX_THDV23_P | REAL | IOD_ST2_TCP | 5615 | 45615 | NSX[4].MAX_THDV23_P
ST2NSX4MAX_THDV2N_P | REAL | IOD_ST2_TCP | 5617 | 45617 | NSX[4].MAX_THDV2N_P
ST2NSX4MAX_THDV31_P | REAL | IOD_ST2_TCP | 5619 | 45619 | NSX[4].MAX_THDV31_P
ST2NSX4MAX_THDV3N_P | REAL | IOD_ST2_TCP | 5621 | 45621 | NSX[4].MAX_THDV3N_P
ST2NSX4MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5623 | 45623 | NSX[4].MAX_VoltageAvgPhToN_V
ST2NSX4MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5625 | 45625 | NSX[4].MAX_VoltageAvgPhToPh_V
ST2NSX4MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5627 | 45627 | NSX[4].MAX_VoltageUnbV12_P
ST2NSX4MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5629 | 45629 | NSX[4].MAX_VoltageUnbV1N_P
ST2NSX4MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5631 | 45631 | NSX[4].MAX_VoltageUnbV23_P
ST2NSX4MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5633 | 45633 | NSX[4].MAX_VoltageUnbV2N_P
ST2NSX4MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5635 | 45635 | NSX[4].MAX_VoltageUnbV31_P
ST2NSX4MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5637 | 45637 | NSX[4].MAX_VoltageUnbV3N_P
ST2NSX4MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 5639 | 45639 | NSX[4].MAX_VoltageV12_V
ST2NSX4MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 5641 | 45641 | NSX[4].MAX_VoltageV1N_V
ST2NSX4MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 5643 | 45643 | NSX[4].MAX_VoltageV23_V
ST2NSX4MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 5645 | 45645 | NSX[4].MAX_VoltageV2N_V
ST2NSX4MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 5647 | 45647 | NSX[4].MAX_VoltageV31_V
ST2NSX4MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 5649 | 45649 | NSX[4].MAX_VoltageV3N_V
ST2NSX4MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5651 | 45651 | NSX[4].MIN_ActivePowerL1_kW
ST2NSX4MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5653 | 45653 | NSX[4].MIN_ActivePowerL2_kW
ST2NSX4MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5655 | 45655 | NSX[4].MIN_ActivePowerL3_kW
ST2NSX4MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5657 | 45657 | NSX[4].MIN_ActivePowerTotal_kW
ST2NSX4MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5659 | 45659 | NSX[4].MIN_ApparetnPowerL1_kVA
ST2NSX4MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5661 | 45661 | NSX[4].MIN_ApparetnPowerL2_kVA
ST2NSX4MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5663 | 45663 | NSX[4].MIN_ApparetnPowerL3_kVA
ST2NSX4MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5665 | 45665 | NSX[4].MIN_ApparetnPowerTotal_kVA
ST2NSX4MIN_CosFL1 | REAL | IOD_ST2_TCP | 5667 | 45667 | NSX[4].MIN_CosFL1
ST2NSX4MIN_CosFL2 | REAL | IOD_ST2_TCP | 5669 | 45669 | NSX[4].MIN_CosFL2
ST2NSX4MIN_CosFL3 | REAL | IOD_ST2_TCP | 5671 | 45671 | NSX[4].MIN_CosFL3
ST2NSX4MIN_CosFTotal | REAL | IOD_ST2_TCP | 5673 | 45673 | NSX[4].MIN_CosFTotal
ST2NSX4MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5675 | 45675 | NSX[4].MIN_CurrentAvgI1I2I3_A
ST2NSX4MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 5677 | 45677 | NSX[4].MIN_CurrentL1_A
ST2NSX4MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 5679 | 45679 | NSX[4].MIN_CurrentL2_A
ST2NSX4MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 5681 | 45681 | NSX[4].MIN_CurrentL3_A
ST2NSX4MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 5683 | 45683 | NSX[4].MIN_CurrentMaxL1L2L3N_A
ST2NSX4MIN_CurrentN_A | REAL | IOD_ST2_TCP | 5685 | 45685 | NSX[4].MIN_CurrentN_A
ST2NSX4MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5687 | 45687 | NSX[4].MIN_DistortionPowerL1_kVAr
ST2NSX4MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5689 | 45689 | NSX[4].MIN_DistortionPowerL2_kVAr
ST2NSX4MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5691 | 45691 | NSX[4].MIN_DistortionPowerL3_kVAr
ST2NSX4MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5693 | 45693 | NSX[4].MIN_DistortionPowerTotal_kVAr
ST2NSX4MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 5695 | 45695 | NSX[4].MIN_Frequency_Hz
ST2NSX4MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5697 | 45697 | NSX[4].MIN_FunReactivePowerL1_kVAr
ST2NSX4MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5699 | 45699 | NSX[4].MIN_FunReactivePowerL2_kVAr
ST2NSX4MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5701 | 45701 | NSX[4].MIN_FunReactivePowerL3_kVAr
ST2NSX4MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5703 | 45703 | NSX[4].MIN_FunReactivePowerTotal_kVAr
ST2NSX4MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 5705 | 45705 | NSX[4].MIN_PowerFactorL1
ST2NSX4MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 5707 | 45707 | NSX[4].MIN_PowerFactorL2
ST2NSX4MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 5709 | 45709 | NSX[4].MIN_PowerFactorL3
ST2NSX4MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 5711 | 45711 | NSX[4].MIN_PowerFactorTotal
ST2NSX4MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5713 | 45713 | NSX[4].MIN_ReactivePowerL1_kVAr
ST2NSX4MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5715 | 45715 | NSX[4].MIN_ReactivePowerL2_kVAr
ST2NSX4MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5717 | 45717 | NSX[4].MIN_ReactivePowerL3_kVAr
ST2NSX4MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5719 | 45719 | NSX[4].MIN_ReactivePowerTotal_kVAr
ST2NSX4MIN_THDI1_P | REAL | IOD_ST2_TCP | 5721 | 45721 | NSX[4].MIN_THDI1_P
ST2NSX4MIN_THDI2_P | REAL | IOD_ST2_TCP | 5723 | 45723 | NSX[4].MIN_THDI2_P
ST2NSX4MIN_THDI3_P | REAL | IOD_ST2_TCP | 5725 | 45725 | NSX[4].MIN_THDI3_P
ST2NSX4MIN_THDV12_P | REAL | IOD_ST2_TCP | 5727 | 45727 | NSX[4].MIN_THDV12_P
ST2NSX4MIN_THDV1N_P | REAL | IOD_ST2_TCP | 5729 | 45729 | NSX[4].MIN_THDV1N_P
ST2NSX4MIN_THDV23_P | REAL | IOD_ST2_TCP | 5731 | 45731 | NSX[4].MIN_THDV23_P
ST2NSX4MIN_THDV2N_P | REAL | IOD_ST2_TCP | 5733 | 45733 | NSX[4].MIN_THDV2N_P
ST2NSX4MIN_THDV31_P | REAL | IOD_ST2_TCP | 5735 | 45735 | NSX[4].MIN_THDV31_P
ST2NSX4MIN_THDV3N_P | REAL | IOD_ST2_TCP | 5737 | 45737 | NSX[4].MIN_THDV3N_P
ST2NSX4MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5739 | 45739 | NSX[4].MIN_VoltageAvgPhToN_V
ST2NSX4MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5741 | 45741 | NSX[4].MIN_VoltageAvgPhToPh_V
ST2NSX4MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5743 | 45743 | NSX[4].MIN_VoltageUnbV12_P
ST2NSX4MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5745 | 45745 | NSX[4].MIN_VoltageUnbV1N_P
ST2NSX4MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5747 | 45747 | NSX[4].MIN_VoltageUnbV23_P
ST2NSX4MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5749 | 45749 | NSX[4].MIN_VoltageUnbV2N_P
ST2NSX4MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5751 | 45751 | NSX[4].MIN_VoltageUnbV31_P
ST2NSX4MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5753 | 45753 | NSX[4].MIN_VoltageUnbV3N_P
ST2NSX4MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 5755 | 45755 | NSX[4].MIN_VoltageV12_V
ST2NSX4MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 5757 | 45757 | NSX[4].MIN_VoltageV1N_V
ST2NSX4MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 5759 | 45759 | NSX[4].MIN_VoltageV23_V
ST2NSX4MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 5761 | 45761 | NSX[4].MIN_VoltageV2N_V
ST2NSX4MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 5763 | 45763 | NSX[4].MIN_VoltageV31_V
ST2NSX4MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 5765 | 45765 | NSX[4].MIN_VoltageV3N_V
ST2NSX4PowerFactorL1 | REAL | IOD_ST2_TCP | 5767 | 45767 | NSX[4].PowerFactorL1
ST2NSX4PowerFactorL2 | REAL | IOD_ST2_TCP | 5769 | 45769 | NSX[4].PowerFactorL2
ST2NSX4PowerFactorL3 | REAL | IOD_ST2_TCP | 5771 | 45771 | NSX[4].PowerFactorL3
ST2NSX4PowerFactorTotal | REAL | IOD_ST2_TCP | 5773 | 45773 | NSX[4].PowerFactorTotal
ST2NSX4RazEner_D | REAL | IOD_ST2_TCP | 5775 | 45775 | NSX[4].RazEner_D
ST2NSX4RazEner_D_SCADA | REAL | IOD_ST2_TCP | 5777 | 45777 | NSX[4].RazEner_D_SCADA
ST2NSX4RazEner_D_TEMP | REAL | IOD_ST2_TCP | 5779 | 45779 | NSX[4].RazEner_D_TEMP
ST2NSX4RazEner_M | REAL | IOD_ST2_TCP | 5781 | 45781 | NSX[4].RazEner_M
ST2NSX4RazEner_M_SCADA | REAL | IOD_ST2_TCP | 5783 | 45783 | NSX[4].RazEner_M_SCADA
ST2NSX4RazEner_M_TEMP | REAL | IOD_ST2_TCP | 5785 | 45785 | NSX[4].RazEner_M_TEMP
ST2NSX4RazEner_T | REAL | IOD_ST2_TCP | 5787 | 45787 | NSX[4].RazEner_T
ST2NSX4RazEner_T_SCADA | REAL | IOD_ST2_TCP | 5789 | 45789 | NSX[4].RazEner_T_SCADA
ST2NSX4RazEner_T_TEMP | REAL | IOD_ST2_TCP | 5791 | 45791 | NSX[4].RazEner_T_TEMP
ST2NSX4ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 5793 | 45793 | NSX[4].ReactiveEnergy_kVArh
ST2NSX4ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 5795 | 45795 | NSX[4].ReactiveNegativeEnergy_kVArh
ST2NSX4ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 5797 | 45797 | NSX[4].ReactivePositiveEnergy_kVArh
ST2NSX4ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 5799 | 45799 | NSX[4].ReactivePowerDemand_kVAr
ST2NSX4ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5801 | 45801 | NSX[4].ReactivePowerL1_kVAr
ST2NSX4ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5803 | 45803 | NSX[4].ReactivePowerL2_kVAr
ST2NSX4ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5805 | 45805 | NSX[4].ReactivePowerL3_kVAr
ST2NSX4ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 5807 | 45807 | NSX[4].ReactivePowerMaxDemand_kVAr
ST2NSX4ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5809 | 45809 | NSX[4].ReactivePowerTotal_kVAr
ST2NSX4THDI1_P | REAL | IOD_ST2_TCP | 5811 | 45811 | NSX[4].THDI1_P
ST2NSX4THDI2_P | REAL | IOD_ST2_TCP | 5813 | 45813 | NSX[4].THDI2_P
ST2NSX4THDI3_P | REAL | IOD_ST2_TCP | 5815 | 45815 | NSX[4].THDI3_P
ST2NSX4THDV12_P | REAL | IOD_ST2_TCP | 5817 | 45817 | NSX[4].THDV12_P
ST2NSX4THDV1N_P | REAL | IOD_ST2_TCP | 5819 | 45819 | NSX[4].THDV1N_P
ST2NSX4THDV23_P | REAL | IOD_ST2_TCP | 5821 | 45821 | NSX[4].THDV23_P
ST2NSX4THDV2N_P | REAL | IOD_ST2_TCP | 5823 | 45823 | NSX[4].THDV2N_P
ST2NSX4THDV31_P | REAL | IOD_ST2_TCP | 5825 | 45825 | NSX[4].THDV31_P
ST2NSX4THDV3N_P | REAL | IOD_ST2_TCP | 5827 | 45827 | NSX[4].THDV3N_P
ST2NSX4VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 5829 | 45829 | NSX[4].VoltageAvgPhToN_V
ST2NSX4VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 5831 | 45831 | NSX[4].VoltageAvgPhToPh_V
ST2NSX4VoltageUnbV12_P | REAL | IOD_ST2_TCP | 5833 | 45833 | NSX[4].VoltageUnbV12_P
ST2NSX4VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 5835 | 45835 | NSX[4].VoltageUnbV1N_P
ST2NSX4VoltageUnbV23_P | REAL | IOD_ST2_TCP | 5837 | 45837 | NSX[4].VoltageUnbV23_P
ST2NSX4VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 5839 | 45839 | NSX[4].VoltageUnbV2N_P
ST2NSX4VoltageUnbV31_P | REAL | IOD_ST2_TCP | 5841 | 45841 | NSX[4].VoltageUnbV31_P
ST2NSX4VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 5843 | 45843 | NSX[4].VoltageUnbV3N_P
ST2NSX4VoltageV12_V | REAL | IOD_ST2_TCP | 5845 | 45845 | NSX[4].VoltageV12_V
ST2NSX4VoltageV1N_V | REAL | IOD_ST2_TCP | 5847 | 45847 | NSX[4].VoltageV1N_V
ST2NSX4VoltageV23_V | REAL | IOD_ST2_TCP | 5849 | 45849 | NSX[4].VoltageV23_V
ST2NSX4VoltageV2N_V | REAL | IOD_ST2_TCP | 5851 | 45851 | NSX[4].VoltageV2N_V
ST2NSX4VoltageV31_V | REAL | IOD_ST2_TCP | 5853 | 45853 | NSX[4].VoltageV31_V
ST2NSX4VoltageV3N_V | REAL | IOD_ST2_TCP | 5855 | 45855 | NSX[4].VoltageV3N_V
ST2NSX5ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5857 | 45857 | NSX[5].ActiveEnergy_kWh
ST2NSX5ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 5859 | 45859 | NSX[5].ActiveNegativeEnergy_kWh
ST2NSX5ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 5861 | 45861 | NSX[5].ActivePositiveEnergy_kWh
ST2NSX5ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 5863 | 45863 | NSX[5].ActivePowerDemand_kW
ST2NSX5ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5865 | 45865 | NSX[5].ActivePowerL1_kW
ST2NSX5ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5867 | 45867 | NSX[5].ActivePowerL2_kW
ST2NSX5ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5869 | 45869 | NSX[5].ActivePowerL3_kW
ST2NSX5ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 5871 | 45871 | NSX[5].ActivePowerMaxDemand_kW
ST2NSX5ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5873 | 45873 | NSX[5].ActivePowerTotal_kW
ST2NSX5ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 5875 | 45875 | NSX[5].ApparentEnergy_kVAh
ST2NSX5ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 5877 | 45877 | NSX[5].ApparentPowerDemand_kVA
ST2NSX5ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 5879 | 45879 | NSX[5].ApparentPowerMaxDemand_kVA
ST2NSX5ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5881 | 45881 | NSX[5].ApparetnPowerL1_kVA
ST2NSX5ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5883 | 45883 | NSX[5].ApparetnPowerL2_kVA
ST2NSX5ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5885 | 45885 | NSX[5].ApparetnPowerL3_kVA
ST2NSX5ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5887 | 45887 | NSX[5].ApparetnPowerTotal_kVA
ST2NSX5CosFL1 | REAL | IOD_ST2_TCP | 5889 | 45889 | NSX[5].CosFL1
ST2NSX5CosFL2 | REAL | IOD_ST2_TCP | 5891 | 45891 | NSX[5].CosFL2
ST2NSX5CosFL3 | REAL | IOD_ST2_TCP | 5893 | 45893 | NSX[5].CosFL3
ST2NSX5CosFTotal | REAL | IOD_ST2_TCP | 5895 | 45895 | NSX[5].CosFTotal
ST2NSX5CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5897 | 45897 | NSX[5].CumulNegativeActiveEnergy_kWh
ST2NSX5CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 5899 | 45899 | NSX[5].CumulPositiveActiveEnergy_kWh
ST2NSX5CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5901 | 45901 | NSX[5].CurrentAvgI1I2I3_A
ST2NSX5CurrentDemandL1_A | REAL | IOD_ST2_TCP | 5903 | 45903 | NSX[5].CurrentDemandL1_A
ST2NSX5CurrentDemandL2_A | REAL | IOD_ST2_TCP | 5905 | 45905 | NSX[5].CurrentDemandL2_A
ST2NSX5CurrentDemandL3_A | REAL | IOD_ST2_TCP | 5907 | 45907 | NSX[5].CurrentDemandL3_A
ST2NSX5CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 5909 | 45909 | NSX[5].CurrentDemandMaxL1_A
ST2NSX5CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 5911 | 45911 | NSX[5].CurrentDemandMaxL2_A
ST2NSX5CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 5913 | 45913 | NSX[5].CurrentDemandMaxL3_A
ST2NSX5CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 5915 | 45915 | NSX[5].CurrentDemandMaxN_A
ST2NSX5CurrentDemandN_A | REAL | IOD_ST2_TCP | 5917 | 45917 | NSX[5].CurrentDemandN_A
ST2NSX5CurrentL1_A | REAL | IOD_ST2_TCP | 5919 | 45919 | NSX[5].CurrentL1_A
ST2NSX5CurrentL2_A | REAL | IOD_ST2_TCP | 5921 | 45921 | NSX[5].CurrentL2_A
ST2NSX5CurrentL3_A | REAL | IOD_ST2_TCP | 5923 | 45923 | NSX[5].CurrentL3_A
ST2NSX5CurrentN_A | REAL | IOD_ST2_TCP | 5925 | 45925 | NSX[5].CurrentN_A
ST2NSX5CurrentUnbI1_P | REAL | IOD_ST2_TCP | 5927 | 45927 | NSX[5].CurrentUnbI1_P
ST2NSX5CurrentUnbI2_P | REAL | IOD_ST2_TCP | 5929 | 45929 | NSX[5].CurrentUnbI2_P
ST2NSX5CurrentUnbI3_P | REAL | IOD_ST2_TCP | 5931 | 45931 | NSX[5].CurrentUnbI3_P
ST2NSX5CurrentUnbN_P | REAL | IOD_ST2_TCP | 5933 | 45933 | NSX[5].CurrentUnbN_P
ST2NSX5DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 5935 | 45935 | NSX[5].DelovnaEnergija_TEMP
ST2NSX5DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5937 | 45937 | NSX[5].DistortionPowerL1_kVAr
ST2NSX5DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5939 | 45939 | NSX[5].DistortionPowerL2_kVAr
ST2NSX5DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5941 | 45941 | NSX[5].DistortionPowerL3_kVAr
ST2NSX5DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5943 | 45943 | NSX[5].DistortionPowerTotal_kVAr
ST2NSX5Frequency_Hz | REAL | IOD_ST2_TCP | 5945 | 45945 | NSX[5].Frequency_Hz
ST2NSX5FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 5947 | 45947 | NSX[5].FunReactivePowerL1_kVAr
ST2NSX5FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 5949 | 45949 | NSX[5].FunReactivePowerL2_kVAr
ST2NSX5FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 5951 | 45951 | NSX[5].FunReactivePowerL3_kVAr
ST2NSX5FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 5953 | 45953 | NSX[5].FunReactivePowerTotal_kVAr
ST2NSX5MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 5955 | 45955 | NSX[5].MAX_ActivePowerL1_kW
ST2NSX5MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 5957 | 45957 | NSX[5].MAX_ActivePowerL2_kW
ST2NSX5MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 5959 | 45959 | NSX[5].MAX_ActivePowerL3_kW
ST2NSX5MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 5961 | 45961 | NSX[5].MAX_ActivePowerTotal_kW
ST2NSX5MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 5963 | 45963 | NSX[5].MAX_ApparetnPowerL1_kVA
ST2NSX5MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 5965 | 45965 | NSX[5].MAX_ApparetnPowerL2_kVA
ST2NSX5MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 5967 | 45967 | NSX[5].MAX_ApparetnPowerL3_kVA
ST2NSX5MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 5969 | 45969 | NSX[5].MAX_ApparetnPowerTotal_kVA
ST2NSX5MAX_CosFL1 | REAL | IOD_ST2_TCP | 5971 | 45971 | NSX[5].MAX_CosFL1
ST2NSX5MAX_CosFL2 | REAL | IOD_ST2_TCP | 5973 | 45973 | NSX[5].MAX_CosFL2
ST2NSX5MAX_CosFL3 | REAL | IOD_ST2_TCP | 5975 | 45975 | NSX[5].MAX_CosFL3
ST2NSX5MAX_CosFTotal | REAL | IOD_ST2_TCP | 5977 | 45977 | NSX[5].MAX_CosFTotal
ST2NSX5MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 5979 | 45979 | NSX[5].MAX_CurrentAvgI1I2I3_A
ST2NSX5MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 5981 | 45981 | NSX[5].MAX_CurrentL1_A
ST2NSX5MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 5983 | 45983 | NSX[5].MAX_CurrentL2_A
ST2NSX5MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 5985 | 45985 | NSX[5].MAX_CurrentL3_A
ST2NSX5MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 5987 | 45987 | NSX[5].MAX_CurrentMaxL1L2L3N_A
ST2NSX5MAX_CurrentN_A | REAL | IOD_ST2_TCP | 5989 | 45989 | NSX[5].MAX_CurrentN_A
ST2NSX5MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 5991 | 45991 | NSX[5].MAX_DistortionPowerL1_kVAr
ST2NSX5MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 5993 | 45993 | NSX[5].MAX_DistortionPowerL2_kVAr
ST2NSX5MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 5995 | 45995 | NSX[5].MAX_DistortionPowerL3_kVAr
ST2NSX5MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 5997 | 45997 | NSX[5].MAX_DistortionPowerTotal_kVAr
ST2NSX5MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 5999 | 45999 | NSX[5].MAX_Frequency_Hz
ST2NSX5MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6001 | 46001 | NSX[5].MAX_FunReactivePowerL1_kVAr
ST2NSX5MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6003 | 46003 | NSX[5].MAX_FunReactivePowerL2_kVAr
ST2NSX5MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6005 | 46005 | NSX[5].MAX_FunReactivePowerL3_kVAr
ST2NSX5MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6007 | 46007 | NSX[5].MAX_FunReactivePowerTotal_kVAr
ST2NSX5MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 6009 | 46009 | NSX[5].MAX_PowerFactorL1
ST2NSX5MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 6011 | 46011 | NSX[5].MAX_PowerFactorL2
ST2NSX5MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 6013 | 46013 | NSX[5].MAX_PowerFactorL3
ST2NSX5MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 6015 | 46015 | NSX[5].MAX_PowerFactorTotal
ST2NSX5MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6017 | 46017 | NSX[5].MAX_ReactivePowerL1_kVAr
ST2NSX5MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6019 | 46019 | NSX[5].MAX_ReactivePowerL2_kVAr
ST2NSX5MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6021 | 46021 | NSX[5].MAX_ReactivePowerL3_kVAr
ST2NSX5MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6023 | 46023 | NSX[5].MAX_ReactivePowerTotal_kVAr
ST2NSX5MAX_THDI1_P | REAL | IOD_ST2_TCP | 6025 | 46025 | NSX[5].MAX_THDI1_P
ST2NSX5MAX_THDI2_P | REAL | IOD_ST2_TCP | 6027 | 46027 | NSX[5].MAX_THDI2_P
ST2NSX5MAX_THDI3_P | REAL | IOD_ST2_TCP | 6029 | 46029 | NSX[5].MAX_THDI3_P
ST2NSX5MAX_THDV12_P | REAL | IOD_ST2_TCP | 6031 | 46031 | NSX[5].MAX_THDV12_P
ST2NSX5MAX_THDV1N_P | REAL | IOD_ST2_TCP | 6033 | 46033 | NSX[5].MAX_THDV1N_P
ST2NSX5MAX_THDV23_P | REAL | IOD_ST2_TCP | 6035 | 46035 | NSX[5].MAX_THDV23_P
ST2NSX5MAX_THDV2N_P | REAL | IOD_ST2_TCP | 6037 | 46037 | NSX[5].MAX_THDV2N_P
ST2NSX5MAX_THDV31_P | REAL | IOD_ST2_TCP | 6039 | 46039 | NSX[5].MAX_THDV31_P
ST2NSX5MAX_THDV3N_P | REAL | IOD_ST2_TCP | 6041 | 46041 | NSX[5].MAX_THDV3N_P
ST2NSX5MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6043 | 46043 | NSX[5].MAX_VoltageAvgPhToN_V
ST2NSX5MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6045 | 46045 | NSX[5].MAX_VoltageAvgPhToPh_V
ST2NSX5MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6047 | 46047 | NSX[5].MAX_VoltageUnbV12_P
ST2NSX5MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6049 | 46049 | NSX[5].MAX_VoltageUnbV1N_P
ST2NSX5MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6051 | 46051 | NSX[5].MAX_VoltageUnbV23_P
ST2NSX5MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6053 | 46053 | NSX[5].MAX_VoltageUnbV2N_P
ST2NSX5MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6055 | 46055 | NSX[5].MAX_VoltageUnbV31_P
ST2NSX5MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6057 | 46057 | NSX[5].MAX_VoltageUnbV3N_P
ST2NSX5MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 6059 | 46059 | NSX[5].MAX_VoltageV12_V
ST2NSX5MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 6061 | 46061 | NSX[5].MAX_VoltageV1N_V
ST2NSX5MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 6063 | 46063 | NSX[5].MAX_VoltageV23_V
ST2NSX5MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 6065 | 46065 | NSX[5].MAX_VoltageV2N_V
ST2NSX5MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 6067 | 46067 | NSX[5].MAX_VoltageV31_V
ST2NSX5MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 6069 | 46069 | NSX[5].MAX_VoltageV3N_V
ST2NSX5MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 6071 | 46071 | NSX[5].MIN_ActivePowerL1_kW
ST2NSX5MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 6073 | 46073 | NSX[5].MIN_ActivePowerL2_kW
ST2NSX5MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 6075 | 46075 | NSX[5].MIN_ActivePowerL3_kW
ST2NSX5MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 6077 | 46077 | NSX[5].MIN_ActivePowerTotal_kW
ST2NSX5MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 6079 | 46079 | NSX[5].MIN_ApparetnPowerL1_kVA
ST2NSX5MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 6081 | 46081 | NSX[5].MIN_ApparetnPowerL2_kVA
ST2NSX5MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 6083 | 46083 | NSX[5].MIN_ApparetnPowerL3_kVA
ST2NSX5MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 6085 | 46085 | NSX[5].MIN_ApparetnPowerTotal_kVA
ST2NSX5MIN_CosFL1 | REAL | IOD_ST2_TCP | 6087 | 46087 | NSX[5].MIN_CosFL1
ST2NSX5MIN_CosFL2 | REAL | IOD_ST2_TCP | 6089 | 46089 | NSX[5].MIN_CosFL2
ST2NSX5MIN_CosFL3 | REAL | IOD_ST2_TCP | 6091 | 46091 | NSX[5].MIN_CosFL3
ST2NSX5MIN_CosFTotal | REAL | IOD_ST2_TCP | 6093 | 46093 | NSX[5].MIN_CosFTotal
ST2NSX5MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 6095 | 46095 | NSX[5].MIN_CurrentAvgI1I2I3_A
ST2NSX5MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 6097 | 46097 | NSX[5].MIN_CurrentL1_A
ST2NSX5MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 6099 | 46099 | NSX[5].MIN_CurrentL2_A
ST2NSX5MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 6101 | 46101 | NSX[5].MIN_CurrentL3_A
ST2NSX5MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 6103 | 46103 | NSX[5].MIN_CurrentMaxL1L2L3N_A
ST2NSX5MIN_CurrentN_A | REAL | IOD_ST2_TCP | 6105 | 46105 | NSX[5].MIN_CurrentN_A
ST2NSX5MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 6107 | 46107 | NSX[5].MIN_DistortionPowerL1_kVAr
ST2NSX5MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 6109 | 46109 | NSX[5].MIN_DistortionPowerL2_kVAr
ST2NSX5MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 6111 | 46111 | NSX[5].MIN_DistortionPowerL3_kVAr
ST2NSX5MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 6113 | 46113 | NSX[5].MIN_DistortionPowerTotal_kVAr
ST2NSX5MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 6115 | 46115 | NSX[5].MIN_Frequency_Hz
ST2NSX5MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6117 | 46117 | NSX[5].MIN_FunReactivePowerL1_kVAr
ST2NSX5MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6119 | 46119 | NSX[5].MIN_FunReactivePowerL2_kVAr
ST2NSX5MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6121 | 46121 | NSX[5].MIN_FunReactivePowerL3_kVAr
ST2NSX5MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6123 | 46123 | NSX[5].MIN_FunReactivePowerTotal_kVAr
ST2NSX5MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 6125 | 46125 | NSX[5].MIN_PowerFactorL1
ST2NSX5MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 6127 | 46127 | NSX[5].MIN_PowerFactorL2
ST2NSX5MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 6129 | 46129 | NSX[5].MIN_PowerFactorL3
ST2NSX5MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 6131 | 46131 | NSX[5].MIN_PowerFactorTotal
ST2NSX5MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6133 | 46133 | NSX[5].MIN_ReactivePowerL1_kVAr
ST2NSX5MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6135 | 46135 | NSX[5].MIN_ReactivePowerL2_kVAr
ST2NSX5MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6137 | 46137 | NSX[5].MIN_ReactivePowerL3_kVAr
ST2NSX5MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6139 | 46139 | NSX[5].MIN_ReactivePowerTotal_kVAr
ST2NSX5MIN_THDI1_P | REAL | IOD_ST2_TCP | 6141 | 46141 | NSX[5].MIN_THDI1_P
ST2NSX5MIN_THDI2_P | REAL | IOD_ST2_TCP | 6143 | 46143 | NSX[5].MIN_THDI2_P
ST2NSX5MIN_THDI3_P | REAL | IOD_ST2_TCP | 6145 | 46145 | NSX[5].MIN_THDI3_P
ST2NSX5MIN_THDV12_P | REAL | IOD_ST2_TCP | 6147 | 46147 | NSX[5].MIN_THDV12_P
ST2NSX5MIN_THDV1N_P | REAL | IOD_ST2_TCP | 6149 | 46149 | NSX[5].MIN_THDV1N_P
ST2NSX5MIN_THDV23_P | REAL | IOD_ST2_TCP | 6151 | 46151 | NSX[5].MIN_THDV23_P
ST2NSX5MIN_THDV2N_P | REAL | IOD_ST2_TCP | 6153 | 46153 | NSX[5].MIN_THDV2N_P
ST2NSX5MIN_THDV31_P | REAL | IOD_ST2_TCP | 6155 | 46155 | NSX[5].MIN_THDV31_P
ST2NSX5MIN_THDV3N_P | REAL | IOD_ST2_TCP | 6157 | 46157 | NSX[5].MIN_THDV3N_P
ST2NSX5MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6159 | 46159 | NSX[5].MIN_VoltageAvgPhToN_V
ST2NSX5MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6161 | 46161 | NSX[5].MIN_VoltageAvgPhToPh_V
ST2NSX5MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6163 | 46163 | NSX[5].MIN_VoltageUnbV12_P
ST2NSX5MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6165 | 46165 | NSX[5].MIN_VoltageUnbV1N_P
ST2NSX5MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6167 | 46167 | NSX[5].MIN_VoltageUnbV23_P
ST2NSX5MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6169 | 46169 | NSX[5].MIN_VoltageUnbV2N_P
ST2NSX5MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6171 | 46171 | NSX[5].MIN_VoltageUnbV31_P
ST2NSX5MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6173 | 46173 | NSX[5].MIN_VoltageUnbV3N_P
ST2NSX5MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 6175 | 46175 | NSX[5].MIN_VoltageV12_V
ST2NSX5MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 6177 | 46177 | NSX[5].MIN_VoltageV1N_V
ST2NSX5MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 6179 | 46179 | NSX[5].MIN_VoltageV23_V
ST2NSX5MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 6181 | 46181 | NSX[5].MIN_VoltageV2N_V
ST2NSX5MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 6183 | 46183 | NSX[5].MIN_VoltageV31_V
ST2NSX5MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 6185 | 46185 | NSX[5].MIN_VoltageV3N_V
ST2NSX5PowerFactorL1 | REAL | IOD_ST2_TCP | 6187 | 46187 | NSX[5].PowerFactorL1
ST2NSX5PowerFactorL2 | REAL | IOD_ST2_TCP | 6189 | 46189 | NSX[5].PowerFactorL2
ST2NSX5PowerFactorL3 | REAL | IOD_ST2_TCP | 6191 | 46191 | NSX[5].PowerFactorL3
ST2NSX5PowerFactorTotal | REAL | IOD_ST2_TCP | 6193 | 46193 | NSX[5].PowerFactorTotal
ST2NSX5RazEner_D | REAL | IOD_ST2_TCP | 6195 | 46195 | NSX[5].RazEner_D
ST2NSX5RazEner_D_SCADA | REAL | IOD_ST2_TCP | 6197 | 46197 | NSX[5].RazEner_D_SCADA
ST2NSX5RazEner_D_TEMP | REAL | IOD_ST2_TCP | 6199 | 46199 | NSX[5].RazEner_D_TEMP
ST2NSX5RazEner_M | REAL | IOD_ST2_TCP | 6201 | 46201 | NSX[5].RazEner_M
ST2NSX5RazEner_M_SCADA | REAL | IOD_ST2_TCP | 6203 | 46203 | NSX[5].RazEner_M_SCADA
ST2NSX5RazEner_M_TEMP | REAL | IOD_ST2_TCP | 6205 | 46205 | NSX[5].RazEner_M_TEMP
ST2NSX5RazEner_T | REAL | IOD_ST2_TCP | 6207 | 46207 | NSX[5].RazEner_T
ST2NSX5RazEner_T_SCADA | REAL | IOD_ST2_TCP | 6209 | 46209 | NSX[5].RazEner_T_SCADA
ST2NSX5RazEner_T_TEMP | REAL | IOD_ST2_TCP | 6211 | 46211 | NSX[5].RazEner_T_TEMP
ST2NSX5ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 6213 | 46213 | NSX[5].ReactiveEnergy_kVArh
ST2NSX5ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 6215 | 46215 | NSX[5].ReactiveNegativeEnergy_kVArh
ST2NSX5ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 6217 | 46217 | NSX[5].ReactivePositiveEnergy_kVArh
ST2NSX5ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 6219 | 46219 | NSX[5].ReactivePowerDemand_kVAr
ST2NSX5ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6221 | 46221 | NSX[5].ReactivePowerL1_kVAr
ST2NSX5ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6223 | 46223 | NSX[5].ReactivePowerL2_kVAr
ST2NSX5ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6225 | 46225 | NSX[5].ReactivePowerL3_kVAr
ST2NSX5ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 6227 | 46227 | NSX[5].ReactivePowerMaxDemand_kVAr
ST2NSX5ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6229 | 46229 | NSX[5].ReactivePowerTotal_kVAr
ST2NSX5THDI1_P | REAL | IOD_ST2_TCP | 6231 | 46231 | NSX[5].THDI1_P
ST2NSX5THDI2_P | REAL | IOD_ST2_TCP | 6233 | 46233 | NSX[5].THDI2_P
ST2NSX5THDI3_P | REAL | IOD_ST2_TCP | 6235 | 46235 | NSX[5].THDI3_P
ST2NSX5THDV12_P | REAL | IOD_ST2_TCP | 6237 | 46237 | NSX[5].THDV12_P
ST2NSX5THDV1N_P | REAL | IOD_ST2_TCP | 6239 | 46239 | NSX[5].THDV1N_P
ST2NSX5THDV23_P | REAL | IOD_ST2_TCP | 6241 | 46241 | NSX[5].THDV23_P
ST2NSX5THDV2N_P | REAL | IOD_ST2_TCP | 6243 | 46243 | NSX[5].THDV2N_P
ST2NSX5THDV31_P | REAL | IOD_ST2_TCP | 6245 | 46245 | NSX[5].THDV31_P
ST2NSX5THDV3N_P | REAL | IOD_ST2_TCP | 6247 | 46247 | NSX[5].THDV3N_P
ST2NSX5VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6249 | 46249 | NSX[5].VoltageAvgPhToN_V
ST2NSX5VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6251 | 46251 | NSX[5].VoltageAvgPhToPh_V
ST2NSX5VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6253 | 46253 | NSX[5].VoltageUnbV12_P
ST2NSX5VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6255 | 46255 | NSX[5].VoltageUnbV1N_P
ST2NSX5VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6257 | 46257 | NSX[5].VoltageUnbV23_P
ST2NSX5VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6259 | 46259 | NSX[5].VoltageUnbV2N_P
ST2NSX5VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6261 | 46261 | NSX[5].VoltageUnbV31_P
ST2NSX5VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6263 | 46263 | NSX[5].VoltageUnbV3N_P
ST2NSX5VoltageV12_V | REAL | IOD_ST2_TCP | 6265 | 46265 | NSX[5].VoltageV12_V
ST2NSX5VoltageV1N_V | REAL | IOD_ST2_TCP | 6267 | 46267 | NSX[5].VoltageV1N_V
ST2NSX5VoltageV23_V | REAL | IOD_ST2_TCP | 6269 | 46269 | NSX[5].VoltageV23_V
ST2NSX5VoltageV2N_V | REAL | IOD_ST2_TCP | 6271 | 46271 | NSX[5].VoltageV2N_V
ST2NSX5VoltageV31_V | REAL | IOD_ST2_TCP | 6273 | 46273 | NSX[5].VoltageV31_V
ST2NSX5VoltageV3N_V | REAL | IOD_ST2_TCP | 6275 | 46275 | NSX[5].VoltageV3N_V
ST2NSX6ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 6277 | 46277 | NSX[6].ActiveEnergy_kWh
ST2NSX6ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 6279 | 46279 | NSX[6].ActiveNegativeEnergy_kWh
ST2NSX6ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 6281 | 46281 | NSX[6].ActivePositiveEnergy_kWh
ST2NSX6ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 6283 | 46283 | NSX[6].ActivePowerDemand_kW
ST2NSX6ActivePowerL1_kW | REAL | IOD_ST2_TCP | 6285 | 46285 | NSX[6].ActivePowerL1_kW
ST2NSX6ActivePowerL2_kW | REAL | IOD_ST2_TCP | 6287 | 46287 | NSX[6].ActivePowerL2_kW
ST2NSX6ActivePowerL3_kW | REAL | IOD_ST2_TCP | 6289 | 46289 | NSX[6].ActivePowerL3_kW
ST2NSX6ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 6291 | 46291 | NSX[6].ActivePowerMaxDemand_kW
ST2NSX6ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 6293 | 46293 | NSX[6].ActivePowerTotal_kW
ST2NSX6ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 6295 | 46295 | NSX[6].ApparentEnergy_kVAh
ST2NSX6ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 6297 | 46297 | NSX[6].ApparentPowerDemand_kVA
ST2NSX6ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 6299 | 46299 | NSX[6].ApparentPowerMaxDemand_kVA
ST2NSX6ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 6301 | 46301 | NSX[6].ApparetnPowerL1_kVA
ST2NSX6ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 6303 | 46303 | NSX[6].ApparetnPowerL2_kVA
ST2NSX6ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 6305 | 46305 | NSX[6].ApparetnPowerL3_kVA
ST2NSX6ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 6307 | 46307 | NSX[6].ApparetnPowerTotal_kVA
ST2NSX6CosFL1 | REAL | IOD_ST2_TCP | 6309 | 46309 | NSX[6].CosFL1
ST2NSX6CosFL2 | REAL | IOD_ST2_TCP | 6311 | 46311 | NSX[6].CosFL2
ST2NSX6CosFL3 | REAL | IOD_ST2_TCP | 6313 | 46313 | NSX[6].CosFL3
ST2NSX6CosFTotal | REAL | IOD_ST2_TCP | 6315 | 46315 | NSX[6].CosFTotal
ST2NSX6CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 6317 | 46317 | NSX[6].CumulNegativeActiveEnergy_kWh
ST2NSX6CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 6319 | 46319 | NSX[6].CumulPositiveActiveEnergy_kWh
ST2NSX6CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 6321 | 46321 | NSX[6].CurrentAvgI1I2I3_A
ST2NSX6CurrentDemandL1_A | REAL | IOD_ST2_TCP | 6323 | 46323 | NSX[6].CurrentDemandL1_A
ST2NSX6CurrentDemandL2_A | REAL | IOD_ST2_TCP | 6325 | 46325 | NSX[6].CurrentDemandL2_A
ST2NSX6CurrentDemandL3_A | REAL | IOD_ST2_TCP | 6327 | 46327 | NSX[6].CurrentDemandL3_A
ST2NSX6CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 6329 | 46329 | NSX[6].CurrentDemandMaxL1_A
ST2NSX6CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 6331 | 46331 | NSX[6].CurrentDemandMaxL2_A
ST2NSX6CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 6333 | 46333 | NSX[6].CurrentDemandMaxL3_A
ST2NSX6CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 6335 | 46335 | NSX[6].CurrentDemandMaxN_A
ST2NSX6CurrentDemandN_A | REAL | IOD_ST2_TCP | 6337 | 46337 | NSX[6].CurrentDemandN_A
ST2NSX6CurrentL1_A | REAL | IOD_ST2_TCP | 6339 | 46339 | NSX[6].CurrentL1_A
ST2NSX6CurrentL2_A | REAL | IOD_ST2_TCP | 6341 | 46341 | NSX[6].CurrentL2_A
ST2NSX6CurrentL3_A | REAL | IOD_ST2_TCP | 6343 | 46343 | NSX[6].CurrentL3_A
ST2NSX6CurrentN_A | REAL | IOD_ST2_TCP | 6345 | 46345 | NSX[6].CurrentN_A
ST2NSX6CurrentUnbI1_P | REAL | IOD_ST2_TCP | 6347 | 46347 | NSX[6].CurrentUnbI1_P
ST2NSX6CurrentUnbI2_P | REAL | IOD_ST2_TCP | 6349 | 46349 | NSX[6].CurrentUnbI2_P
ST2NSX6CurrentUnbI3_P | REAL | IOD_ST2_TCP | 6351 | 46351 | NSX[6].CurrentUnbI3_P
ST2NSX6CurrentUnbN_P | REAL | IOD_ST2_TCP | 6353 | 46353 | NSX[6].CurrentUnbN_P
ST2NSX6DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 6355 | 46355 | NSX[6].DelovnaEnergija_TEMP
ST2NSX6DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 6357 | 46357 | NSX[6].DistortionPowerL1_kVAr
ST2NSX6DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 6359 | 46359 | NSX[6].DistortionPowerL2_kVAr
ST2NSX6DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 6361 | 46361 | NSX[6].DistortionPowerL3_kVAr
ST2NSX6DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 6363 | 46363 | NSX[6].DistortionPowerTotal_kVAr
ST2NSX6Frequency_Hz | REAL | IOD_ST2_TCP | 6365 | 46365 | NSX[6].Frequency_Hz
ST2NSX6FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6367 | 46367 | NSX[6].FunReactivePowerL1_kVAr
ST2NSX6FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6369 | 46369 | NSX[6].FunReactivePowerL2_kVAr
ST2NSX6FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6371 | 46371 | NSX[6].FunReactivePowerL3_kVAr
ST2NSX6FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6373 | 46373 | NSX[6].FunReactivePowerTotal_kVAr
ST2NSX6MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 6375 | 46375 | NSX[6].MAX_ActivePowerL1_kW
ST2NSX6MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 6377 | 46377 | NSX[6].MAX_ActivePowerL2_kW
ST2NSX6MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 6379 | 46379 | NSX[6].MAX_ActivePowerL3_kW
ST2NSX6MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 6381 | 46381 | NSX[6].MAX_ActivePowerTotal_kW
ST2NSX6MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 6383 | 46383 | NSX[6].MAX_ApparetnPowerL1_kVA
ST2NSX6MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 6385 | 46385 | NSX[6].MAX_ApparetnPowerL2_kVA
ST2NSX6MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 6387 | 46387 | NSX[6].MAX_ApparetnPowerL3_kVA
ST2NSX6MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 6389 | 46389 | NSX[6].MAX_ApparetnPowerTotal_kVA
ST2NSX6MAX_CosFL1 | REAL | IOD_ST2_TCP | 6391 | 46391 | NSX[6].MAX_CosFL1
ST2NSX6MAX_CosFL2 | REAL | IOD_ST2_TCP | 6393 | 46393 | NSX[6].MAX_CosFL2
ST2NSX6MAX_CosFL3 | REAL | IOD_ST2_TCP | 6395 | 46395 | NSX[6].MAX_CosFL3
ST2NSX6MAX_CosFTotal | REAL | IOD_ST2_TCP | 6397 | 46397 | NSX[6].MAX_CosFTotal
ST2NSX6MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 6399 | 46399 | NSX[6].MAX_CurrentAvgI1I2I3_A
ST2NSX6MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 6401 | 46401 | NSX[6].MAX_CurrentL1_A
ST2NSX6MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 6403 | 46403 | NSX[6].MAX_CurrentL2_A
ST2NSX6MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 6405 | 46405 | NSX[6].MAX_CurrentL3_A
ST2NSX6MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 6407 | 46407 | NSX[6].MAX_CurrentMaxL1L2L3N_A
ST2NSX6MAX_CurrentN_A | REAL | IOD_ST2_TCP | 6409 | 46409 | NSX[6].MAX_CurrentN_A
ST2NSX6MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 6411 | 46411 | NSX[6].MAX_DistortionPowerL1_kVAr
ST2NSX6MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 6413 | 46413 | NSX[6].MAX_DistortionPowerL2_kVAr
ST2NSX6MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 6415 | 46415 | NSX[6].MAX_DistortionPowerL3_kVAr
ST2NSX6MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 6417 | 46417 | NSX[6].MAX_DistortionPowerTotal_kVAr
ST2NSX6MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 6419 | 46419 | NSX[6].MAX_Frequency_Hz
ST2NSX6MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6421 | 46421 | NSX[6].MAX_FunReactivePowerL1_kVAr
ST2NSX6MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6423 | 46423 | NSX[6].MAX_FunReactivePowerL2_kVAr
ST2NSX6MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6425 | 46425 | NSX[6].MAX_FunReactivePowerL3_kVAr
ST2NSX6MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6427 | 46427 | NSX[6].MAX_FunReactivePowerTotal_kVAr
ST2NSX6MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 6429 | 46429 | NSX[6].MAX_PowerFactorL1
ST2NSX6MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 6431 | 46431 | NSX[6].MAX_PowerFactorL2
ST2NSX6MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 6433 | 46433 | NSX[6].MAX_PowerFactorL3
ST2NSX6MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 6435 | 46435 | NSX[6].MAX_PowerFactorTotal
ST2NSX6MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6437 | 46437 | NSX[6].MAX_ReactivePowerL1_kVAr
ST2NSX6MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6439 | 46439 | NSX[6].MAX_ReactivePowerL2_kVAr
ST2NSX6MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6441 | 46441 | NSX[6].MAX_ReactivePowerL3_kVAr
ST2NSX6MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6443 | 46443 | NSX[6].MAX_ReactivePowerTotal_kVAr
ST2NSX6MAX_THDI1_P | REAL | IOD_ST2_TCP | 6445 | 46445 | NSX[6].MAX_THDI1_P
ST2NSX6MAX_THDI2_P | REAL | IOD_ST2_TCP | 6447 | 46447 | NSX[6].MAX_THDI2_P
ST2NSX6MAX_THDI3_P | REAL | IOD_ST2_TCP | 6449 | 46449 | NSX[6].MAX_THDI3_P
ST2NSX6MAX_THDV12_P | REAL | IOD_ST2_TCP | 6451 | 46451 | NSX[6].MAX_THDV12_P
ST2NSX6MAX_THDV1N_P | REAL | IOD_ST2_TCP | 6453 | 46453 | NSX[6].MAX_THDV1N_P
ST2NSX6MAX_THDV23_P | REAL | IOD_ST2_TCP | 6455 | 46455 | NSX[6].MAX_THDV23_P
ST2NSX6MAX_THDV2N_P | REAL | IOD_ST2_TCP | 6457 | 46457 | NSX[6].MAX_THDV2N_P
ST2NSX6MAX_THDV31_P | REAL | IOD_ST2_TCP | 6459 | 46459 | NSX[6].MAX_THDV31_P
ST2NSX6MAX_THDV3N_P | REAL | IOD_ST2_TCP | 6461 | 46461 | NSX[6].MAX_THDV3N_P
ST2NSX6MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6463 | 46463 | NSX[6].MAX_VoltageAvgPhToN_V
ST2NSX6MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6465 | 46465 | NSX[6].MAX_VoltageAvgPhToPh_V
ST2NSX6MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6467 | 46467 | NSX[6].MAX_VoltageUnbV12_P
ST2NSX6MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6469 | 46469 | NSX[6].MAX_VoltageUnbV1N_P
ST2NSX6MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6471 | 46471 | NSX[6].MAX_VoltageUnbV23_P
ST2NSX6MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6473 | 46473 | NSX[6].MAX_VoltageUnbV2N_P
ST2NSX6MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6475 | 46475 | NSX[6].MAX_VoltageUnbV31_P
ST2NSX6MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6477 | 46477 | NSX[6].MAX_VoltageUnbV3N_P
ST2NSX6MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 6479 | 46479 | NSX[6].MAX_VoltageV12_V
ST2NSX6MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 6481 | 46481 | NSX[6].MAX_VoltageV1N_V
ST2NSX6MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 6483 | 46483 | NSX[6].MAX_VoltageV23_V
ST2NSX6MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 6485 | 46485 | NSX[6].MAX_VoltageV2N_V
ST2NSX6MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 6487 | 46487 | NSX[6].MAX_VoltageV31_V
ST2NSX6MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 6489 | 46489 | NSX[6].MAX_VoltageV3N_V
ST2NSX6MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 6491 | 46491 | NSX[6].MIN_ActivePowerL1_kW
ST2NSX6MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 6493 | 46493 | NSX[6].MIN_ActivePowerL2_kW
ST2NSX6MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 6495 | 46495 | NSX[6].MIN_ActivePowerL3_kW
ST2NSX6MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 6497 | 46497 | NSX[6].MIN_ActivePowerTotal_kW
ST2NSX6MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 6499 | 46499 | NSX[6].MIN_ApparetnPowerL1_kVA
ST2NSX6MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 6501 | 46501 | NSX[6].MIN_ApparetnPowerL2_kVA
ST2NSX6MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 6503 | 46503 | NSX[6].MIN_ApparetnPowerL3_kVA
ST2NSX6MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 6505 | 46505 | NSX[6].MIN_ApparetnPowerTotal_kVA
ST2NSX6MIN_CosFL1 | REAL | IOD_ST2_TCP | 6507 | 46507 | NSX[6].MIN_CosFL1
ST2NSX6MIN_CosFL2 | REAL | IOD_ST2_TCP | 6509 | 46509 | NSX[6].MIN_CosFL2
ST2NSX6MIN_CosFL3 | REAL | IOD_ST2_TCP | 6511 | 46511 | NSX[6].MIN_CosFL3
ST2NSX6MIN_CosFTotal | REAL | IOD_ST2_TCP | 6513 | 46513 | NSX[6].MIN_CosFTotal
ST2NSX6MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 6515 | 46515 | NSX[6].MIN_CurrentAvgI1I2I3_A
ST2NSX6MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 6517 | 46517 | NSX[6].MIN_CurrentL1_A
ST2NSX6MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 6519 | 46519 | NSX[6].MIN_CurrentL2_A
ST2NSX6MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 6521 | 46521 | NSX[6].MIN_CurrentL3_A
ST2NSX6MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 6523 | 46523 | NSX[6].MIN_CurrentMaxL1L2L3N_A
ST2NSX6MIN_CurrentN_A | REAL | IOD_ST2_TCP | 6525 | 46525 | NSX[6].MIN_CurrentN_A
ST2NSX6MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 6527 | 46527 | NSX[6].MIN_DistortionPowerL1_kVAr
ST2NSX6MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 6529 | 46529 | NSX[6].MIN_DistortionPowerL2_kVAr
ST2NSX6MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 6531 | 46531 | NSX[6].MIN_DistortionPowerL3_kVAr
ST2NSX6MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 6533 | 46533 | NSX[6].MIN_DistortionPowerTotal_kVAr
ST2NSX6MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 6535 | 46535 | NSX[6].MIN_Frequency_Hz
ST2NSX6MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6537 | 46537 | NSX[6].MIN_FunReactivePowerL1_kVAr
ST2NSX6MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6539 | 46539 | NSX[6].MIN_FunReactivePowerL2_kVAr
ST2NSX6MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6541 | 46541 | NSX[6].MIN_FunReactivePowerL3_kVAr
ST2NSX6MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6543 | 46543 | NSX[6].MIN_FunReactivePowerTotal_kVAr
ST2NSX6MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 6545 | 46545 | NSX[6].MIN_PowerFactorL1
ST2NSX6MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 6547 | 46547 | NSX[6].MIN_PowerFactorL2
ST2NSX6MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 6549 | 46549 | NSX[6].MIN_PowerFactorL3
ST2NSX6MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 6551 | 46551 | NSX[6].MIN_PowerFactorTotal
ST2NSX6MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6553 | 46553 | NSX[6].MIN_ReactivePowerL1_kVAr
ST2NSX6MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6555 | 46555 | NSX[6].MIN_ReactivePowerL2_kVAr
ST2NSX6MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6557 | 46557 | NSX[6].MIN_ReactivePowerL3_kVAr
ST2NSX6MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6559 | 46559 | NSX[6].MIN_ReactivePowerTotal_kVAr
ST2NSX6MIN_THDI1_P | REAL | IOD_ST2_TCP | 6561 | 46561 | NSX[6].MIN_THDI1_P
ST2NSX6MIN_THDI2_P | REAL | IOD_ST2_TCP | 6563 | 46563 | NSX[6].MIN_THDI2_P
ST2NSX6MIN_THDI3_P | REAL | IOD_ST2_TCP | 6565 | 46565 | NSX[6].MIN_THDI3_P
ST2NSX6MIN_THDV12_P | REAL | IOD_ST2_TCP | 6567 | 46567 | NSX[6].MIN_THDV12_P
ST2NSX6MIN_THDV1N_P | REAL | IOD_ST2_TCP | 6569 | 46569 | NSX[6].MIN_THDV1N_P
ST2NSX6MIN_THDV23_P | REAL | IOD_ST2_TCP | 6571 | 46571 | NSX[6].MIN_THDV23_P
ST2NSX6MIN_THDV2N_P | REAL | IOD_ST2_TCP | 6573 | 46573 | NSX[6].MIN_THDV2N_P
ST2NSX6MIN_THDV31_P | REAL | IOD_ST2_TCP | 6575 | 46575 | NSX[6].MIN_THDV31_P
ST2NSX6MIN_THDV3N_P | REAL | IOD_ST2_TCP | 6577 | 46577 | NSX[6].MIN_THDV3N_P
ST2NSX6MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6579 | 46579 | NSX[6].MIN_VoltageAvgPhToN_V
ST2NSX6MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6581 | 46581 | NSX[6].MIN_VoltageAvgPhToPh_V
ST2NSX6MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6583 | 46583 | NSX[6].MIN_VoltageUnbV12_P
ST2NSX6MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6585 | 46585 | NSX[6].MIN_VoltageUnbV1N_P
ST2NSX6MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6587 | 46587 | NSX[6].MIN_VoltageUnbV23_P
ST2NSX6MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6589 | 46589 | NSX[6].MIN_VoltageUnbV2N_P
ST2NSX6MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6591 | 46591 | NSX[6].MIN_VoltageUnbV31_P
ST2NSX6MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6593 | 46593 | NSX[6].MIN_VoltageUnbV3N_P
ST2NSX6MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 6595 | 46595 | NSX[6].MIN_VoltageV12_V
ST2NSX6MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 6597 | 46597 | NSX[6].MIN_VoltageV1N_V
ST2NSX6MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 6599 | 46599 | NSX[6].MIN_VoltageV23_V
ST2NSX6MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 6601 | 46601 | NSX[6].MIN_VoltageV2N_V
ST2NSX6MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 6603 | 46603 | NSX[6].MIN_VoltageV31_V
ST2NSX6MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 6605 | 46605 | NSX[6].MIN_VoltageV3N_V
ST2NSX6PowerFactorL1 | REAL | IOD_ST2_TCP | 6607 | 46607 | NSX[6].PowerFactorL1
ST2NSX6PowerFactorL2 | REAL | IOD_ST2_TCP | 6609 | 46609 | NSX[6].PowerFactorL2
ST2NSX6PowerFactorL3 | REAL | IOD_ST2_TCP | 6611 | 46611 | NSX[6].PowerFactorL3
ST2NSX6PowerFactorTotal | REAL | IOD_ST2_TCP | 6613 | 46613 | NSX[6].PowerFactorTotal
ST2NSX6RazEner_D | REAL | IOD_ST2_TCP | 6615 | 46615 | NSX[6].RazEner_D
ST2NSX6RazEner_D_SCADA | REAL | IOD_ST2_TCP | 6617 | 46617 | NSX[6].RazEner_D_SCADA
ST2NSX6RazEner_D_TEMP | REAL | IOD_ST2_TCP | 6619 | 46619 | NSX[6].RazEner_D_TEMP
ST2NSX6RazEner_M | REAL | IOD_ST2_TCP | 6621 | 46621 | NSX[6].RazEner_M
ST2NSX6RazEner_M_SCADA | REAL | IOD_ST2_TCP | 6623 | 46623 | NSX[6].RazEner_M_SCADA
ST2NSX6RazEner_M_TEMP | REAL | IOD_ST2_TCP | 6625 | 46625 | NSX[6].RazEner_M_TEMP
ST2NSX6RazEner_T | REAL | IOD_ST2_TCP | 6627 | 46627 | NSX[6].RazEner_T
ST2NSX6RazEner_T_SCADA | REAL | IOD_ST2_TCP | 6629 | 46629 | NSX[6].RazEner_T_SCADA
ST2NSX6RazEner_T_TEMP | REAL | IOD_ST2_TCP | 6631 | 46631 | NSX[6].RazEner_T_TEMP
ST2NSX6ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 6633 | 46633 | NSX[6].ReactiveEnergy_kVArh
ST2NSX6ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 6635 | 46635 | NSX[6].ReactiveNegativeEnergy_kVArh
ST2NSX6ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 6637 | 46637 | NSX[6].ReactivePositiveEnergy_kVArh
ST2NSX6ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 6639 | 46639 | NSX[6].ReactivePowerDemand_kVAr
ST2NSX6ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 6641 | 46641 | NSX[6].ReactivePowerL1_kVAr
ST2NSX6ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 6643 | 46643 | NSX[6].ReactivePowerL2_kVAr
ST2NSX6ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 6645 | 46645 | NSX[6].ReactivePowerL3_kVAr
ST2NSX6ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 6647 | 46647 | NSX[6].ReactivePowerMaxDemand_kVAr
ST2NSX6ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 6649 | 46649 | NSX[6].ReactivePowerTotal_kVAr
ST2NSX6THDI1_P | REAL | IOD_ST2_TCP | 6651 | 46651 | NSX[6].THDI1_P
ST2NSX6THDI2_P | REAL | IOD_ST2_TCP | 6653 | 46653 | NSX[6].THDI2_P
ST2NSX6THDI3_P | REAL | IOD_ST2_TCP | 6655 | 46655 | NSX[6].THDI3_P
ST2NSX6THDV12_P | REAL | IOD_ST2_TCP | 6657 | 46657 | NSX[6].THDV12_P
ST2NSX6THDV1N_P | REAL | IOD_ST2_TCP | 6659 | 46659 | NSX[6].THDV1N_P
ST2NSX6THDV23_P | REAL | IOD_ST2_TCP | 6661 | 46661 | NSX[6].THDV23_P
ST2NSX6THDV2N_P | REAL | IOD_ST2_TCP | 6663 | 46663 | NSX[6].THDV2N_P
ST2NSX6THDV31_P | REAL | IOD_ST2_TCP | 6665 | 46665 | NSX[6].THDV31_P
ST2NSX6THDV3N_P | REAL | IOD_ST2_TCP | 6667 | 46667 | NSX[6].THDV3N_P
ST2NSX6VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 6669 | 46669 | NSX[6].VoltageAvgPhToN_V
ST2NSX6VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 6671 | 46671 | NSX[6].VoltageAvgPhToPh_V
ST2NSX6VoltageUnbV12_P | REAL | IOD_ST2_TCP | 6673 | 46673 | NSX[6].VoltageUnbV12_P
ST2NSX6VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 6675 | 46675 | NSX[6].VoltageUnbV1N_P
ST2NSX6VoltageUnbV23_P | REAL | IOD_ST2_TCP | 6677 | 46677 | NSX[6].VoltageUnbV23_P
ST2NSX6VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 6679 | 46679 | NSX[6].VoltageUnbV2N_P
ST2NSX6VoltageUnbV31_P | REAL | IOD_ST2_TCP | 6681 | 46681 | NSX[6].VoltageUnbV31_P
ST2NSX6VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 6683 | 46683 | NSX[6].VoltageUnbV3N_P
ST2NSX6VoltageV12_V | REAL | IOD_ST2_TCP | 6685 | 46685 | NSX[6].VoltageV12_V
ST2NSX6VoltageV1N_V | REAL | IOD_ST2_TCP | 6687 | 46687 | NSX[6].VoltageV1N_V
ST2NSX6VoltageV23_V | REAL | IOD_ST2_TCP | 6689 | 46689 | NSX[6].VoltageV23_V
ST2NSX6VoltageV2N_V | REAL | IOD_ST2_TCP | 6691 | 46691 | NSX[6].VoltageV2N_V
ST2NSX6VoltageV31_V | REAL | IOD_ST2_TCP | 6693 | 46693 | NSX[6].VoltageV31_V
ST2NSX6VoltageV3N_V | REAL | IOD_ST2_TCP | 6695 | 46695 | NSX[6].VoltageV3N_V
ST2PMMVirACurrent10 | REAL | IOD_ST2_TCP | 6697 | 46697 | PMM.VirA.Current[10]
ST2PMMVirACurrent11 | REAL | IOD_ST2_TCP | 6699 | 46699 | PMM.VirA.Current[11]
ST2PMMVirACurrent12 | REAL | IOD_ST2_TCP | 6701 | 46701 | PMM.VirA.Current[12]
ST2PMMVirACurrent13 | REAL | IOD_ST2_TCP | 6703 | 46703 | PMM.VirA.Current[13]
ST2PMMVirACurrent14 | REAL | IOD_ST2_TCP | 6705 | 46705 | PMM.VirA.Current[14]
ST2PMMVirACurrent15 | REAL | IOD_ST2_TCP | 6707 | 46707 | PMM.VirA.Current[15]
ST2PMMVirACurrent16 | REAL | IOD_ST2_TCP | 6709 | 46709 | PMM.VirA.Current[16]
ST2PMMVirACurrent17 | REAL | IOD_ST2_TCP | 6711 | 46711 | PMM.VirA.Current[17]
ST2PMMVirACurrent18 | REAL | IOD_ST2_TCP | 6713 | 46713 | PMM.VirA.Current[18]
ST2PMMVirACurrent19 | REAL | IOD_ST2_TCP | 6715 | 46715 | PMM.VirA.Current[19]
ST2PMMVirACurrent1 | REAL | IOD_ST2_TCP | 6717 | 46717 | PMM.VirA.Current[1]
ST2PMMVirACurrent20 | REAL | IOD_ST2_TCP | 6719 | 46719 | PMM.VirA.Current[20]
ST2PMMVirACurrent21 | REAL | IOD_ST2_TCP | 6721 | 46721 | PMM.VirA.Current[21]
ST2PMMVirACurrent22 | REAL | IOD_ST2_TCP | 6723 | 46723 | PMM.VirA.Current[22]
ST2PMMVirACurrent23 | REAL | IOD_ST2_TCP | 6725 | 46725 | PMM.VirA.Current[23]
ST2PMMVirACurrent24 | REAL | IOD_ST2_TCP | 6727 | 46727 | PMM.VirA.Current[24]
ST2PMMVirACurrent25 | REAL | IOD_ST2_TCP | 6729 | 46729 | PMM.VirA.Current[25]
ST2PMMVirACurrent26 | REAL | IOD_ST2_TCP | 6731 | 46731 | PMM.VirA.Current[26]
ST2PMMVirACurrent27 | REAL | IOD_ST2_TCP | 6733 | 46733 | PMM.VirA.Current[27]
ST2PMMVirACurrent28 | REAL | IOD_ST2_TCP | 6735 | 46735 | PMM.VirA.Current[28]
ST2PMMVirACurrent29 | REAL | IOD_ST2_TCP | 6737 | 46737 | PMM.VirA.Current[29]
ST2PMMVirACurrent2 | REAL | IOD_ST2_TCP | 6739 | 46739 | PMM.VirA.Current[2]
ST2PMMVirACurrent30 | REAL | IOD_ST2_TCP | 6741 | 46741 | PMM.VirA.Current[30]
ST2PMMVirACurrent31 | REAL | IOD_ST2_TCP | 6743 | 46743 | PMM.VirA.Current[31]
ST2PMMVirACurrent32 | REAL | IOD_ST2_TCP | 6745 | 46745 | PMM.VirA.Current[32]
ST2PMMVirACurrent33 | REAL | IOD_ST2_TCP | 6747 | 46747 | PMM.VirA.Current[33]
ST2PMMVirACurrent34 | REAL | IOD_ST2_TCP | 6749 | 46749 | PMM.VirA.Current[34]
ST2PMMVirACurrent35 | REAL | IOD_ST2_TCP | 6751 | 46751 | PMM.VirA.Current[35]
ST2PMMVirACurrent36 | REAL | IOD_ST2_TCP | 6753 | 46753 | PMM.VirA.Current[36]
ST2PMMVirACurrent37 | REAL | IOD_ST2_TCP | 6755 | 46755 | PMM.VirA.Current[37]
ST2PMMVirACurrent38 | REAL | IOD_ST2_TCP | 6757 | 46757 | PMM.VirA.Current[38]
ST2PMMVirACurrent39 | REAL | IOD_ST2_TCP | 6759 | 46759 | PMM.VirA.Current[39]
ST2PMMVirACurrent3 | REAL | IOD_ST2_TCP | 6761 | 46761 | PMM.VirA.Current[3]
ST2PMMVirACurrent40 | REAL | IOD_ST2_TCP | 6763 | 46763 | PMM.VirA.Current[40]
ST2PMMVirACurrent41 | REAL | IOD_ST2_TCP | 6765 | 46765 | PMM.VirA.Current[41]
ST2PMMVirACurrent42 | REAL | IOD_ST2_TCP | 6767 | 46767 | PMM.VirA.Current[42]
ST2PMMVirACurrent43 | REAL | IOD_ST2_TCP | 6769 | 46769 | PMM.VirA.Current[43]
ST2PMMVirACurrent44 | REAL | IOD_ST2_TCP | 6771 | 46771 | PMM.VirA.Current[44]
ST2PMMVirACurrent4 | REAL | IOD_ST2_TCP | 6773 | 46773 | PMM.VirA.Current[4]
ST2PMMVirACurrent5 | REAL | IOD_ST2_TCP | 6775 | 46775 | PMM.VirA.Current[5]
ST2PMMVirACurrent6 | REAL | IOD_ST2_TCP | 6777 | 46777 | PMM.VirA.Current[6]
ST2PMMVirACurrent7 | REAL | IOD_ST2_TCP | 6779 | 46779 | PMM.VirA.Current[7]
ST2PMMVirACurrent8 | REAL | IOD_ST2_TCP | 6781 | 46781 | PMM.VirA.Current[8]
ST2PMMVirACurrent9 | REAL | IOD_ST2_TCP | 6783 | 46783 | PMM.VirA.Current[9]
ST2PMMVirA_fsys | REAL | IOD_ST2_TCP | 6785 | 46785 | PMM.VirA_fsys
ST2PMMVirA_Isys | REAL | IOD_ST2_TCP | 6787 | 46787 | PMM.VirA_Isys
ST2PMMVirA_PFsys | REAL | IOD_ST2_TCP | 6789 | 46789 | PMM.VirA_PFsys
ST2PMMVirA_Psys | REAL | IOD_ST2_TCP | 6791 | 46791 | PMM.VirA_Psys
ST2PMMVirA_Qsys | REAL | IOD_ST2_TCP | 6793 | 46793 | PMM.VirA_Qsys
ST2PMMVirA_Ssys | REAL | IOD_ST2_TCP | 6795 | 46795 | PMM.VirA_Ssys
ST2PMMVirA_Usys | REAL | IOD_ST2_TCP | 6797 | 46797 | PMM.VirA_Usys
ST2PMMVirAActiveEnergyConsumed_kWh | REAL | IOD_ST2_TCP | 6799 | 46799 | PMM.VirAActiveEnergyConsumed_kWh
ST2PMMVirAActivePowerPhaseA_kW | REAL | IOD_ST2_TCP | 6801 | 46801 | PMM.VirAActivePowerPhaseA_kW
ST2PMMVirAActivePowerPhaseB_kW | REAL | IOD_ST2_TCP | 6803 | 46803 | PMM.VirAActivePowerPhaseB_kW
ST2PMMVirAActivePowerPhaseC_kW | REAL | IOD_ST2_TCP | 6805 | 46805 | PMM.VirAActivePowerPhaseC_kW
ST2PMMVirAAparentPowerPhaseA | REAL | IOD_ST2_TCP | 6807 | 46807 | PMM.VirAAparentPowerPhaseA
ST2PMMVirAAparentPowerPhaseB | REAL | IOD_ST2_TCP | 6809 | 46809 | PMM.VirAAparentPowerPhaseB
ST2PMMVirAAparentPowerPhaseC | REAL | IOD_ST2_TCP | 6811 | 46811 | PMM.VirAAparentPowerPhaseC
ST2PMMVirACurrentInPhaseA_A | REAL | IOD_ST2_TCP | 6813 | 46813 | PMM.VirACurrentInPhaseA_A
ST2PMMVirACurrentInPhaseB_A | REAL | IOD_ST2_TCP | 6815 | 46815 | PMM.VirACurrentInPhaseB_A
ST2PMMVirACurrentInPhaseC_A | REAL | IOD_ST2_TCP | 6817 | 46817 | PMM.VirACurrentInPhaseC_A
ST2PMMVirAReactiveEnergyConsumed_kVARh | REAL | IOD_ST2_TCP | 6819 | 46819 | PMM.VirAReactiveEnergyConsumed_kVARh
ST2PMMVirAReactivePowerPhaseA | REAL | IOD_ST2_TCP | 6821 | 46821 | PMM.VirAReactivePowerPhaseA
ST2PMMVirAReactivePowerPhaseB | REAL | IOD_ST2_TCP | 6823 | 46823 | PMM.VirAReactivePowerPhaseB
ST2PMMVirAReactivePowerPhaseC | REAL | IOD_ST2_TCP | 6825 | 46825 | PMM.VirAReactivePowerPhaseC
ST2PMMVirAVoltageBetweenPhaseAB_V | REAL | IOD_ST2_TCP | 6827 | 46827 | PMM.VirAVoltageBetweenPhaseAB_V
ST2PMMVirAVoltageBetweenPhaseAN_V | REAL | IOD_ST2_TCP | 6829 | 46829 | PMM.VirAVoltageBetweenPhaseAN_V
ST2PMMVirAVoltageBetweenPhaseBC_V | REAL | IOD_ST2_TCP | 6831 | 46831 | PMM.VirAVoltageBetweenPhaseBC_V
ST2PMMVirAVoltageBetweenPhaseBN_V | REAL | IOD_ST2_TCP | 6833 | 46833 | PMM.VirAVoltageBetweenPhaseBN_V
ST2PMMVirAVoltageBetweenPhaseCA_V | REAL | IOD_ST2_TCP | 6835 | 46835 | PMM.VirAVoltageBetweenPhaseCA_V
ST2PMMVirAVoltageBetweenPhaseCN_V | REAL | IOD_ST2_TCP | 6837 | 46837 | PMM.VirAVoltageBetweenPhaseCN_V
ST2PMMVirBCurrent10 | REAL | IOD_ST2_TCP | 6839 | 46839 | PMM.VirB.Current[10]
ST2PMMVirBCurrent11 | REAL | IOD_ST2_TCP | 6841 | 46841 | PMM.VirB.Current[11]
ST2PMMVirBCurrent12 | REAL | IOD_ST2_TCP | 6843 | 46843 | PMM.VirB.Current[12]
ST2PMMVirBCurrent13 | REAL | IOD_ST2_TCP | 6845 | 46845 | PMM.VirB.Current[13]
ST2PMMVirBCurrent14 | REAL | IOD_ST2_TCP | 6847 | 46847 | PMM.VirB.Current[14]
ST2PMMVirBCurrent15 | REAL | IOD_ST2_TCP | 6849 | 46849 | PMM.VirB.Current[15]
ST2PMMVirBCurrent16 | REAL | IOD_ST2_TCP | 6851 | 46851 | PMM.VirB.Current[16]
ST2PMMVirBCurrent17 | REAL | IOD_ST2_TCP | 6853 | 46853 | PMM.VirB.Current[17]
ST2PMMVirBCurrent18 | REAL | IOD_ST2_TCP | 6855 | 46855 | PMM.VirB.Current[18]
ST2PMMVirBCurrent19 | REAL | IOD_ST2_TCP | 6857 | 46857 | PMM.VirB.Current[19]
ST2PMMVirBCurrent1 | REAL | IOD_ST2_TCP | 6859 | 46859 | PMM.VirB.Current[1]
ST2PMMVirBCurrent20 | REAL | IOD_ST2_TCP | 6861 | 46861 | PMM.VirB.Current[20]
ST2PMMVirBCurrent21 | REAL | IOD_ST2_TCP | 6863 | 46863 | PMM.VirB.Current[21]
ST2PMMVirBCurrent22 | REAL | IOD_ST2_TCP | 6865 | 46865 | PMM.VirB.Current[22]
ST2PMMVirBCurrent23 | REAL | IOD_ST2_TCP | 6867 | 46867 | PMM.VirB.Current[23]
ST2PMMVirBCurrent24 | REAL | IOD_ST2_TCP | 6869 | 46869 | PMM.VirB.Current[24]
ST2PMMVirBCurrent25 | REAL | IOD_ST2_TCP | 6871 | 46871 | PMM.VirB.Current[25]
ST2PMMVirBCurrent26 | REAL | IOD_ST2_TCP | 6873 | 46873 | PMM.VirB.Current[26]
ST2PMMVirBCurrent27 | REAL | IOD_ST2_TCP | 6875 | 46875 | PMM.VirB.Current[27]
ST2PMMVirBCurrent28 | REAL | IOD_ST2_TCP | 6877 | 46877 | PMM.VirB.Current[28]
ST2PMMVirBCurrent29 | REAL | IOD_ST2_TCP | 6879 | 46879 | PMM.VirB.Current[29]
ST2PMMVirBCurrent2 | REAL | IOD_ST2_TCP | 6881 | 46881 | PMM.VirB.Current[2]
ST2PMMVirBCurrent30 | REAL | IOD_ST2_TCP | 6883 | 46883 | PMM.VirB.Current[30]
ST2PMMVirBCurrent31 | REAL | IOD_ST2_TCP | 6885 | 46885 | PMM.VirB.Current[31]
ST2PMMVirBCurrent32 | REAL | IOD_ST2_TCP | 6887 | 46887 | PMM.VirB.Current[32]
ST2PMMVirBCurrent33 | REAL | IOD_ST2_TCP | 6889 | 46889 | PMM.VirB.Current[33]
ST2PMMVirBCurrent34 | REAL | IOD_ST2_TCP | 6891 | 46891 | PMM.VirB.Current[34]
ST2PMMVirBCurrent35 | REAL | IOD_ST2_TCP | 6893 | 46893 | PMM.VirB.Current[35]
ST2PMMVirBCurrent36 | REAL | IOD_ST2_TCP | 6895 | 46895 | PMM.VirB.Current[36]
ST2PMMVirBCurrent37 | REAL | IOD_ST2_TCP | 6897 | 46897 | PMM.VirB.Current[37]
ST2PMMVirBCurrent38 | REAL | IOD_ST2_TCP | 6899 | 46899 | PMM.VirB.Current[38]
ST2PMMVirBCurrent39 | REAL | IOD_ST2_TCP | 6901 | 46901 | PMM.VirB.Current[39]
ST2PMMVirBCurrent3 | REAL | IOD_ST2_TCP | 6903 | 46903 | PMM.VirB.Current[3]
ST2PMMVirBCurrent40 | REAL | IOD_ST2_TCP | 6905 | 46905 | PMM.VirB.Current[40]
ST2PMMVirBCurrent41 | REAL | IOD_ST2_TCP | 6907 | 46907 | PMM.VirB.Current[41]
ST2PMMVirBCurrent42 | REAL | IOD_ST2_TCP | 6909 | 46909 | PMM.VirB.Current[42]
ST2PMMVirBCurrent43 | REAL | IOD_ST2_TCP | 6911 | 46911 | PMM.VirB.Current[43]
ST2PMMVirBCurrent44 | REAL | IOD_ST2_TCP | 6913 | 46913 | PMM.VirB.Current[44]
ST2PMMVirBCurrent4 | REAL | IOD_ST2_TCP | 6915 | 46915 | PMM.VirB.Current[4]
ST2PMMVirBCurrent5 | REAL | IOD_ST2_TCP | 6917 | 46917 | PMM.VirB.Current[5]
ST2PMMVirBCurrent6 | REAL | IOD_ST2_TCP | 6919 | 46919 | PMM.VirB.Current[6]
ST2PMMVirBCurrent7 | REAL | IOD_ST2_TCP | 6921 | 46921 | PMM.VirB.Current[7]
ST2PMMVirBCurrent8 | REAL | IOD_ST2_TCP | 6923 | 46923 | PMM.VirB.Current[8]
ST2PMMVirBCurrent9 | REAL | IOD_ST2_TCP | 6925 | 46925 | PMM.VirB.Current[9]
ST2PMMVirB_fsys | REAL | IOD_ST2_TCP | 6927 | 46927 | PMM.VirB_fsys
ST2PMMVirB_Isys | REAL | IOD_ST2_TCP | 6929 | 46929 | PMM.VirB_Isys
ST2PMMVirB_PFsys | REAL | IOD_ST2_TCP | 6931 | 46931 | PMM.VirB_PFsys
ST2PMMVirB_Psys | REAL | IOD_ST2_TCP | 6933 | 46933 | PMM.VirB_Psys
ST2PMMVirB_Qsys | REAL | IOD_ST2_TCP | 6935 | 46935 | PMM.VirB_Qsys
ST2PMMVirB_Ssys | REAL | IOD_ST2_TCP | 6937 | 46937 | PMM.VirB_Ssys
ST2PMMVirB_Usys | REAL | IOD_ST2_TCP | 6939 | 46939 | PMM.VirB_Usys
ST2PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_ST2_TCP | 6941 | 46941 | PMM.VirBActiveEnergyConsumed_kWh
ST2PMMVirBActivePowerPhaseA_kW | REAL | IOD_ST2_TCP | 6943 | 46943 | PMM.VirBActivePowerPhaseA_kW
ST2PMMVirBActivePowerPhaseB_kW | REAL | IOD_ST2_TCP | 6945 | 46945 | PMM.VirBActivePowerPhaseB_kW
ST2PMMVirBActivePowerPhaseC_kW | REAL | IOD_ST2_TCP | 6947 | 46947 | PMM.VirBActivePowerPhaseC_kW
ST2PMMVirBAparentPowerPhaseA | REAL | IOD_ST2_TCP | 6949 | 46949 | PMM.VirBAparentPowerPhaseA
ST2PMMVirBAparentPowerPhaseB | REAL | IOD_ST2_TCP | 6951 | 46951 | PMM.VirBAparentPowerPhaseB
ST2PMMVirBAparentPowerPhaseC | REAL | IOD_ST2_TCP | 6953 | 46953 | PMM.VirBAparentPowerPhaseC
ST2PMMVirBCurrentInPhaseA_A | REAL | IOD_ST2_TCP | 6955 | 46955 | PMM.VirBCurrentInPhaseA_A
ST2PMMVirBCurrentInPhaseB_A | REAL | IOD_ST2_TCP | 6957 | 46957 | PMM.VirBCurrentInPhaseB_A
ST2PMMVirBCurrentInPhaseC_A | REAL | IOD_ST2_TCP | 6959 | 46959 | PMM.VirBCurrentInPhaseC_A
ST2PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_ST2_TCP | 6961 | 46961 | PMM.VirBReactiveEnergyConsumed_kVARh
ST2PMMVirBReactivePowerPhaseA | REAL | IOD_ST2_TCP | 6963 | 46963 | PMM.VirBReactivePowerPhaseA
ST2PMMVirBReactivePowerPhaseB | REAL | IOD_ST2_TCP | 6965 | 46965 | PMM.VirBReactivePowerPhaseB
ST2PMMVirBReactivePowerPhaseC | REAL | IOD_ST2_TCP | 6967 | 46967 | PMM.VirBReactivePowerPhaseC
ST2PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_ST2_TCP | 6969 | 46969 | PMM.VirBVoltageBetweenPhaseAB_V
ST2PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_ST2_TCP | 6971 | 46971 | PMM.VirBVoltageBetweenPhaseAN_V
ST2PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_ST2_TCP | 6973 | 46973 | PMM.VirBVoltageBetweenPhaseBC_V
ST2PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_ST2_TCP | 6975 | 46975 | PMM.VirBVoltageBetweenPhaseBN_V
ST2PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_ST2_TCP | 6977 | 46977 | PMM.VirBVoltageBetweenPhaseCA_V
ST2PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_ST2_TCP | 6979 | 46979 | PMM.VirBVoltageBetweenPhaseCN_V
ST2Date_Time0 | STRING | IOD_ST2_TCP | 7001 | 47001[15] | Date_Time[0]
ST2Date_Time1 | STRING | IOD_ST2_TCP | 7016 | 47016[15] | Date_Time[1]
ST2Date_Time2 | STRING | IOD_ST2_TCP | 7031 | 47031[15] | Date_Time[2]
ST2Date_Time3 | STRING | IOD_ST2_TCP | 7046 | 47046[15] | Date_Time[3]
ST2kom_nast_cas_izpada | STRING | IOD_ST2_TCP | 7061 | 47061[15] | kom_nast_cas_izpada
ST2UserCurrentName | STRING | IOD_ST2_TCP | 7076 | 47076[15] | UserCurrentName
ST2UserDisplay | STRING | IOD_ST2_TCP | 7091 | 47091[15] | UserDisplay
ST2NSX1StatusSwitch | UINT | IOD_ST2_TCP | 8001 | 48001 | NSX[1].StatusSwitch
ST2NSX2StatusSwitch | UINT | IOD_ST2_TCP | 8002 | 48002 | NSX[2].StatusSwitch
ST2NSX3StatusSwitch | UINT | IOD_ST2_TCP | 8003 | 48003 | NSX[3].StatusSwitch
ST2NSX4StatusSwitch | UINT | IOD_ST2_TCP | 8004 | 48004 | NSX[4].StatusSwitch
ST2NSX5StatusSwitch | UINT | IOD_ST2_TCP | 8005 | 48005 | NSX[5].StatusSwitch
ST2NSX6StatusSwitch | UINT | IOD_ST2_TCP | 8006 | 48006 | NSX[6].StatusSwitch
ST2PMMVirAAlarmPhase_C01_16_60to80 | UINT | IOD_ST2_TCP | 8007 | 48007 | PMM.VirAAlarmPhase.C01_16_60to80
ST2PMMVirAAlarmPhase_C01_16_over80 | UINT | IOD_ST2_TCP | 8008 | 48008 | PMM.VirAAlarmPhase.C01_16_over80
ST2PMMVirAAlarmPhase_C17_32_60to80 | UINT | IOD_ST2_TCP | 8009 | 48009 | PMM.VirAAlarmPhase.C17_32_60to80
ST2PMMVirAAlarmPhase_C17_32_over80 | UINT | IOD_ST2_TCP | 8010 | 48010 | PMM.VirAAlarmPhase.C17_32_over80
ST2PMMVirAAlarmPhase_C33_44_60to80 | UINT | IOD_ST2_TCP | 8011 | 48011 | PMM.VirAAlarmPhase.C33_44_60to80
ST2PMMVirAAlarmPhase_C33_44_over80 | UINT | IOD_ST2_TCP | 8012 | 48012 | PMM.VirAAlarmPhase.C33_44_over80
ST2PMMVirBAlarmPhase_C01_16_60to80 | UINT | IOD_ST2_TCP | 8013 | 48013 | PMM.VirBAlarmPhase.C01_16_60to80
ST2PMMVirBAlarmPhase_C01_16_over80 | UINT | IOD_ST2_TCP | 8014 | 48014 | PMM.VirBAlarmPhase.C01_16_over80
ST2PMMVirBAlarmPhase_C17_32_60to80 | UINT | IOD_ST2_TCP | 8015 | 48015 | PMM.VirBAlarmPhase.C17_32_60to80
ST2PMMVirBAlarmPhase_C17_32_over80 | UINT | IOD_ST2_TCP | 8016 | 48016 | PMM.VirBAlarmPhase.C17_32_over80
ST2PMMVirBAlarmPhase_C33_44_60to80 | UINT | IOD_ST2_TCP | 8017 | 48017 | PMM.VirBAlarmPhase.C33_44_60to80
ST2PMMVirBAlarmPhase_C33_44_over80 | UINT | IOD_ST2_TCP | 8018 | 48018 | PMM.VirBAlarmPhase.C33_44_over80

## variable_new
ST2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_ST2_TCP | 00001
ST2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_ST2_TCP | 00002
ST2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_ST2_TCP | 00003
ST2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_ST2_TCP | 00004
ST2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_ST2_TCP | 00005
ST2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_ST2_TCP | 00006
ST2ComError | DIGITAL | IOD_ST2_TCP | 00007
ST2ComSCADA | DIGITAL | IOD_ST2_TCP | 00008
ST2ComSCADA1 | DIGITAL | IOD_ST2_TCP | 00009
ST2ComSCADA2 | DIGITAL | IOD_ST2_TCP | 00010
ST2ComSCADA3 | DIGITAL | IOD_ST2_TCP | 00011
ST2Date_Time0 | STRING | IOD_ST2_TCP | 47001[15]
ST2Date_Time1 | STRING | IOD_ST2_TCP | 47016[15]
ST2Date_Time2 | STRING | IOD_ST2_TCP | 47031[15]
ST2Date_Time3 | STRING | IOD_ST2_TCP | 47046[15]
ST2DateTimeDan | INT | IOD_ST2_TCP | 40001
ST2DateTimeLeto | INT | IOD_ST2_TCP | 40002
ST2DateTimeLeto2 | INT | IOD_ST2_TCP | 40003
ST2DateTimeMesec | INT | IOD_ST2_TCP | 40004
ST2DateTimeMinuta | INT | IOD_ST2_TCP | 40005
ST2DateTimePLC_Dan | INT | IOD_ST2_TCP | 40006
ST2DateTimePLC_DanVTednu | INT | IOD_ST2_TCP | 40007
ST2DateTimePLC_Leto | INT | IOD_ST2_TCP | 40008
ST2DateTimePLC_Mesec | INT | IOD_ST2_TCP | 40009
ST2DateTimePLC_Minuta | INT | IOD_ST2_TCP | 40010
ST2DateTimePLC_Sekunda | INT | IOD_ST2_TCP | 40011
ST2DateTimePLC_Ura | INT | IOD_ST2_TCP | 40012
ST2DateTimeSekunda | INT | IOD_ST2_TCP | 40013
ST2DateTimeUra | INT | IOD_ST2_TCP | 40014
ST2DI2_I10_Rezerva3 | DIGITAL | IOD_ST2_TCP | 00012
ST2DI2_I11_Rezerva4 | DIGITAL | IOD_ST2_TCP | 00013
ST2DI2_I12_Rezerva5 | DIGITAL | IOD_ST2_TCP | 00014
ST2DI2_I13_Rezerva6 | DIGITAL | IOD_ST2_TCP | 00015
ST2DI2_I8_Rezerva1 | DIGITAL | IOD_ST2_TCP | 00016
ST2DI2_I9_Rezerva2 | DIGITAL | IOD_ST2_TCP | 00017
ST2DI_SB_IROGSM21_Q0_Izkljucen | DIGITAL | IOD_ST2_TCP | 00018
ST2DI_SB_IROGSM21_Q0_Vkljucen | DIGITAL | IOD_ST2_TCP | 00019
ST2DI_SB_IROGSM21_Q11_Izkljucen | DIGITAL | IOD_ST2_TCP | 00020
ST2DI_SB_IROGSM21_Q11_Vkljucen | DIGITAL | IOD_ST2_TCP | 00021
ST2DI_SB_IROGSM21_Q12_Izkljucen | DIGITAL | IOD_ST2_TCP | 00022
ST2DI_SB_IROGSM21_Q12_Vkljucen | DIGITAL | IOD_ST2_TCP | 00023
ST2DI_SB_IROGSM21_Q13_Izpad | DIGITAL | IOD_ST2_TCP | 00024
ST2DI_SB_IROGSM21_Q13_Vkljucen | DIGITAL | IOD_ST2_TCP | 00025
ST2DI_SB_IROGSM21_Q14_Izpad | DIGITAL | IOD_ST2_TCP | 00026
ST2DI_SB_IROGSM21_Q14_Vkljucen | DIGITAL | IOD_ST2_TCP | 00027
ST2DI_SB_IROGSM21_Q15_Izpad | DIGITAL | IOD_ST2_TCP | 00028
ST2DI_SB_IROGSM21_Q15_Vkljucen | DIGITAL | IOD_ST2_TCP | 00029
ST2DI_SB_IROGSM21_SkupnaNapaka | DIGITAL | IOD_ST2_TCP | 00030
ST2DI_SB_IROGSM22_Q0_Izkljucen | DIGITAL | IOD_ST2_TCP | 00031
ST2DI_SB_IROGSM22_Q0_Vkljucen | DIGITAL | IOD_ST2_TCP | 00032
ST2DI_SB_IROGSM22_Q11_Izkljucen | DIGITAL | IOD_ST2_TCP | 00033
ST2DI_SB_IROGSM22_Q11_Vkljucen | DIGITAL | IOD_ST2_TCP | 00034
ST2DI_SB_IROGSM22_Q12_Izkljucen | DIGITAL | IOD_ST2_TCP | 00035
ST2DI_SB_IROGSM22_Q12_Vkljucen | DIGITAL | IOD_ST2_TCP | 00036
ST2DI_SB_IROGSM22_Q13_Izpad | DIGITAL | IOD_ST2_TCP | 00037
ST2DI_SB_IROGSM22_Q13_Vkljucen | DIGITAL | IOD_ST2_TCP | 00038
ST2DI_SB_IROGSM22_Q14_Izpad | DIGITAL | IOD_ST2_TCP | 00039
ST2DI_SB_IROGSM22_Q14_Vkljucen | DIGITAL | IOD_ST2_TCP | 00040
ST2DI_SB_IROGSM22_Q15_Izpad | DIGITAL | IOD_ST2_TCP | 00041
ST2DI_SB_IROGSM22_Q15_Vkljucen | DIGITAL | IOD_ST2_TCP | 00042
ST2DI_SB_IROGSM22_SkupnaNapaka | DIGITAL | IOD_ST2_TCP | 00043
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_ST2_TCP | 00044
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_ST2_TCP | 00045
ST2ErrComNSX1 | DIGITAL | IOD_ST2_TCP | 00046
ST2ErrComNSX2 | DIGITAL | IOD_ST2_TCP | 00047
ST2ErrComNSX3 | DIGITAL | IOD_ST2_TCP | 00048
ST2ErrComNSX4 | DIGITAL | IOD_ST2_TCP | 00049
ST2ErrComNSX5 | DIGITAL | IOD_ST2_TCP | 00050
ST2ErrComNSX6 | DIGITAL | IOD_ST2_TCP | 00051
ST2ErrComPMM1 | DIGITAL | IOD_ST2_TCP | 00052
ST2ErrComPort2 | DIGITAL | IOD_ST2_TCP | 00053
ST2ErrorComPMM1Error | DIGITAL | IOD_ST2_TCP | 00054
ST2ErrorComPMM1Status | INT | IOD_ST2_TCP | 40015
ST2HIA1_vlaga_s | INT | IOD_ST2_TCP | 40016
ST2HIA2_vlaga_s | INT | IOD_ST2_TCP | 40017
ST2HIA3_vlaga_s | INT | IOD_ST2_TCP | 40018
ST2HIA4_vlaga_s | INT | IOD_ST2_TCP | 40019
ST2HIA5_vlaga_s | INT | IOD_ST2_TCP | 40020
ST2HIA6_vlaga_s | INT | IOD_ST2_TCP | 40021
ST2HIA7_vlaga_s | INT | IOD_ST2_TCP | 40022
ST2HIA8_vlaga_s | INT | IOD_ST2_TCP | 40023
ST2iPMM_VirA_Tok1 | REAL | IOD_ST2_TCP | 44001
ST2iPMM_VirA_Tok10 | REAL | IOD_ST2_TCP | 44003
ST2iPMM_VirA_Tok11 | REAL | IOD_ST2_TCP | 44005
ST2iPMM_VirA_Tok12 | REAL | IOD_ST2_TCP | 44007
ST2iPMM_VirA_Tok13 | REAL | IOD_ST2_TCP | 44009
ST2iPMM_VirA_Tok14 | REAL | IOD_ST2_TCP | 44011
ST2iPMM_VirA_Tok15 | REAL | IOD_ST2_TCP | 44013
ST2iPMM_VirA_Tok16 | REAL | IOD_ST2_TCP | 44015
ST2iPMM_VirA_Tok17 | REAL | IOD_ST2_TCP | 44017
ST2iPMM_VirA_Tok18 | REAL | IOD_ST2_TCP | 44019
ST2iPMM_VirA_Tok19 | REAL | IOD_ST2_TCP | 44021
ST2iPMM_VirA_Tok2 | REAL | IOD_ST2_TCP | 44023
ST2iPMM_VirA_Tok20 | REAL | IOD_ST2_TCP | 44025
ST2iPMM_VirA_Tok21 | REAL | IOD_ST2_TCP | 44027
ST2iPMM_VirA_Tok22 | REAL | IOD_ST2_TCP | 44029
ST2iPMM_VirA_Tok23 | REAL | IOD_ST2_TCP | 44031
ST2iPMM_VirA_Tok24 | REAL | IOD_ST2_TCP | 44033
ST2iPMM_VirA_Tok25 | REAL | IOD_ST2_TCP | 44035
ST2iPMM_VirA_Tok26 | REAL | IOD_ST2_TCP | 44037
ST2iPMM_VirA_Tok27 | REAL | IOD_ST2_TCP | 44039
ST2iPMM_VirA_Tok28 | REAL | IOD_ST2_TCP | 44041
ST2iPMM_VirA_Tok29 | REAL | IOD_ST2_TCP | 44043
ST2iPMM_VirA_Tok3 | REAL | IOD_ST2_TCP | 44045
ST2iPMM_VirA_Tok30 | REAL | IOD_ST2_TCP | 44047
ST2iPMM_VirA_Tok31 | REAL | IOD_ST2_TCP | 44049
ST2iPMM_VirA_Tok32 | REAL | IOD_ST2_TCP | 44051
ST2iPMM_VirA_Tok33 | REAL | IOD_ST2_TCP | 44053
ST2iPMM_VirA_Tok34 | REAL | IOD_ST2_TCP | 44055
ST2iPMM_VirA_Tok35 | REAL | IOD_ST2_TCP | 44057
ST2iPMM_VirA_Tok36 | REAL | IOD_ST2_TCP | 44059
ST2iPMM_VirA_Tok37 | REAL | IOD_ST2_TCP | 44061
ST2iPMM_VirA_Tok38 | REAL | IOD_ST2_TCP | 44063
ST2iPMM_VirA_Tok39 | REAL | IOD_ST2_TCP | 44065
ST2iPMM_VirA_Tok4 | REAL | IOD_ST2_TCP | 44067
ST2iPMM_VirA_Tok40 | REAL | IOD_ST2_TCP | 44069
ST2iPMM_VirA_Tok41 | REAL | IOD_ST2_TCP | 44071
ST2iPMM_VirA_Tok42 | REAL | IOD_ST2_TCP | 44073
ST2iPMM_VirA_Tok43 | REAL | IOD_ST2_TCP | 44075
ST2iPMM_VirA_Tok44 | REAL | IOD_ST2_TCP | 44077
ST2iPMM_VirA_Tok5 | REAL | IOD_ST2_TCP | 44079
ST2iPMM_VirA_Tok6 | REAL | IOD_ST2_TCP | 44081
ST2iPMM_VirA_Tok7 | REAL | IOD_ST2_TCP | 44083
ST2iPMM_VirA_Tok8 | REAL | IOD_ST2_TCP | 44085
ST2iPMM_VirA_Tok9 | REAL | IOD_ST2_TCP | 44087
ST2iPMM_VirB_Tok1 | REAL | IOD_ST2_TCP | 44089
ST2iPMM_VirB_Tok10 | REAL | IOD_ST2_TCP | 44091
ST2iPMM_VirB_Tok11 | REAL | IOD_ST2_TCP | 44093
ST2iPMM_VirB_Tok12 | REAL | IOD_ST2_TCP | 44095
ST2iPMM_VirB_Tok13 | REAL | IOD_ST2_TCP | 44097
ST2iPMM_VirB_Tok14 | REAL | IOD_ST2_TCP | 44099
ST2iPMM_VirB_Tok15 | REAL | IOD_ST2_TCP | 44101
ST2iPMM_VirB_Tok16 | REAL | IOD_ST2_TCP | 44103
ST2iPMM_VirB_Tok17 | REAL | IOD_ST2_TCP | 44105
ST2iPMM_VirB_Tok18 | REAL | IOD_ST2_TCP | 44107
ST2iPMM_VirB_Tok19 | REAL | IOD_ST2_TCP | 44109
ST2iPMM_VirB_Tok2 | REAL | IOD_ST2_TCP | 44111
ST2iPMM_VirB_Tok20 | REAL | IOD_ST2_TCP | 44113
ST2iPMM_VirB_Tok21 | REAL | IOD_ST2_TCP | 44115
ST2iPMM_VirB_Tok22 | REAL | IOD_ST2_TCP | 44117
ST2iPMM_VirB_Tok23 | REAL | IOD_ST2_TCP | 44119
ST2iPMM_VirB_Tok24 | REAL | IOD_ST2_TCP | 44121
ST2iPMM_VirB_Tok25 | REAL | IOD_ST2_TCP | 44123
ST2iPMM_VirB_Tok26 | REAL | IOD_ST2_TCP | 44125
ST2iPMM_VirB_Tok27 | REAL | IOD_ST2_TCP | 44127
ST2iPMM_VirB_Tok28 | REAL | IOD_ST2_TCP | 44129
ST2iPMM_VirB_Tok29 | REAL | IOD_ST2_TCP | 44131
ST2iPMM_VirB_Tok3 | REAL | IOD_ST2_TCP | 44133
ST2iPMM_VirB_Tok30 | REAL | IOD_ST2_TCP | 44135
ST2iPMM_VirB_Tok31 | REAL | IOD_ST2_TCP | 44137
ST2iPMM_VirB_Tok32 | REAL | IOD_ST2_TCP | 44139
ST2iPMM_VirB_Tok33 | REAL | IOD_ST2_TCP | 44141
ST2iPMM_VirB_Tok34 | REAL | IOD_ST2_TCP | 44143
ST2iPMM_VirB_Tok35 | REAL | IOD_ST2_TCP | 44145
ST2iPMM_VirB_Tok36 | REAL | IOD_ST2_TCP | 44147
ST2iPMM_VirB_Tok37 | REAL | IOD_ST2_TCP | 44149
ST2iPMM_VirB_Tok38 | REAL | IOD_ST2_TCP | 44151
ST2iPMM_VirB_Tok39 | REAL | IOD_ST2_TCP | 44153
ST2iPMM_VirB_Tok4 | REAL | IOD_ST2_TCP | 44155
ST2iPMM_VirB_Tok40 | REAL | IOD_ST2_TCP | 44157
ST2iPMM_VirB_Tok41 | REAL | IOD_ST2_TCP | 44159
ST2iPMM_VirB_Tok42 | REAL | IOD_ST2_TCP | 44161
ST2iPMM_VirB_Tok43 | REAL | IOD_ST2_TCP | 44163
ST2iPMM_VirB_Tok44 | REAL | IOD_ST2_TCP | 44165
ST2iPMM_VirB_Tok5 | REAL | IOD_ST2_TCP | 44167
ST2iPMM_VirB_Tok6 | REAL | IOD_ST2_TCP | 44169
ST2iPMM_VirB_Tok7 | REAL | IOD_ST2_TCP | 44171
ST2iPMM_VirB_Tok8 | REAL | IOD_ST2_TCP | 44173
ST2iPMM_VirB_Tok9 | REAL | IOD_ST2_TCP | 44175
ST2kom_nast_cas_izpada | STRING | IOD_ST2_TCP | 47061[15]
ST2napaka_kom_panel | DIGITAL | IOD_ST2_TCP | 00055
ST2napaka_kom_scada | DIGITAL | IOD_ST2_TCP | 00056
ST2napaka_kom_scada2 | DIGITAL | IOD_ST2_TCP | 00057
ST2NapakaSenzorSkupno | DIGITAL | IOD_ST2_TCP | 00058
ST2NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST2_TCP | 00059
ST2NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST2_TCP | 00060
ST2NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST2_TCP | 00061
ST2NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST2_TCP | 00062
ST2NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST2_TCP | 00063
ST2NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST2_TCP | 00064
ST2NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST2_TCP | 00065
ST2NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST2_TCP | 00066
ST2NapakaTSTempTIA1 | DIGITAL | IOD_ST2_TCP | 00067
ST2NapakaTSTempTIA2 | DIGITAL | IOD_ST2_TCP | 00068
ST2NapakaTSTempTIA3 | DIGITAL | IOD_ST2_TCP | 00069
ST2NapakaTSTempTIA4 | DIGITAL | IOD_ST2_TCP | 00070
ST2NapakaTSTempTIA5 | DIGITAL | IOD_ST2_TCP | 00071
ST2NapakaTSTempTIA6 | DIGITAL | IOD_ST2_TCP | 00072
ST2NapakaTSTempTIA7 | DIGITAL | IOD_ST2_TCP | 00073
ST2NapakaTSTempTIA8 | DIGITAL | IOD_ST2_TCP | 00074
ST2NSX1ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44177
ST2NSX1ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 44179
ST2NSX1ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 44181
ST2NSX1ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 44183
ST2NSX1ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44185
ST2NSX1ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44187
ST2NSX1ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44189
ST2NSX1ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 44191
ST2NSX1ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44193
ST2NSX1ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 44195
ST2NSX1ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 44197
ST2NSX1ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 44199
ST2NSX1ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44201
ST2NSX1ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44203
ST2NSX1ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44205
ST2NSX1ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44207
ST2NSX1CosFL1 | REAL | IOD_ST2_TCP | 44209
ST2NSX1CosFL2 | REAL | IOD_ST2_TCP | 44211
ST2NSX1CosFL3 | REAL | IOD_ST2_TCP | 44213
ST2NSX1CosFTotal | REAL | IOD_ST2_TCP | 44215
ST2NSX1CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44217
ST2NSX1CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44219
ST2NSX1CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44221
ST2NSX1CurrentDemandL1_A | REAL | IOD_ST2_TCP | 44223
ST2NSX1CurrentDemandL2_A | REAL | IOD_ST2_TCP | 44225
ST2NSX1CurrentDemandL3_A | REAL | IOD_ST2_TCP | 44227
ST2NSX1CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 44229
ST2NSX1CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 44231
ST2NSX1CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 44233
ST2NSX1CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 44235
ST2NSX1CurrentDemandN_A | REAL | IOD_ST2_TCP | 44237
ST2NSX1CurrentL1_A | REAL | IOD_ST2_TCP | 44239
ST2NSX1CurrentL2_A | REAL | IOD_ST2_TCP | 44241
ST2NSX1CurrentL3_A | REAL | IOD_ST2_TCP | 44243
ST2NSX1CurrentN_A | REAL | IOD_ST2_TCP | 44245
ST2NSX1CurrentUnbI1_P | REAL | IOD_ST2_TCP | 44247
ST2NSX1CurrentUnbI2_P | REAL | IOD_ST2_TCP | 44249
ST2NSX1CurrentUnbI3_P | REAL | IOD_ST2_TCP | 44251
ST2NSX1CurrentUnbN_P | REAL | IOD_ST2_TCP | 44253
ST2NSX1DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 44255
ST2NSX1DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44257
ST2NSX1DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44259
ST2NSX1DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44261
ST2NSX1DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44263
ST2NSX1Frequency_Hz | REAL | IOD_ST2_TCP | 44265
ST2NSX1FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44267
ST2NSX1FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44269
ST2NSX1FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44271
ST2NSX1FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44273
ST2NSX1MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44275
ST2NSX1MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44277
ST2NSX1MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44279
ST2NSX1MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44281
ST2NSX1MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44283
ST2NSX1MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44285
ST2NSX1MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44287
ST2NSX1MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44289
ST2NSX1MAX_CosFL1 | REAL | IOD_ST2_TCP | 44291
ST2NSX1MAX_CosFL2 | REAL | IOD_ST2_TCP | 44293
ST2NSX1MAX_CosFL3 | REAL | IOD_ST2_TCP | 44295
ST2NSX1MAX_CosFTotal | REAL | IOD_ST2_TCP | 44297
ST2NSX1MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44299
ST2NSX1MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 44301
ST2NSX1MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 44303
ST2NSX1MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 44305
ST2NSX1MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 44307
ST2NSX1MAX_CurrentN_A | REAL | IOD_ST2_TCP | 44309
ST2NSX1MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44311
ST2NSX1MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44313
ST2NSX1MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44315
ST2NSX1MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44317
ST2NSX1MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 44319
ST2NSX1MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44321
ST2NSX1MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44323
ST2NSX1MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44325
ST2NSX1MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44327
ST2NSX1MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 44329
ST2NSX1MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 44331
ST2NSX1MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 44333
ST2NSX1MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 44335
ST2NSX1MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44337
ST2NSX1MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44339
ST2NSX1MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44341
ST2NSX1MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44343
ST2NSX1MAX_THDI1_P | REAL | IOD_ST2_TCP | 44345
ST2NSX1MAX_THDI2_P | REAL | IOD_ST2_TCP | 44347
ST2NSX1MAX_THDI3_P | REAL | IOD_ST2_TCP | 44349
ST2NSX1MAX_THDV12_P | REAL | IOD_ST2_TCP | 44351
ST2NSX1MAX_THDV1N_P | REAL | IOD_ST2_TCP | 44353
ST2NSX1MAX_THDV23_P | REAL | IOD_ST2_TCP | 44355
ST2NSX1MAX_THDV2N_P | REAL | IOD_ST2_TCP | 44357
ST2NSX1MAX_THDV31_P | REAL | IOD_ST2_TCP | 44359
ST2NSX1MAX_THDV3N_P | REAL | IOD_ST2_TCP | 44361
ST2NSX1MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44363
ST2NSX1MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44365
ST2NSX1MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44367
ST2NSX1MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44369
ST2NSX1MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44371
ST2NSX1MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44373
ST2NSX1MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 44375
ST2NSX1MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 44377
ST2NSX1MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 44379
ST2NSX1MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 44381
ST2NSX1MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 44383
ST2NSX1MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 44385
ST2NSX1MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 44387
ST2NSX1MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 44389
ST2NSX1MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44391
ST2NSX1MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44393
ST2NSX1MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44395
ST2NSX1MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44397
ST2NSX1MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44399
ST2NSX1MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44401
ST2NSX1MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44403
ST2NSX1MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44405
ST2NSX1MIN_CosFL1 | REAL | IOD_ST2_TCP | 44407
ST2NSX1MIN_CosFL2 | REAL | IOD_ST2_TCP | 44409
ST2NSX1MIN_CosFL3 | REAL | IOD_ST2_TCP | 44411
ST2NSX1MIN_CosFTotal | REAL | IOD_ST2_TCP | 44413
ST2NSX1MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44415
ST2NSX1MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 44417
ST2NSX1MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 44419
ST2NSX1MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 44421
ST2NSX1MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 44423
ST2NSX1MIN_CurrentN_A | REAL | IOD_ST2_TCP | 44425
ST2NSX1MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44427
ST2NSX1MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44429
ST2NSX1MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44431
ST2NSX1MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44433
ST2NSX1MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 44435
ST2NSX1MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44437
ST2NSX1MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44439
ST2NSX1MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44441
ST2NSX1MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44443
ST2NSX1MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 44445
ST2NSX1MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 44447
ST2NSX1MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 44449
ST2NSX1MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 44451
ST2NSX1MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44453
ST2NSX1MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44455
ST2NSX1MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44457
ST2NSX1MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44459
ST2NSX1MIN_THDI1_P | REAL | IOD_ST2_TCP | 44461
ST2NSX1MIN_THDI2_P | REAL | IOD_ST2_TCP | 44463
ST2NSX1MIN_THDI3_P | REAL | IOD_ST2_TCP | 44465
ST2NSX1MIN_THDV12_P | REAL | IOD_ST2_TCP | 44467
ST2NSX1MIN_THDV1N_P | REAL | IOD_ST2_TCP | 44469
ST2NSX1MIN_THDV23_P | REAL | IOD_ST2_TCP | 44471
ST2NSX1MIN_THDV2N_P | REAL | IOD_ST2_TCP | 44473
ST2NSX1MIN_THDV31_P | REAL | IOD_ST2_TCP | 44475
ST2NSX1MIN_THDV3N_P | REAL | IOD_ST2_TCP | 44477
ST2NSX1MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44479
ST2NSX1MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44481
ST2NSX1MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44483
ST2NSX1MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44485
ST2NSX1MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44487
ST2NSX1MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44489
ST2NSX1MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 44491
ST2NSX1MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 44493
ST2NSX1MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 44495
ST2NSX1MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 44497
ST2NSX1MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 44499
ST2NSX1MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 44501
ST2NSX1MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 44503
ST2NSX1MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 44505
ST2NSX1PowerFactorL1 | REAL | IOD_ST2_TCP | 44507
ST2NSX1PowerFactorL2 | REAL | IOD_ST2_TCP | 44509
ST2NSX1PowerFactorL3 | REAL | IOD_ST2_TCP | 44511
ST2NSX1PowerFactorTotal | REAL | IOD_ST2_TCP | 44513
ST2NSX1RazEner_D | REAL | IOD_ST2_TCP | 44515
ST2NSX1RazEner_D_SCADA | REAL | IOD_ST2_TCP | 44517
ST2NSX1RazEner_D_TEMP | REAL | IOD_ST2_TCP | 44519
ST2NSX1RazEner_M | REAL | IOD_ST2_TCP | 44521
ST2NSX1RazEner_M_SCADA | REAL | IOD_ST2_TCP | 44523
ST2NSX1RazEner_M_TEMP | REAL | IOD_ST2_TCP | 44525
ST2NSX1RazEner_T | REAL | IOD_ST2_TCP | 44527
ST2NSX1RazEner_T_SCADA | REAL | IOD_ST2_TCP | 44529
ST2NSX1RazEner_T_TEMP | REAL | IOD_ST2_TCP | 44531
ST2NSX1ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 44533
ST2NSX1ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 44535
ST2NSX1ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 44537
ST2NSX1ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 44539
ST2NSX1ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44541
ST2NSX1ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44543
ST2NSX1ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44545
ST2NSX1ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 44547
ST2NSX1ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44549
ST2NSX1ResetMAX | DIGITAL | IOD_ST2_TCP | 00075
ST2NSX1ResetMIN | DIGITAL | IOD_ST2_TCP | 00076
ST2NSX1StatusSwitch | UINT | IOD_ST2_TCP | 48001
ST2NSX1THDI1_P | REAL | IOD_ST2_TCP | 44551
ST2NSX1THDI2_P | REAL | IOD_ST2_TCP | 44553
ST2NSX1THDI3_P | REAL | IOD_ST2_TCP | 44555
ST2NSX1THDV12_P | REAL | IOD_ST2_TCP | 44557
ST2NSX1THDV1N_P | REAL | IOD_ST2_TCP | 44559
ST2NSX1THDV23_P | REAL | IOD_ST2_TCP | 44561
ST2NSX1THDV2N_P | REAL | IOD_ST2_TCP | 44563
ST2NSX1THDV31_P | REAL | IOD_ST2_TCP | 44565
ST2NSX1THDV3N_P | REAL | IOD_ST2_TCP | 44567
ST2NSX1VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44569
ST2NSX1VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44571
ST2NSX1VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44573
ST2NSX1VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44575
ST2NSX1VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44577
ST2NSX1VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44579
ST2NSX1VoltageUnbV31_P | REAL | IOD_ST2_TCP | 44581
ST2NSX1VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 44583
ST2NSX1VoltageV12_V | REAL | IOD_ST2_TCP | 44585
ST2NSX1VoltageV1N_V | REAL | IOD_ST2_TCP | 44587
ST2NSX1VoltageV23_V | REAL | IOD_ST2_TCP | 44589
ST2NSX1VoltageV2N_V | REAL | IOD_ST2_TCP | 44591
ST2NSX1VoltageV31_V | REAL | IOD_ST2_TCP | 44593
ST2NSX1VoltageV3N_V | REAL | IOD_ST2_TCP | 44595
ST2NSX2ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44597
ST2NSX2ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 44599
ST2NSX2ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 44601
ST2NSX2ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 44603
ST2NSX2ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44605
ST2NSX2ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44607
ST2NSX2ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44609
ST2NSX2ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 44611
ST2NSX2ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44613
ST2NSX2ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 44615
ST2NSX2ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 44617
ST2NSX2ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 44619
ST2NSX2ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44621
ST2NSX2ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44623
ST2NSX2ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44625
ST2NSX2ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44627
ST2NSX2CosFL1 | REAL | IOD_ST2_TCP | 44629
ST2NSX2CosFL2 | REAL | IOD_ST2_TCP | 44631
ST2NSX2CosFL3 | REAL | IOD_ST2_TCP | 44633
ST2NSX2CosFTotal | REAL | IOD_ST2_TCP | 44635
ST2NSX2CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44637
ST2NSX2CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 44639
ST2NSX2CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44641
ST2NSX2CurrentDemandL1_A | REAL | IOD_ST2_TCP | 44643
ST2NSX2CurrentDemandL2_A | REAL | IOD_ST2_TCP | 44645
ST2NSX2CurrentDemandL3_A | REAL | IOD_ST2_TCP | 44647
ST2NSX2CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 44649
ST2NSX2CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 44651
ST2NSX2CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 44653
ST2NSX2CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 44655
ST2NSX2CurrentDemandN_A | REAL | IOD_ST2_TCP | 44657
ST2NSX2CurrentL1_A | REAL | IOD_ST2_TCP | 44659
ST2NSX2CurrentL2_A | REAL | IOD_ST2_TCP | 44661
ST2NSX2CurrentL3_A | REAL | IOD_ST2_TCP | 44663
ST2NSX2CurrentN_A | REAL | IOD_ST2_TCP | 44665
ST2NSX2CurrentUnbI1_P | REAL | IOD_ST2_TCP | 44667
ST2NSX2CurrentUnbI2_P | REAL | IOD_ST2_TCP | 44669
ST2NSX2CurrentUnbI3_P | REAL | IOD_ST2_TCP | 44671
ST2NSX2CurrentUnbN_P | REAL | IOD_ST2_TCP | 44673
ST2NSX2DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 44675
ST2NSX2DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44677
ST2NSX2DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44679
ST2NSX2DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44681
ST2NSX2DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44683
ST2NSX2Frequency_Hz | REAL | IOD_ST2_TCP | 44685
ST2NSX2FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44687
ST2NSX2FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44689
ST2NSX2FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44691
ST2NSX2FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44693
ST2NSX2MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44695
ST2NSX2MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44697
ST2NSX2MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44699
ST2NSX2MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44701
ST2NSX2MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44703
ST2NSX2MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44705
ST2NSX2MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44707
ST2NSX2MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44709
ST2NSX2MAX_CosFL1 | REAL | IOD_ST2_TCP | 44711
ST2NSX2MAX_CosFL2 | REAL | IOD_ST2_TCP | 44713
ST2NSX2MAX_CosFL3 | REAL | IOD_ST2_TCP | 44715
ST2NSX2MAX_CosFTotal | REAL | IOD_ST2_TCP | 44717
ST2NSX2MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44719
ST2NSX2MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 44721
ST2NSX2MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 44723
ST2NSX2MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 44725
ST2NSX2MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 44727
ST2NSX2MAX_CurrentN_A | REAL | IOD_ST2_TCP | 44729
ST2NSX2MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44731
ST2NSX2MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44733
ST2NSX2MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44735
ST2NSX2MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44737
ST2NSX2MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 44739
ST2NSX2MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44741
ST2NSX2MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44743
ST2NSX2MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44745
ST2NSX2MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44747
ST2NSX2MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 44749
ST2NSX2MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 44751
ST2NSX2MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 44753
ST2NSX2MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 44755
ST2NSX2MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44757
ST2NSX2MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44759
ST2NSX2MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44761
ST2NSX2MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44763
ST2NSX2MAX_THDI1_P | REAL | IOD_ST2_TCP | 44765
ST2NSX2MAX_THDI2_P | REAL | IOD_ST2_TCP | 44767
ST2NSX2MAX_THDI3_P | REAL | IOD_ST2_TCP | 44769
ST2NSX2MAX_THDV12_P | REAL | IOD_ST2_TCP | 44771
ST2NSX2MAX_THDV1N_P | REAL | IOD_ST2_TCP | 44773
ST2NSX2MAX_THDV23_P | REAL | IOD_ST2_TCP | 44775
ST2NSX2MAX_THDV2N_P | REAL | IOD_ST2_TCP | 44777
ST2NSX2MAX_THDV31_P | REAL | IOD_ST2_TCP | 44779
ST2NSX2MAX_THDV3N_P | REAL | IOD_ST2_TCP | 44781
ST2NSX2MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44783
ST2NSX2MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44785
ST2NSX2MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44787
ST2NSX2MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44789
ST2NSX2MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44791
ST2NSX2MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44793
ST2NSX2MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 44795
ST2NSX2MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 44797
ST2NSX2MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 44799
ST2NSX2MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 44801
ST2NSX2MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 44803
ST2NSX2MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 44805
ST2NSX2MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 44807
ST2NSX2MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 44809
ST2NSX2MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 44811
ST2NSX2MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 44813
ST2NSX2MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 44815
ST2NSX2MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 44817
ST2NSX2MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 44819
ST2NSX2MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 44821
ST2NSX2MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 44823
ST2NSX2MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 44825
ST2NSX2MIN_CosFL1 | REAL | IOD_ST2_TCP | 44827
ST2NSX2MIN_CosFL2 | REAL | IOD_ST2_TCP | 44829
ST2NSX2MIN_CosFL3 | REAL | IOD_ST2_TCP | 44831
ST2NSX2MIN_CosFTotal | REAL | IOD_ST2_TCP | 44833
ST2NSX2MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 44835
ST2NSX2MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 44837
ST2NSX2MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 44839
ST2NSX2MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 44841
ST2NSX2MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 44843
ST2NSX2MIN_CurrentN_A | REAL | IOD_ST2_TCP | 44845
ST2NSX2MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 44847
ST2NSX2MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 44849
ST2NSX2MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 44851
ST2NSX2MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 44853
ST2NSX2MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 44855
ST2NSX2MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44857
ST2NSX2MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44859
ST2NSX2MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44861
ST2NSX2MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44863
ST2NSX2MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 44865
ST2NSX2MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 44867
ST2NSX2MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 44869
ST2NSX2MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 44871
ST2NSX2MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44873
ST2NSX2MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44875
ST2NSX2MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44877
ST2NSX2MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44879
ST2NSX2MIN_THDI1_P | REAL | IOD_ST2_TCP | 44881
ST2NSX2MIN_THDI2_P | REAL | IOD_ST2_TCP | 44883
ST2NSX2MIN_THDI3_P | REAL | IOD_ST2_TCP | 44885
ST2NSX2MIN_THDV12_P | REAL | IOD_ST2_TCP | 44887
ST2NSX2MIN_THDV1N_P | REAL | IOD_ST2_TCP | 44889
ST2NSX2MIN_THDV23_P | REAL | IOD_ST2_TCP | 44891
ST2NSX2MIN_THDV2N_P | REAL | IOD_ST2_TCP | 44893
ST2NSX2MIN_THDV31_P | REAL | IOD_ST2_TCP | 44895
ST2NSX2MIN_THDV3N_P | REAL | IOD_ST2_TCP | 44897
ST2NSX2MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44899
ST2NSX2MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44901
ST2NSX2MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44903
ST2NSX2MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44905
ST2NSX2MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44907
ST2NSX2MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44909
ST2NSX2MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 44911
ST2NSX2MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 44913
ST2NSX2MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 44915
ST2NSX2MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 44917
ST2NSX2MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 44919
ST2NSX2MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 44921
ST2NSX2MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 44923
ST2NSX2MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 44925
ST2NSX2PowerFactorL1 | REAL | IOD_ST2_TCP | 44927
ST2NSX2PowerFactorL2 | REAL | IOD_ST2_TCP | 44929
ST2NSX2PowerFactorL3 | REAL | IOD_ST2_TCP | 44931
ST2NSX2PowerFactorTotal | REAL | IOD_ST2_TCP | 44933
ST2NSX2RazEner_D | REAL | IOD_ST2_TCP | 44935
ST2NSX2RazEner_D_SCADA | REAL | IOD_ST2_TCP | 44937
ST2NSX2RazEner_D_TEMP | REAL | IOD_ST2_TCP | 44939
ST2NSX2RazEner_M | REAL | IOD_ST2_TCP | 44941
ST2NSX2RazEner_M_SCADA | REAL | IOD_ST2_TCP | 44943
ST2NSX2RazEner_M_TEMP | REAL | IOD_ST2_TCP | 44945
ST2NSX2RazEner_T | REAL | IOD_ST2_TCP | 44947
ST2NSX2RazEner_T_SCADA | REAL | IOD_ST2_TCP | 44949
ST2NSX2RazEner_T_TEMP | REAL | IOD_ST2_TCP | 44951
ST2NSX2ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 44953
ST2NSX2ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 44955
ST2NSX2ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 44957
ST2NSX2ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 44959
ST2NSX2ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 44961
ST2NSX2ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 44963
ST2NSX2ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 44965
ST2NSX2ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 44967
ST2NSX2ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 44969
ST2NSX2ResetMAX | DIGITAL | IOD_ST2_TCP | 00077
ST2NSX2ResetMIN | DIGITAL | IOD_ST2_TCP | 00078
ST2NSX2StatusSwitch | UINT | IOD_ST2_TCP | 48002
ST2NSX2THDI1_P | REAL | IOD_ST2_TCP | 44971
ST2NSX2THDI2_P | REAL | IOD_ST2_TCP | 44973
ST2NSX2THDI3_P | REAL | IOD_ST2_TCP | 44975
ST2NSX2THDV12_P | REAL | IOD_ST2_TCP | 44977
ST2NSX2THDV1N_P | REAL | IOD_ST2_TCP | 44979
ST2NSX2THDV23_P | REAL | IOD_ST2_TCP | 44981
ST2NSX2THDV2N_P | REAL | IOD_ST2_TCP | 44983
ST2NSX2THDV31_P | REAL | IOD_ST2_TCP | 44985
ST2NSX2THDV3N_P | REAL | IOD_ST2_TCP | 44987
ST2NSX2VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 44989
ST2NSX2VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 44991
ST2NSX2VoltageUnbV12_P | REAL | IOD_ST2_TCP | 44993
ST2NSX2VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 44995
ST2NSX2VoltageUnbV23_P | REAL | IOD_ST2_TCP | 44997
ST2NSX2VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 44999
ST2NSX2VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45001
ST2NSX2VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45003
ST2NSX2VoltageV12_V | REAL | IOD_ST2_TCP | 45005
ST2NSX2VoltageV1N_V | REAL | IOD_ST2_TCP | 45007
ST2NSX2VoltageV23_V | REAL | IOD_ST2_TCP | 45009
ST2NSX2VoltageV2N_V | REAL | IOD_ST2_TCP | 45011
ST2NSX2VoltageV31_V | REAL | IOD_ST2_TCP | 45013
ST2NSX2VoltageV3N_V | REAL | IOD_ST2_TCP | 45015
ST2NSX3ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45017
ST2NSX3ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 45019
ST2NSX3ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 45021
ST2NSX3ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 45023
ST2NSX3ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45025
ST2NSX3ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45027
ST2NSX3ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45029
ST2NSX3ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 45031
ST2NSX3ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45033
ST2NSX3ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 45035
ST2NSX3ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 45037
ST2NSX3ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 45039
ST2NSX3ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45041
ST2NSX3ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45043
ST2NSX3ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45045
ST2NSX3ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45047
ST2NSX3CosFL1 | REAL | IOD_ST2_TCP | 45049
ST2NSX3CosFL2 | REAL | IOD_ST2_TCP | 45051
ST2NSX3CosFL3 | REAL | IOD_ST2_TCP | 45053
ST2NSX3CosFTotal | REAL | IOD_ST2_TCP | 45055
ST2NSX3CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45057
ST2NSX3CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45059
ST2NSX3CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45061
ST2NSX3CurrentDemandL1_A | REAL | IOD_ST2_TCP | 45063
ST2NSX3CurrentDemandL2_A | REAL | IOD_ST2_TCP | 45065
ST2NSX3CurrentDemandL3_A | REAL | IOD_ST2_TCP | 45067
ST2NSX3CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 45069
ST2NSX3CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 45071
ST2NSX3CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 45073
ST2NSX3CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 45075
ST2NSX3CurrentDemandN_A | REAL | IOD_ST2_TCP | 45077
ST2NSX3CurrentL1_A | REAL | IOD_ST2_TCP | 45079
ST2NSX3CurrentL2_A | REAL | IOD_ST2_TCP | 45081
ST2NSX3CurrentL3_A | REAL | IOD_ST2_TCP | 45083
ST2NSX3CurrentN_A | REAL | IOD_ST2_TCP | 45085
ST2NSX3CurrentUnbI1_P | REAL | IOD_ST2_TCP | 45087
ST2NSX3CurrentUnbI2_P | REAL | IOD_ST2_TCP | 45089
ST2NSX3CurrentUnbI3_P | REAL | IOD_ST2_TCP | 45091
ST2NSX3CurrentUnbN_P | REAL | IOD_ST2_TCP | 45093
ST2NSX3DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 45095
ST2NSX3DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45097
ST2NSX3DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45099
ST2NSX3DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45101
ST2NSX3DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45103
ST2NSX3Frequency_Hz | REAL | IOD_ST2_TCP | 45105
ST2NSX3FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45107
ST2NSX3FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45109
ST2NSX3FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45111
ST2NSX3FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45113
ST2NSX3MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45115
ST2NSX3MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45117
ST2NSX3MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45119
ST2NSX3MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45121
ST2NSX3MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45123
ST2NSX3MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45125
ST2NSX3MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45127
ST2NSX3MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45129
ST2NSX3MAX_CosFL1 | REAL | IOD_ST2_TCP | 45131
ST2NSX3MAX_CosFL2 | REAL | IOD_ST2_TCP | 45133
ST2NSX3MAX_CosFL3 | REAL | IOD_ST2_TCP | 45135
ST2NSX3MAX_CosFTotal | REAL | IOD_ST2_TCP | 45137
ST2NSX3MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45139
ST2NSX3MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 45141
ST2NSX3MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 45143
ST2NSX3MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 45145
ST2NSX3MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 45147
ST2NSX3MAX_CurrentN_A | REAL | IOD_ST2_TCP | 45149
ST2NSX3MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45151
ST2NSX3MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45153
ST2NSX3MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45155
ST2NSX3MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45157
ST2NSX3MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 45159
ST2NSX3MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45161
ST2NSX3MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45163
ST2NSX3MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45165
ST2NSX3MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45167
ST2NSX3MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 45169
ST2NSX3MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 45171
ST2NSX3MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 45173
ST2NSX3MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 45175
ST2NSX3MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45177
ST2NSX3MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45179
ST2NSX3MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45181
ST2NSX3MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45183
ST2NSX3MAX_THDI1_P | REAL | IOD_ST2_TCP | 45185
ST2NSX3MAX_THDI2_P | REAL | IOD_ST2_TCP | 45187
ST2NSX3MAX_THDI3_P | REAL | IOD_ST2_TCP | 45189
ST2NSX3MAX_THDV12_P | REAL | IOD_ST2_TCP | 45191
ST2NSX3MAX_THDV1N_P | REAL | IOD_ST2_TCP | 45193
ST2NSX3MAX_THDV23_P | REAL | IOD_ST2_TCP | 45195
ST2NSX3MAX_THDV2N_P | REAL | IOD_ST2_TCP | 45197
ST2NSX3MAX_THDV31_P | REAL | IOD_ST2_TCP | 45199
ST2NSX3MAX_THDV3N_P | REAL | IOD_ST2_TCP | 45201
ST2NSX3MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45203
ST2NSX3MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45205
ST2NSX3MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45207
ST2NSX3MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45209
ST2NSX3MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45211
ST2NSX3MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45213
ST2NSX3MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45215
ST2NSX3MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45217
ST2NSX3MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 45219
ST2NSX3MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 45221
ST2NSX3MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 45223
ST2NSX3MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 45225
ST2NSX3MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 45227
ST2NSX3MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 45229
ST2NSX3MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45231
ST2NSX3MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45233
ST2NSX3MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45235
ST2NSX3MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45237
ST2NSX3MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45239
ST2NSX3MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45241
ST2NSX3MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45243
ST2NSX3MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45245
ST2NSX3MIN_CosFL1 | REAL | IOD_ST2_TCP | 45247
ST2NSX3MIN_CosFL2 | REAL | IOD_ST2_TCP | 45249
ST2NSX3MIN_CosFL3 | REAL | IOD_ST2_TCP | 45251
ST2NSX3MIN_CosFTotal | REAL | IOD_ST2_TCP | 45253
ST2NSX3MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45255
ST2NSX3MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 45257
ST2NSX3MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 45259
ST2NSX3MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 45261
ST2NSX3MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 45263
ST2NSX3MIN_CurrentN_A | REAL | IOD_ST2_TCP | 45265
ST2NSX3MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45267
ST2NSX3MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45269
ST2NSX3MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45271
ST2NSX3MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45273
ST2NSX3MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 45275
ST2NSX3MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45277
ST2NSX3MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45279
ST2NSX3MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45281
ST2NSX3MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45283
ST2NSX3MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 45285
ST2NSX3MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 45287
ST2NSX3MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 45289
ST2NSX3MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 45291
ST2NSX3MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45293
ST2NSX3MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45295
ST2NSX3MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45297
ST2NSX3MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45299
ST2NSX3MIN_THDI1_P | REAL | IOD_ST2_TCP | 45301
ST2NSX3MIN_THDI2_P | REAL | IOD_ST2_TCP | 45303
ST2NSX3MIN_THDI3_P | REAL | IOD_ST2_TCP | 45305
ST2NSX3MIN_THDV12_P | REAL | IOD_ST2_TCP | 45307
ST2NSX3MIN_THDV1N_P | REAL | IOD_ST2_TCP | 45309
ST2NSX3MIN_THDV23_P | REAL | IOD_ST2_TCP | 45311
ST2NSX3MIN_THDV2N_P | REAL | IOD_ST2_TCP | 45313
ST2NSX3MIN_THDV31_P | REAL | IOD_ST2_TCP | 45315
ST2NSX3MIN_THDV3N_P | REAL | IOD_ST2_TCP | 45317
ST2NSX3MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45319
ST2NSX3MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45321
ST2NSX3MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45323
ST2NSX3MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45325
ST2NSX3MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45327
ST2NSX3MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45329
ST2NSX3MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45331
ST2NSX3MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45333
ST2NSX3MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 45335
ST2NSX3MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 45337
ST2NSX3MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 45339
ST2NSX3MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 45341
ST2NSX3MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 45343
ST2NSX3MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 45345
ST2NSX3PowerFactorL1 | REAL | IOD_ST2_TCP | 45347
ST2NSX3PowerFactorL2 | REAL | IOD_ST2_TCP | 45349
ST2NSX3PowerFactorL3 | REAL | IOD_ST2_TCP | 45351
ST2NSX3PowerFactorTotal | REAL | IOD_ST2_TCP | 45353
ST2NSX3RazEner_D | REAL | IOD_ST2_TCP | 45355
ST2NSX3RazEner_D_SCADA | REAL | IOD_ST2_TCP | 45357
ST2NSX3RazEner_D_TEMP | REAL | IOD_ST2_TCP | 45359
ST2NSX3RazEner_M | REAL | IOD_ST2_TCP | 45361
ST2NSX3RazEner_M_SCADA | REAL | IOD_ST2_TCP | 45363
ST2NSX3RazEner_M_TEMP | REAL | IOD_ST2_TCP | 45365
ST2NSX3RazEner_T | REAL | IOD_ST2_TCP | 45367
ST2NSX3RazEner_T_SCADA | REAL | IOD_ST2_TCP | 45369
ST2NSX3RazEner_T_TEMP | REAL | IOD_ST2_TCP | 45371
ST2NSX3ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 45373
ST2NSX3ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 45375
ST2NSX3ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 45377
ST2NSX3ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 45379
ST2NSX3ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45381
ST2NSX3ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45383
ST2NSX3ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45385
ST2NSX3ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 45387
ST2NSX3ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45389
ST2NSX3ResetMAX | DIGITAL | IOD_ST2_TCP | 00079
ST2NSX3ResetMIN | DIGITAL | IOD_ST2_TCP | 00080
ST2NSX3StatusSwitch | UINT | IOD_ST2_TCP | 48003
ST2NSX3THDI1_P | REAL | IOD_ST2_TCP | 45391
ST2NSX3THDI2_P | REAL | IOD_ST2_TCP | 45393
ST2NSX3THDI3_P | REAL | IOD_ST2_TCP | 45395
ST2NSX3THDV12_P | REAL | IOD_ST2_TCP | 45397
ST2NSX3THDV1N_P | REAL | IOD_ST2_TCP | 45399
ST2NSX3THDV23_P | REAL | IOD_ST2_TCP | 45401
ST2NSX3THDV2N_P | REAL | IOD_ST2_TCP | 45403
ST2NSX3THDV31_P | REAL | IOD_ST2_TCP | 45405
ST2NSX3THDV3N_P | REAL | IOD_ST2_TCP | 45407
ST2NSX3VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45409
ST2NSX3VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45411
ST2NSX3VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45413
ST2NSX3VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45415
ST2NSX3VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45417
ST2NSX3VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45419
ST2NSX3VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45421
ST2NSX3VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45423
ST2NSX3VoltageV12_V | REAL | IOD_ST2_TCP | 45425
ST2NSX3VoltageV1N_V | REAL | IOD_ST2_TCP | 45427
ST2NSX3VoltageV23_V | REAL | IOD_ST2_TCP | 45429
ST2NSX3VoltageV2N_V | REAL | IOD_ST2_TCP | 45431
ST2NSX3VoltageV31_V | REAL | IOD_ST2_TCP | 45433
ST2NSX3VoltageV3N_V | REAL | IOD_ST2_TCP | 45435
ST2NSX4ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45437
ST2NSX4ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 45439
ST2NSX4ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 45441
ST2NSX4ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 45443
ST2NSX4ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45445
ST2NSX4ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45447
ST2NSX4ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45449
ST2NSX4ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 45451
ST2NSX4ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45453
ST2NSX4ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 45455
ST2NSX4ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 45457
ST2NSX4ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 45459
ST2NSX4ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45461
ST2NSX4ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45463
ST2NSX4ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45465
ST2NSX4ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45467
ST2NSX4CosFL1 | REAL | IOD_ST2_TCP | 45469
ST2NSX4CosFL2 | REAL | IOD_ST2_TCP | 45471
ST2NSX4CosFL3 | REAL | IOD_ST2_TCP | 45473
ST2NSX4CosFTotal | REAL | IOD_ST2_TCP | 45475
ST2NSX4CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45477
ST2NSX4CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45479
ST2NSX4CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45481
ST2NSX4CurrentDemandL1_A | REAL | IOD_ST2_TCP | 45483
ST2NSX4CurrentDemandL2_A | REAL | IOD_ST2_TCP | 45485
ST2NSX4CurrentDemandL3_A | REAL | IOD_ST2_TCP | 45487
ST2NSX4CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 45489
ST2NSX4CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 45491
ST2NSX4CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 45493
ST2NSX4CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 45495
ST2NSX4CurrentDemandN_A | REAL | IOD_ST2_TCP | 45497
ST2NSX4CurrentL1_A | REAL | IOD_ST2_TCP | 45499
ST2NSX4CurrentL2_A | REAL | IOD_ST2_TCP | 45501
ST2NSX4CurrentL3_A | REAL | IOD_ST2_TCP | 45503
ST2NSX4CurrentN_A | REAL | IOD_ST2_TCP | 45505
ST2NSX4CurrentUnbI1_P | REAL | IOD_ST2_TCP | 45507
ST2NSX4CurrentUnbI2_P | REAL | IOD_ST2_TCP | 45509
ST2NSX4CurrentUnbI3_P | REAL | IOD_ST2_TCP | 45511
ST2NSX4CurrentUnbN_P | REAL | IOD_ST2_TCP | 45513
ST2NSX4DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 45515
ST2NSX4DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45517
ST2NSX4DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45519
ST2NSX4DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45521
ST2NSX4DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45523
ST2NSX4Frequency_Hz | REAL | IOD_ST2_TCP | 45525
ST2NSX4FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45527
ST2NSX4FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45529
ST2NSX4FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45531
ST2NSX4FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45533
ST2NSX4MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45535
ST2NSX4MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45537
ST2NSX4MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45539
ST2NSX4MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45541
ST2NSX4MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45543
ST2NSX4MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45545
ST2NSX4MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45547
ST2NSX4MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45549
ST2NSX4MAX_CosFL1 | REAL | IOD_ST2_TCP | 45551
ST2NSX4MAX_CosFL2 | REAL | IOD_ST2_TCP | 45553
ST2NSX4MAX_CosFL3 | REAL | IOD_ST2_TCP | 45555
ST2NSX4MAX_CosFTotal | REAL | IOD_ST2_TCP | 45557
ST2NSX4MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45559
ST2NSX4MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 45561
ST2NSX4MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 45563
ST2NSX4MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 45565
ST2NSX4MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 45567
ST2NSX4MAX_CurrentN_A | REAL | IOD_ST2_TCP | 45569
ST2NSX4MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45571
ST2NSX4MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45573
ST2NSX4MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45575
ST2NSX4MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45577
ST2NSX4MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 45579
ST2NSX4MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45581
ST2NSX4MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45583
ST2NSX4MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45585
ST2NSX4MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45587
ST2NSX4MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 45589
ST2NSX4MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 45591
ST2NSX4MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 45593
ST2NSX4MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 45595
ST2NSX4MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45597
ST2NSX4MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45599
ST2NSX4MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45601
ST2NSX4MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45603
ST2NSX4MAX_THDI1_P | REAL | IOD_ST2_TCP | 45605
ST2NSX4MAX_THDI2_P | REAL | IOD_ST2_TCP | 45607
ST2NSX4MAX_THDI3_P | REAL | IOD_ST2_TCP | 45609
ST2NSX4MAX_THDV12_P | REAL | IOD_ST2_TCP | 45611
ST2NSX4MAX_THDV1N_P | REAL | IOD_ST2_TCP | 45613
ST2NSX4MAX_THDV23_P | REAL | IOD_ST2_TCP | 45615
ST2NSX4MAX_THDV2N_P | REAL | IOD_ST2_TCP | 45617
ST2NSX4MAX_THDV31_P | REAL | IOD_ST2_TCP | 45619
ST2NSX4MAX_THDV3N_P | REAL | IOD_ST2_TCP | 45621
ST2NSX4MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45623
ST2NSX4MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45625
ST2NSX4MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45627
ST2NSX4MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45629
ST2NSX4MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45631
ST2NSX4MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45633
ST2NSX4MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45635
ST2NSX4MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45637
ST2NSX4MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 45639
ST2NSX4MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 45641
ST2NSX4MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 45643
ST2NSX4MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 45645
ST2NSX4MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 45647
ST2NSX4MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 45649
ST2NSX4MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45651
ST2NSX4MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45653
ST2NSX4MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45655
ST2NSX4MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45657
ST2NSX4MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45659
ST2NSX4MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45661
ST2NSX4MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45663
ST2NSX4MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45665
ST2NSX4MIN_CosFL1 | REAL | IOD_ST2_TCP | 45667
ST2NSX4MIN_CosFL2 | REAL | IOD_ST2_TCP | 45669
ST2NSX4MIN_CosFL3 | REAL | IOD_ST2_TCP | 45671
ST2NSX4MIN_CosFTotal | REAL | IOD_ST2_TCP | 45673
ST2NSX4MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45675
ST2NSX4MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 45677
ST2NSX4MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 45679
ST2NSX4MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 45681
ST2NSX4MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 45683
ST2NSX4MIN_CurrentN_A | REAL | IOD_ST2_TCP | 45685
ST2NSX4MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45687
ST2NSX4MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45689
ST2NSX4MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45691
ST2NSX4MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45693
ST2NSX4MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 45695
ST2NSX4MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45697
ST2NSX4MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45699
ST2NSX4MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45701
ST2NSX4MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45703
ST2NSX4MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 45705
ST2NSX4MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 45707
ST2NSX4MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 45709
ST2NSX4MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 45711
ST2NSX4MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45713
ST2NSX4MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45715
ST2NSX4MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45717
ST2NSX4MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45719
ST2NSX4MIN_THDI1_P | REAL | IOD_ST2_TCP | 45721
ST2NSX4MIN_THDI2_P | REAL | IOD_ST2_TCP | 45723
ST2NSX4MIN_THDI3_P | REAL | IOD_ST2_TCP | 45725
ST2NSX4MIN_THDV12_P | REAL | IOD_ST2_TCP | 45727
ST2NSX4MIN_THDV1N_P | REAL | IOD_ST2_TCP | 45729
ST2NSX4MIN_THDV23_P | REAL | IOD_ST2_TCP | 45731
ST2NSX4MIN_THDV2N_P | REAL | IOD_ST2_TCP | 45733
ST2NSX4MIN_THDV31_P | REAL | IOD_ST2_TCP | 45735
ST2NSX4MIN_THDV3N_P | REAL | IOD_ST2_TCP | 45737
ST2NSX4MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45739
ST2NSX4MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45741
ST2NSX4MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45743
ST2NSX4MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45745
ST2NSX4MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45747
ST2NSX4MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45749
ST2NSX4MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45751
ST2NSX4MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45753
ST2NSX4MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 45755
ST2NSX4MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 45757
ST2NSX4MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 45759
ST2NSX4MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 45761
ST2NSX4MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 45763
ST2NSX4MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 45765
ST2NSX4PowerFactorL1 | REAL | IOD_ST2_TCP | 45767
ST2NSX4PowerFactorL2 | REAL | IOD_ST2_TCP | 45769
ST2NSX4PowerFactorL3 | REAL | IOD_ST2_TCP | 45771
ST2NSX4PowerFactorTotal | REAL | IOD_ST2_TCP | 45773
ST2NSX4RazEner_D | REAL | IOD_ST2_TCP | 45775
ST2NSX4RazEner_D_SCADA | REAL | IOD_ST2_TCP | 45777
ST2NSX4RazEner_D_TEMP | REAL | IOD_ST2_TCP | 45779
ST2NSX4RazEner_M | REAL | IOD_ST2_TCP | 45781
ST2NSX4RazEner_M_SCADA | REAL | IOD_ST2_TCP | 45783
ST2NSX4RazEner_M_TEMP | REAL | IOD_ST2_TCP | 45785
ST2NSX4RazEner_T | REAL | IOD_ST2_TCP | 45787
ST2NSX4RazEner_T_SCADA | REAL | IOD_ST2_TCP | 45789
ST2NSX4RazEner_T_TEMP | REAL | IOD_ST2_TCP | 45791
ST2NSX4ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 45793
ST2NSX4ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 45795
ST2NSX4ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 45797
ST2NSX4ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 45799
ST2NSX4ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45801
ST2NSX4ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45803
ST2NSX4ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45805
ST2NSX4ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 45807
ST2NSX4ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45809
ST2NSX4ResetMAX | DIGITAL | IOD_ST2_TCP | 00081
ST2NSX4ResetMIN | DIGITAL | IOD_ST2_TCP | 00082
ST2NSX4StatusSwitch | UINT | IOD_ST2_TCP | 48004
ST2NSX4THDI1_P | REAL | IOD_ST2_TCP | 45811
ST2NSX4THDI2_P | REAL | IOD_ST2_TCP | 45813
ST2NSX4THDI3_P | REAL | IOD_ST2_TCP | 45815
ST2NSX4THDV12_P | REAL | IOD_ST2_TCP | 45817
ST2NSX4THDV1N_P | REAL | IOD_ST2_TCP | 45819
ST2NSX4THDV23_P | REAL | IOD_ST2_TCP | 45821
ST2NSX4THDV2N_P | REAL | IOD_ST2_TCP | 45823
ST2NSX4THDV31_P | REAL | IOD_ST2_TCP | 45825
ST2NSX4THDV3N_P | REAL | IOD_ST2_TCP | 45827
ST2NSX4VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 45829
ST2NSX4VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 45831
ST2NSX4VoltageUnbV12_P | REAL | IOD_ST2_TCP | 45833
ST2NSX4VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 45835
ST2NSX4VoltageUnbV23_P | REAL | IOD_ST2_TCP | 45837
ST2NSX4VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 45839
ST2NSX4VoltageUnbV31_P | REAL | IOD_ST2_TCP | 45841
ST2NSX4VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 45843
ST2NSX4VoltageV12_V | REAL | IOD_ST2_TCP | 45845
ST2NSX4VoltageV1N_V | REAL | IOD_ST2_TCP | 45847
ST2NSX4VoltageV23_V | REAL | IOD_ST2_TCP | 45849
ST2NSX4VoltageV2N_V | REAL | IOD_ST2_TCP | 45851
ST2NSX4VoltageV31_V | REAL | IOD_ST2_TCP | 45853
ST2NSX4VoltageV3N_V | REAL | IOD_ST2_TCP | 45855
ST2NSX5ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45857
ST2NSX5ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 45859
ST2NSX5ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 45861
ST2NSX5ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 45863
ST2NSX5ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45865
ST2NSX5ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45867
ST2NSX5ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45869
ST2NSX5ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 45871
ST2NSX5ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45873
ST2NSX5ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 45875
ST2NSX5ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 45877
ST2NSX5ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 45879
ST2NSX5ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45881
ST2NSX5ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45883
ST2NSX5ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45885
ST2NSX5ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45887
ST2NSX5CosFL1 | REAL | IOD_ST2_TCP | 45889
ST2NSX5CosFL2 | REAL | IOD_ST2_TCP | 45891
ST2NSX5CosFL3 | REAL | IOD_ST2_TCP | 45893
ST2NSX5CosFTotal | REAL | IOD_ST2_TCP | 45895
ST2NSX5CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45897
ST2NSX5CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 45899
ST2NSX5CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45901
ST2NSX5CurrentDemandL1_A | REAL | IOD_ST2_TCP | 45903
ST2NSX5CurrentDemandL2_A | REAL | IOD_ST2_TCP | 45905
ST2NSX5CurrentDemandL3_A | REAL | IOD_ST2_TCP | 45907
ST2NSX5CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 45909
ST2NSX5CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 45911
ST2NSX5CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 45913
ST2NSX5CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 45915
ST2NSX5CurrentDemandN_A | REAL | IOD_ST2_TCP | 45917
ST2NSX5CurrentL1_A | REAL | IOD_ST2_TCP | 45919
ST2NSX5CurrentL2_A | REAL | IOD_ST2_TCP | 45921
ST2NSX5CurrentL3_A | REAL | IOD_ST2_TCP | 45923
ST2NSX5CurrentN_A | REAL | IOD_ST2_TCP | 45925
ST2NSX5CurrentUnbI1_P | REAL | IOD_ST2_TCP | 45927
ST2NSX5CurrentUnbI2_P | REAL | IOD_ST2_TCP | 45929
ST2NSX5CurrentUnbI3_P | REAL | IOD_ST2_TCP | 45931
ST2NSX5CurrentUnbN_P | REAL | IOD_ST2_TCP | 45933
ST2NSX5DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 45935
ST2NSX5DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45937
ST2NSX5DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45939
ST2NSX5DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45941
ST2NSX5DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45943
ST2NSX5Frequency_Hz | REAL | IOD_ST2_TCP | 45945
ST2NSX5FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 45947
ST2NSX5FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 45949
ST2NSX5FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 45951
ST2NSX5FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 45953
ST2NSX5MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 45955
ST2NSX5MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 45957
ST2NSX5MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 45959
ST2NSX5MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 45961
ST2NSX5MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 45963
ST2NSX5MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 45965
ST2NSX5MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 45967
ST2NSX5MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 45969
ST2NSX5MAX_CosFL1 | REAL | IOD_ST2_TCP | 45971
ST2NSX5MAX_CosFL2 | REAL | IOD_ST2_TCP | 45973
ST2NSX5MAX_CosFL3 | REAL | IOD_ST2_TCP | 45975
ST2NSX5MAX_CosFTotal | REAL | IOD_ST2_TCP | 45977
ST2NSX5MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 45979
ST2NSX5MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 45981
ST2NSX5MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 45983
ST2NSX5MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 45985
ST2NSX5MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 45987
ST2NSX5MAX_CurrentN_A | REAL | IOD_ST2_TCP | 45989
ST2NSX5MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 45991
ST2NSX5MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 45993
ST2NSX5MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 45995
ST2NSX5MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 45997
ST2NSX5MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 45999
ST2NSX5MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46001
ST2NSX5MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46003
ST2NSX5MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46005
ST2NSX5MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46007
ST2NSX5MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 46009
ST2NSX5MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 46011
ST2NSX5MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 46013
ST2NSX5MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 46015
ST2NSX5MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46017
ST2NSX5MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46019
ST2NSX5MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46021
ST2NSX5MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46023
ST2NSX5MAX_THDI1_P | REAL | IOD_ST2_TCP | 46025
ST2NSX5MAX_THDI2_P | REAL | IOD_ST2_TCP | 46027
ST2NSX5MAX_THDI3_P | REAL | IOD_ST2_TCP | 46029
ST2NSX5MAX_THDV12_P | REAL | IOD_ST2_TCP | 46031
ST2NSX5MAX_THDV1N_P | REAL | IOD_ST2_TCP | 46033
ST2NSX5MAX_THDV23_P | REAL | IOD_ST2_TCP | 46035
ST2NSX5MAX_THDV2N_P | REAL | IOD_ST2_TCP | 46037
ST2NSX5MAX_THDV31_P | REAL | IOD_ST2_TCP | 46039
ST2NSX5MAX_THDV3N_P | REAL | IOD_ST2_TCP | 46041
ST2NSX5MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46043
ST2NSX5MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46045
ST2NSX5MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46047
ST2NSX5MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46049
ST2NSX5MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46051
ST2NSX5MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46053
ST2NSX5MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46055
ST2NSX5MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46057
ST2NSX5MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 46059
ST2NSX5MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 46061
ST2NSX5MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 46063
ST2NSX5MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 46065
ST2NSX5MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 46067
ST2NSX5MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 46069
ST2NSX5MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 46071
ST2NSX5MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 46073
ST2NSX5MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 46075
ST2NSX5MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 46077
ST2NSX5MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 46079
ST2NSX5MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 46081
ST2NSX5MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 46083
ST2NSX5MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 46085
ST2NSX5MIN_CosFL1 | REAL | IOD_ST2_TCP | 46087
ST2NSX5MIN_CosFL2 | REAL | IOD_ST2_TCP | 46089
ST2NSX5MIN_CosFL3 | REAL | IOD_ST2_TCP | 46091
ST2NSX5MIN_CosFTotal | REAL | IOD_ST2_TCP | 46093
ST2NSX5MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 46095
ST2NSX5MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 46097
ST2NSX5MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 46099
ST2NSX5MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 46101
ST2NSX5MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 46103
ST2NSX5MIN_CurrentN_A | REAL | IOD_ST2_TCP | 46105
ST2NSX5MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 46107
ST2NSX5MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 46109
ST2NSX5MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 46111
ST2NSX5MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 46113
ST2NSX5MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 46115
ST2NSX5MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46117
ST2NSX5MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46119
ST2NSX5MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46121
ST2NSX5MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46123
ST2NSX5MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 46125
ST2NSX5MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 46127
ST2NSX5MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 46129
ST2NSX5MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 46131
ST2NSX5MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46133
ST2NSX5MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46135
ST2NSX5MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46137
ST2NSX5MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46139
ST2NSX5MIN_THDI1_P | REAL | IOD_ST2_TCP | 46141
ST2NSX5MIN_THDI2_P | REAL | IOD_ST2_TCP | 46143
ST2NSX5MIN_THDI3_P | REAL | IOD_ST2_TCP | 46145
ST2NSX5MIN_THDV12_P | REAL | IOD_ST2_TCP | 46147
ST2NSX5MIN_THDV1N_P | REAL | IOD_ST2_TCP | 46149
ST2NSX5MIN_THDV23_P | REAL | IOD_ST2_TCP | 46151
ST2NSX5MIN_THDV2N_P | REAL | IOD_ST2_TCP | 46153
ST2NSX5MIN_THDV31_P | REAL | IOD_ST2_TCP | 46155
ST2NSX5MIN_THDV3N_P | REAL | IOD_ST2_TCP | 46157
ST2NSX5MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46159
ST2NSX5MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46161
ST2NSX5MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46163
ST2NSX5MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46165
ST2NSX5MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46167
ST2NSX5MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46169
ST2NSX5MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46171
ST2NSX5MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46173
ST2NSX5MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 46175
ST2NSX5MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 46177
ST2NSX5MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 46179
ST2NSX5MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 46181
ST2NSX5MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 46183
ST2NSX5MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 46185
ST2NSX5PowerFactorL1 | REAL | IOD_ST2_TCP | 46187
ST2NSX5PowerFactorL2 | REAL | IOD_ST2_TCP | 46189
ST2NSX5PowerFactorL3 | REAL | IOD_ST2_TCP | 46191
ST2NSX5PowerFactorTotal | REAL | IOD_ST2_TCP | 46193
ST2NSX5RazEner_D | REAL | IOD_ST2_TCP | 46195
ST2NSX5RazEner_D_SCADA | REAL | IOD_ST2_TCP | 46197
ST2NSX5RazEner_D_TEMP | REAL | IOD_ST2_TCP | 46199
ST2NSX5RazEner_M | REAL | IOD_ST2_TCP | 46201
ST2NSX5RazEner_M_SCADA | REAL | IOD_ST2_TCP | 46203
ST2NSX5RazEner_M_TEMP | REAL | IOD_ST2_TCP | 46205
ST2NSX5RazEner_T | REAL | IOD_ST2_TCP | 46207
ST2NSX5RazEner_T_SCADA | REAL | IOD_ST2_TCP | 46209
ST2NSX5RazEner_T_TEMP | REAL | IOD_ST2_TCP | 46211
ST2NSX5ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 46213
ST2NSX5ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 46215
ST2NSX5ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 46217
ST2NSX5ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 46219
ST2NSX5ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46221
ST2NSX5ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46223
ST2NSX5ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46225
ST2NSX5ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 46227
ST2NSX5ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46229
ST2NSX5ResetMAX | DIGITAL | IOD_ST2_TCP | 00083
ST2NSX5ResetMIN | DIGITAL | IOD_ST2_TCP | 00084
ST2NSX5StatusSwitch | UINT | IOD_ST2_TCP | 48005
ST2NSX5THDI1_P | REAL | IOD_ST2_TCP | 46231
ST2NSX5THDI2_P | REAL | IOD_ST2_TCP | 46233
ST2NSX5THDI3_P | REAL | IOD_ST2_TCP | 46235
ST2NSX5THDV12_P | REAL | IOD_ST2_TCP | 46237
ST2NSX5THDV1N_P | REAL | IOD_ST2_TCP | 46239
ST2NSX5THDV23_P | REAL | IOD_ST2_TCP | 46241
ST2NSX5THDV2N_P | REAL | IOD_ST2_TCP | 46243
ST2NSX5THDV31_P | REAL | IOD_ST2_TCP | 46245
ST2NSX5THDV3N_P | REAL | IOD_ST2_TCP | 46247
ST2NSX5VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46249
ST2NSX5VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46251
ST2NSX5VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46253
ST2NSX5VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46255
ST2NSX5VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46257
ST2NSX5VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46259
ST2NSX5VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46261
ST2NSX5VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46263
ST2NSX5VoltageV12_V | REAL | IOD_ST2_TCP | 46265
ST2NSX5VoltageV1N_V | REAL | IOD_ST2_TCP | 46267
ST2NSX5VoltageV23_V | REAL | IOD_ST2_TCP | 46269
ST2NSX5VoltageV2N_V | REAL | IOD_ST2_TCP | 46271
ST2NSX5VoltageV31_V | REAL | IOD_ST2_TCP | 46273
ST2NSX5VoltageV3N_V | REAL | IOD_ST2_TCP | 46275
ST2NSX6ActiveEnergy_kWh | REAL | IOD_ST2_TCP | 46277
ST2NSX6ActiveNegativeEnergy_kWh | REAL | IOD_ST2_TCP | 46279
ST2NSX6ActivePositiveEnergy_kWh | REAL | IOD_ST2_TCP | 46281
ST2NSX6ActivePowerDemand_kW | REAL | IOD_ST2_TCP | 46283
ST2NSX6ActivePowerL1_kW | REAL | IOD_ST2_TCP | 46285
ST2NSX6ActivePowerL2_kW | REAL | IOD_ST2_TCP | 46287
ST2NSX6ActivePowerL3_kW | REAL | IOD_ST2_TCP | 46289
ST2NSX6ActivePowerMaxDemand_kW | REAL | IOD_ST2_TCP | 46291
ST2NSX6ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 46293
ST2NSX6ApparentEnergy_kVAh | REAL | IOD_ST2_TCP | 46295
ST2NSX6ApparentPowerDemand_kVA | REAL | IOD_ST2_TCP | 46297
ST2NSX6ApparentPowerMaxDemand_kVA | REAL | IOD_ST2_TCP | 46299
ST2NSX6ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 46301
ST2NSX6ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 46303
ST2NSX6ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 46305
ST2NSX6ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 46307
ST2NSX6CosFL1 | REAL | IOD_ST2_TCP | 46309
ST2NSX6CosFL2 | REAL | IOD_ST2_TCP | 46311
ST2NSX6CosFL3 | REAL | IOD_ST2_TCP | 46313
ST2NSX6CosFTotal | REAL | IOD_ST2_TCP | 46315
ST2NSX6CumulNegativeActiveEnergy_kWh | REAL | IOD_ST2_TCP | 46317
ST2NSX6CumulPositiveActiveEnergy_kWh | REAL | IOD_ST2_TCP | 46319
ST2NSX6CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 46321
ST2NSX6CurrentDemandL1_A | REAL | IOD_ST2_TCP | 46323
ST2NSX6CurrentDemandL2_A | REAL | IOD_ST2_TCP | 46325
ST2NSX6CurrentDemandL3_A | REAL | IOD_ST2_TCP | 46327
ST2NSX6CurrentDemandMaxL1_A | REAL | IOD_ST2_TCP | 46329
ST2NSX6CurrentDemandMaxL2_A | REAL | IOD_ST2_TCP | 46331
ST2NSX6CurrentDemandMaxL3_A | REAL | IOD_ST2_TCP | 46333
ST2NSX6CurrentDemandMaxN_A | REAL | IOD_ST2_TCP | 46335
ST2NSX6CurrentDemandN_A | REAL | IOD_ST2_TCP | 46337
ST2NSX6CurrentL1_A | REAL | IOD_ST2_TCP | 46339
ST2NSX6CurrentL2_A | REAL | IOD_ST2_TCP | 46341
ST2NSX6CurrentL3_A | REAL | IOD_ST2_TCP | 46343
ST2NSX6CurrentN_A | REAL | IOD_ST2_TCP | 46345
ST2NSX6CurrentUnbI1_P | REAL | IOD_ST2_TCP | 46347
ST2NSX6CurrentUnbI2_P | REAL | IOD_ST2_TCP | 46349
ST2NSX6CurrentUnbI3_P | REAL | IOD_ST2_TCP | 46351
ST2NSX6CurrentUnbN_P | REAL | IOD_ST2_TCP | 46353
ST2NSX6DelovnaEnergija_TEMP | REAL | IOD_ST2_TCP | 46355
ST2NSX6DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 46357
ST2NSX6DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 46359
ST2NSX6DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 46361
ST2NSX6DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 46363
ST2NSX6Frequency_Hz | REAL | IOD_ST2_TCP | 46365
ST2NSX6FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46367
ST2NSX6FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46369
ST2NSX6FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46371
ST2NSX6FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46373
ST2NSX6MAX_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 46375
ST2NSX6MAX_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 46377
ST2NSX6MAX_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 46379
ST2NSX6MAX_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 46381
ST2NSX6MAX_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 46383
ST2NSX6MAX_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 46385
ST2NSX6MAX_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 46387
ST2NSX6MAX_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 46389
ST2NSX6MAX_CosFL1 | REAL | IOD_ST2_TCP | 46391
ST2NSX6MAX_CosFL2 | REAL | IOD_ST2_TCP | 46393
ST2NSX6MAX_CosFL3 | REAL | IOD_ST2_TCP | 46395
ST2NSX6MAX_CosFTotal | REAL | IOD_ST2_TCP | 46397
ST2NSX6MAX_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 46399
ST2NSX6MAX_CurrentL1_A | REAL | IOD_ST2_TCP | 46401
ST2NSX6MAX_CurrentL2_A | REAL | IOD_ST2_TCP | 46403
ST2NSX6MAX_CurrentL3_A | REAL | IOD_ST2_TCP | 46405
ST2NSX6MAX_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 46407
ST2NSX6MAX_CurrentN_A | REAL | IOD_ST2_TCP | 46409
ST2NSX6MAX_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 46411
ST2NSX6MAX_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 46413
ST2NSX6MAX_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 46415
ST2NSX6MAX_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 46417
ST2NSX6MAX_Frequency_Hz | REAL | IOD_ST2_TCP | 46419
ST2NSX6MAX_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46421
ST2NSX6MAX_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46423
ST2NSX6MAX_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46425
ST2NSX6MAX_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46427
ST2NSX6MAX_PowerFactorL1 | REAL | IOD_ST2_TCP | 46429
ST2NSX6MAX_PowerFactorL2 | REAL | IOD_ST2_TCP | 46431
ST2NSX6MAX_PowerFactorL3 | REAL | IOD_ST2_TCP | 46433
ST2NSX6MAX_PowerFactorTotal | REAL | IOD_ST2_TCP | 46435
ST2NSX6MAX_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46437
ST2NSX6MAX_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46439
ST2NSX6MAX_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46441
ST2NSX6MAX_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46443
ST2NSX6MAX_THDI1_P | REAL | IOD_ST2_TCP | 46445
ST2NSX6MAX_THDI2_P | REAL | IOD_ST2_TCP | 46447
ST2NSX6MAX_THDI3_P | REAL | IOD_ST2_TCP | 46449
ST2NSX6MAX_THDV12_P | REAL | IOD_ST2_TCP | 46451
ST2NSX6MAX_THDV1N_P | REAL | IOD_ST2_TCP | 46453
ST2NSX6MAX_THDV23_P | REAL | IOD_ST2_TCP | 46455
ST2NSX6MAX_THDV2N_P | REAL | IOD_ST2_TCP | 46457
ST2NSX6MAX_THDV31_P | REAL | IOD_ST2_TCP | 46459
ST2NSX6MAX_THDV3N_P | REAL | IOD_ST2_TCP | 46461
ST2NSX6MAX_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46463
ST2NSX6MAX_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46465
ST2NSX6MAX_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46467
ST2NSX6MAX_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46469
ST2NSX6MAX_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46471
ST2NSX6MAX_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46473
ST2NSX6MAX_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46475
ST2NSX6MAX_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46477
ST2NSX6MAX_VoltageV12_V | REAL | IOD_ST2_TCP | 46479
ST2NSX6MAX_VoltageV1N_V | REAL | IOD_ST2_TCP | 46481
ST2NSX6MAX_VoltageV23_V | REAL | IOD_ST2_TCP | 46483
ST2NSX6MAX_VoltageV2N_V | REAL | IOD_ST2_TCP | 46485
ST2NSX6MAX_VoltageV31_V | REAL | IOD_ST2_TCP | 46487
ST2NSX6MAX_VoltageV3N_V | REAL | IOD_ST2_TCP | 46489
ST2NSX6MIN_ActivePowerL1_kW | REAL | IOD_ST2_TCP | 46491
ST2NSX6MIN_ActivePowerL2_kW | REAL | IOD_ST2_TCP | 46493
ST2NSX6MIN_ActivePowerL3_kW | REAL | IOD_ST2_TCP | 46495
ST2NSX6MIN_ActivePowerTotal_kW | REAL | IOD_ST2_TCP | 46497
ST2NSX6MIN_ApparetnPowerL1_kVA | REAL | IOD_ST2_TCP | 46499
ST2NSX6MIN_ApparetnPowerL2_kVA | REAL | IOD_ST2_TCP | 46501
ST2NSX6MIN_ApparetnPowerL3_kVA | REAL | IOD_ST2_TCP | 46503
ST2NSX6MIN_ApparetnPowerTotal_kVA | REAL | IOD_ST2_TCP | 46505
ST2NSX6MIN_CosFL1 | REAL | IOD_ST2_TCP | 46507
ST2NSX6MIN_CosFL2 | REAL | IOD_ST2_TCP | 46509
ST2NSX6MIN_CosFL3 | REAL | IOD_ST2_TCP | 46511
ST2NSX6MIN_CosFTotal | REAL | IOD_ST2_TCP | 46513
ST2NSX6MIN_CurrentAvgI1I2I3_A | REAL | IOD_ST2_TCP | 46515
ST2NSX6MIN_CurrentL1_A | REAL | IOD_ST2_TCP | 46517
ST2NSX6MIN_CurrentL2_A | REAL | IOD_ST2_TCP | 46519
ST2NSX6MIN_CurrentL3_A | REAL | IOD_ST2_TCP | 46521
ST2NSX6MIN_CurrentMaxL1L2L3N_A | REAL | IOD_ST2_TCP | 46523
ST2NSX6MIN_CurrentN_A | REAL | IOD_ST2_TCP | 46525
ST2NSX6MIN_DistortionPowerL1_kVAr | REAL | IOD_ST2_TCP | 46527
ST2NSX6MIN_DistortionPowerL2_kVAr | REAL | IOD_ST2_TCP | 46529
ST2NSX6MIN_DistortionPowerL3_kVAr | REAL | IOD_ST2_TCP | 46531
ST2NSX6MIN_DistortionPowerTotal_kVAr | REAL | IOD_ST2_TCP | 46533
ST2NSX6MIN_Frequency_Hz | REAL | IOD_ST2_TCP | 46535
ST2NSX6MIN_FunReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46537
ST2NSX6MIN_FunReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46539
ST2NSX6MIN_FunReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46541
ST2NSX6MIN_FunReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46543
ST2NSX6MIN_PowerFactorL1 | REAL | IOD_ST2_TCP | 46545
ST2NSX6MIN_PowerFactorL2 | REAL | IOD_ST2_TCP | 46547
ST2NSX6MIN_PowerFactorL3 | REAL | IOD_ST2_TCP | 46549
ST2NSX6MIN_PowerFactorTotal | REAL | IOD_ST2_TCP | 46551
ST2NSX6MIN_ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46553
ST2NSX6MIN_ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46555
ST2NSX6MIN_ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46557
ST2NSX6MIN_ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46559
ST2NSX6MIN_THDI1_P | REAL | IOD_ST2_TCP | 46561
ST2NSX6MIN_THDI2_P | REAL | IOD_ST2_TCP | 46563
ST2NSX6MIN_THDI3_P | REAL | IOD_ST2_TCP | 46565
ST2NSX6MIN_THDV12_P | REAL | IOD_ST2_TCP | 46567
ST2NSX6MIN_THDV1N_P | REAL | IOD_ST2_TCP | 46569
ST2NSX6MIN_THDV23_P | REAL | IOD_ST2_TCP | 46571
ST2NSX6MIN_THDV2N_P | REAL | IOD_ST2_TCP | 46573
ST2NSX6MIN_THDV31_P | REAL | IOD_ST2_TCP | 46575
ST2NSX6MIN_THDV3N_P | REAL | IOD_ST2_TCP | 46577
ST2NSX6MIN_VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46579
ST2NSX6MIN_VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46581
ST2NSX6MIN_VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46583
ST2NSX6MIN_VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46585
ST2NSX6MIN_VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46587
ST2NSX6MIN_VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46589
ST2NSX6MIN_VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46591
ST2NSX6MIN_VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46593
ST2NSX6MIN_VoltageV12_V | REAL | IOD_ST2_TCP | 46595
ST2NSX6MIN_VoltageV1N_V | REAL | IOD_ST2_TCP | 46597
ST2NSX6MIN_VoltageV23_V | REAL | IOD_ST2_TCP | 46599
ST2NSX6MIN_VoltageV2N_V | REAL | IOD_ST2_TCP | 46601
ST2NSX6MIN_VoltageV31_V | REAL | IOD_ST2_TCP | 46603
ST2NSX6MIN_VoltageV3N_V | REAL | IOD_ST2_TCP | 46605
ST2NSX6PowerFactorL1 | REAL | IOD_ST2_TCP | 46607
ST2NSX6PowerFactorL2 | REAL | IOD_ST2_TCP | 46609
ST2NSX6PowerFactorL3 | REAL | IOD_ST2_TCP | 46611
ST2NSX6PowerFactorTotal | REAL | IOD_ST2_TCP | 46613
ST2NSX6RazEner_D | REAL | IOD_ST2_TCP | 46615
ST2NSX6RazEner_D_SCADA | REAL | IOD_ST2_TCP | 46617
ST2NSX6RazEner_D_TEMP | REAL | IOD_ST2_TCP | 46619
ST2NSX6RazEner_M | REAL | IOD_ST2_TCP | 46621
ST2NSX6RazEner_M_SCADA | REAL | IOD_ST2_TCP | 46623
ST2NSX6RazEner_M_TEMP | REAL | IOD_ST2_TCP | 46625
ST2NSX6RazEner_T | REAL | IOD_ST2_TCP | 46627
ST2NSX6RazEner_T_SCADA | REAL | IOD_ST2_TCP | 46629
ST2NSX6RazEner_T_TEMP | REAL | IOD_ST2_TCP | 46631
ST2NSX6ReactiveEnergy_kVArh | REAL | IOD_ST2_TCP | 46633
ST2NSX6ReactiveNegativeEnergy_kVArh | REAL | IOD_ST2_TCP | 46635
ST2NSX6ReactivePositiveEnergy_kVArh | REAL | IOD_ST2_TCP | 46637
ST2NSX6ReactivePowerDemand_kVAr | REAL | IOD_ST2_TCP | 46639
ST2NSX6ReactivePowerL1_kVAr | REAL | IOD_ST2_TCP | 46641
ST2NSX6ReactivePowerL2_kVAr | REAL | IOD_ST2_TCP | 46643
ST2NSX6ReactivePowerL3_kVAr | REAL | IOD_ST2_TCP | 46645
ST2NSX6ReactivePowerMaxDemand_kVAr | REAL | IOD_ST2_TCP | 46647
ST2NSX6ReactivePowerTotal_kVAr | REAL | IOD_ST2_TCP | 46649
ST2NSX6ResetMAX | DIGITAL | IOD_ST2_TCP | 00085
ST2NSX6ResetMIN | DIGITAL | IOD_ST2_TCP | 00086
ST2NSX6StatusSwitch | UINT | IOD_ST2_TCP | 48006
ST2NSX6THDI1_P | REAL | IOD_ST2_TCP | 46651
ST2NSX6THDI2_P | REAL | IOD_ST2_TCP | 46653
ST2NSX6THDI3_P | REAL | IOD_ST2_TCP | 46655
ST2NSX6THDV12_P | REAL | IOD_ST2_TCP | 46657
ST2NSX6THDV1N_P | REAL | IOD_ST2_TCP | 46659
ST2NSX6THDV23_P | REAL | IOD_ST2_TCP | 46661
ST2NSX6THDV2N_P | REAL | IOD_ST2_TCP | 46663
ST2NSX6THDV31_P | REAL | IOD_ST2_TCP | 46665
ST2NSX6THDV3N_P | REAL | IOD_ST2_TCP | 46667
ST2NSX6VoltageAvgPhToN_V | REAL | IOD_ST2_TCP | 46669
ST2NSX6VoltageAvgPhToPh_V | REAL | IOD_ST2_TCP | 46671
ST2NSX6VoltageUnbV12_P | REAL | IOD_ST2_TCP | 46673
ST2NSX6VoltageUnbV1N_P | REAL | IOD_ST2_TCP | 46675
ST2NSX6VoltageUnbV23_P | REAL | IOD_ST2_TCP | 46677
ST2NSX6VoltageUnbV2N_P | REAL | IOD_ST2_TCP | 46679
ST2NSX6VoltageUnbV31_P | REAL | IOD_ST2_TCP | 46681
ST2NSX6VoltageUnbV3N_P | REAL | IOD_ST2_TCP | 46683
ST2NSX6VoltageV12_V | REAL | IOD_ST2_TCP | 46685
ST2NSX6VoltageV1N_V | REAL | IOD_ST2_TCP | 46687
ST2NSX6VoltageV23_V | REAL | IOD_ST2_TCP | 46689
ST2NSX6VoltageV2N_V | REAL | IOD_ST2_TCP | 46691
ST2NSX6VoltageV31_V | REAL | IOD_ST2_TCP | 46693
ST2NSX6VoltageV3N_V | REAL | IOD_ST2_TCP | 46695
ST2PLC_SB_IROGSM21_F2_2_NOT_OK | DIGITAL | IOD_ST2_TCP | 00087
ST2PLC_SB_IROGSM22_F2_2_NOT_OK | DIGITAL | IOD_ST2_TCP | 00088
ST2PMMQA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2_TCP | 00089
ST2PMMQB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_ST2_TCP | 00090
ST2PMMSkNapaka_med60in80 | DIGITAL | IOD_ST2_TCP | 00091
ST2PMMSkNapaka_nad80 | DIGITAL | IOD_ST2_TCP | 00092
ST2PMMSkNapakaVirA_med60in80 | DIGITAL | IOD_ST2_TCP | 00093
ST2PMMSkNapakaVirA_nad80 | DIGITAL | IOD_ST2_TCP | 00094
ST2PMMSkNapakaVirB_med60in80 | DIGITAL | IOD_ST2_TCP | 00095
ST2PMMSkNapakaVirB_nad80 | DIGITAL | IOD_ST2_TCP | 00096
ST2PMMVirACurrent10 | REAL | IOD_ST2_TCP | 46697
ST2PMMVirACurrent11 | REAL | IOD_ST2_TCP | 46699
ST2PMMVirACurrent12 | REAL | IOD_ST2_TCP | 46701
ST2PMMVirACurrent13 | REAL | IOD_ST2_TCP | 46703
ST2PMMVirACurrent14 | REAL | IOD_ST2_TCP | 46705
ST2PMMVirACurrent15 | REAL | IOD_ST2_TCP | 46707
ST2PMMVirACurrent16 | REAL | IOD_ST2_TCP | 46709
ST2PMMVirACurrent17 | REAL | IOD_ST2_TCP | 46711
ST2PMMVirACurrent18 | REAL | IOD_ST2_TCP | 46713
ST2PMMVirACurrent19 | REAL | IOD_ST2_TCP | 46715
ST2PMMVirACurrent1 | REAL | IOD_ST2_TCP | 46717
ST2PMMVirACurrent20 | REAL | IOD_ST2_TCP | 46719
ST2PMMVirACurrent21 | REAL | IOD_ST2_TCP | 46721
ST2PMMVirACurrent22 | REAL | IOD_ST2_TCP | 46723
ST2PMMVirACurrent23 | REAL | IOD_ST2_TCP | 46725
ST2PMMVirACurrent24 | REAL | IOD_ST2_TCP | 46727
ST2PMMVirACurrent25 | REAL | IOD_ST2_TCP | 46729
ST2PMMVirACurrent26 | REAL | IOD_ST2_TCP | 46731
ST2PMMVirACurrent27 | REAL | IOD_ST2_TCP | 46733
ST2PMMVirACurrent28 | REAL | IOD_ST2_TCP | 46735
ST2PMMVirACurrent29 | REAL | IOD_ST2_TCP | 46737
ST2PMMVirACurrent2 | REAL | IOD_ST2_TCP | 46739
ST2PMMVirACurrent30 | REAL | IOD_ST2_TCP | 46741
ST2PMMVirACurrent31 | REAL | IOD_ST2_TCP | 46743
ST2PMMVirACurrent32 | REAL | IOD_ST2_TCP | 46745
ST2PMMVirACurrent33 | REAL | IOD_ST2_TCP | 46747
ST2PMMVirACurrent34 | REAL | IOD_ST2_TCP | 46749
ST2PMMVirACurrent35 | REAL | IOD_ST2_TCP | 46751
ST2PMMVirACurrent36 | REAL | IOD_ST2_TCP | 46753
ST2PMMVirACurrent37 | REAL | IOD_ST2_TCP | 46755
ST2PMMVirACurrent38 | REAL | IOD_ST2_TCP | 46757
ST2PMMVirACurrent39 | REAL | IOD_ST2_TCP | 46759
ST2PMMVirACurrent3 | REAL | IOD_ST2_TCP | 46761
ST2PMMVirACurrent40 | REAL | IOD_ST2_TCP | 46763
ST2PMMVirACurrent41 | REAL | IOD_ST2_TCP | 46765
ST2PMMVirACurrent42 | REAL | IOD_ST2_TCP | 46767
ST2PMMVirACurrent43 | REAL | IOD_ST2_TCP | 46769
ST2PMMVirACurrent44 | REAL | IOD_ST2_TCP | 46771
ST2PMMVirACurrent4 | REAL | IOD_ST2_TCP | 46773
ST2PMMVirACurrent5 | REAL | IOD_ST2_TCP | 46775
ST2PMMVirACurrent6 | REAL | IOD_ST2_TCP | 46777
ST2PMMVirACurrent7 | REAL | IOD_ST2_TCP | 46779
ST2PMMVirACurrent8 | REAL | IOD_ST2_TCP | 46781
ST2PMMVirACurrent9 | REAL | IOD_ST2_TCP | 46783
ST2PMMVirA_fsys | REAL | IOD_ST2_TCP | 46785
ST2PMMVirA_Isys | REAL | IOD_ST2_TCP | 46787
ST2PMMVirA_NapakaOzemljitve | DIGITAL | IOD_ST2_TCP | 00097
ST2PMMVirA_PFsys | REAL | IOD_ST2_TCP | 46789
ST2PMMVirA_Psys | REAL | IOD_ST2_TCP | 46791
ST2PMMVirA_Qsys | REAL | IOD_ST2_TCP | 46793
ST2PMMVirA_Ssys | REAL | IOD_ST2_TCP | 46795
ST2PMMVirA_Usys | REAL | IOD_ST2_TCP | 46797
ST2PMMVirAActiveEnergyConsumed_kWh | REAL | IOD_ST2_TCP | 46799
ST2PMMVirAActivePowerPhaseA_kW | REAL | IOD_ST2_TCP | 46801
ST2PMMVirAActivePowerPhaseB_kW | REAL | IOD_ST2_TCP | 46803
ST2PMMVirAActivePowerPhaseC_kW | REAL | IOD_ST2_TCP | 46805
ST2PMMVirAAlarmPhase_C01_16_60to80 | UINT | IOD_ST2_TCP | 48007
ST2PMMVirAAlarmPhase_C01_16_over80 | UINT | IOD_ST2_TCP | 48008
ST2PMMVirAAlarmPhase_C17_32_60to80 | UINT | IOD_ST2_TCP | 48009
ST2PMMVirAAlarmPhase_C17_32_over80 | UINT | IOD_ST2_TCP | 48010
ST2PMMVirAAlarmPhase_C33_44_60to80 | UINT | IOD_ST2_TCP | 48011
ST2PMMVirAAlarmPhase_C33_44_over80 | UINT | IOD_ST2_TCP | 48012
ST2PMMVirAAparentPowerPhaseA | REAL | IOD_ST2_TCP | 46807
ST2PMMVirAAparentPowerPhaseB | REAL | IOD_ST2_TCP | 46809
ST2PMMVirAAparentPowerPhaseC | REAL | IOD_ST2_TCP | 46811
ST2PMMVirACurrentInPhaseA_A | REAL | IOD_ST2_TCP | 46813
ST2PMMVirACurrentInPhaseB_A | REAL | IOD_ST2_TCP | 46815
ST2PMMVirACurrentInPhaseC_A | REAL | IOD_ST2_TCP | 46817
ST2PMMVirAReactiveEnergyConsumed_kVARh | REAL | IOD_ST2_TCP | 46819
ST2PMMVirAReactivePowerPhaseA | REAL | IOD_ST2_TCP | 46821
ST2PMMVirAReactivePowerPhaseB | REAL | IOD_ST2_TCP | 46823
ST2PMMVirAReactivePowerPhaseC | REAL | IOD_ST2_TCP | 46825
ST2PMMVirAVoltageBetweenPhaseAB_V | REAL | IOD_ST2_TCP | 46827
ST2PMMVirAVoltageBetweenPhaseAN_V | REAL | IOD_ST2_TCP | 46829
ST2PMMVirAVoltageBetweenPhaseBC_V | REAL | IOD_ST2_TCP | 46831
ST2PMMVirAVoltageBetweenPhaseBN_V | REAL | IOD_ST2_TCP | 46833
ST2PMMVirAVoltageBetweenPhaseCA_V | REAL | IOD_ST2_TCP | 46835
ST2PMMVirAVoltageBetweenPhaseCN_V | REAL | IOD_ST2_TCP | 46837
ST2PMMVirBCurrent10 | REAL | IOD_ST2_TCP | 46839
ST2PMMVirBCurrent11 | REAL | IOD_ST2_TCP | 46841
ST2PMMVirBCurrent12 | REAL | IOD_ST2_TCP | 46843
ST2PMMVirBCurrent13 | REAL | IOD_ST2_TCP | 46845
ST2PMMVirBCurrent14 | REAL | IOD_ST2_TCP | 46847
ST2PMMVirBCurrent15 | REAL | IOD_ST2_TCP | 46849
ST2PMMVirBCurrent16 | REAL | IOD_ST2_TCP | 46851
ST2PMMVirBCurrent17 | REAL | IOD_ST2_TCP | 46853
ST2PMMVirBCurrent18 | REAL | IOD_ST2_TCP | 46855
ST2PMMVirBCurrent19 | REAL | IOD_ST2_TCP | 46857
ST2PMMVirBCurrent1 | REAL | IOD_ST2_TCP | 46859
ST2PMMVirBCurrent20 | REAL | IOD_ST2_TCP | 46861
ST2PMMVirBCurrent21 | REAL | IOD_ST2_TCP | 46863
ST2PMMVirBCurrent22 | REAL | IOD_ST2_TCP | 46865
ST2PMMVirBCurrent23 | REAL | IOD_ST2_TCP | 46867
ST2PMMVirBCurrent24 | REAL | IOD_ST2_TCP | 46869
ST2PMMVirBCurrent25 | REAL | IOD_ST2_TCP | 46871
ST2PMMVirBCurrent26 | REAL | IOD_ST2_TCP | 46873
ST2PMMVirBCurrent27 | REAL | IOD_ST2_TCP | 46875
ST2PMMVirBCurrent28 | REAL | IOD_ST2_TCP | 46877
ST2PMMVirBCurrent29 | REAL | IOD_ST2_TCP | 46879
ST2PMMVirBCurrent2 | REAL | IOD_ST2_TCP | 46881
ST2PMMVirBCurrent30 | REAL | IOD_ST2_TCP | 46883
ST2PMMVirBCurrent31 | REAL | IOD_ST2_TCP | 46885
ST2PMMVirBCurrent32 | REAL | IOD_ST2_TCP | 46887
ST2PMMVirBCurrent33 | REAL | IOD_ST2_TCP | 46889
ST2PMMVirBCurrent34 | REAL | IOD_ST2_TCP | 46891
ST2PMMVirBCurrent35 | REAL | IOD_ST2_TCP | 46893
ST2PMMVirBCurrent36 | REAL | IOD_ST2_TCP | 46895
ST2PMMVirBCurrent37 | REAL | IOD_ST2_TCP | 46897
ST2PMMVirBCurrent38 | REAL | IOD_ST2_TCP | 46899
ST2PMMVirBCurrent39 | REAL | IOD_ST2_TCP | 46901
ST2PMMVirBCurrent3 | REAL | IOD_ST2_TCP | 46903
ST2PMMVirBCurrent40 | REAL | IOD_ST2_TCP | 46905
ST2PMMVirBCurrent41 | REAL | IOD_ST2_TCP | 46907
ST2PMMVirBCurrent42 | REAL | IOD_ST2_TCP | 46909
ST2PMMVirBCurrent43 | REAL | IOD_ST2_TCP | 46911
ST2PMMVirBCurrent44 | REAL | IOD_ST2_TCP | 46913
ST2PMMVirBCurrent4 | REAL | IOD_ST2_TCP | 46915
ST2PMMVirBCurrent5 | REAL | IOD_ST2_TCP | 46917
ST2PMMVirBCurrent6 | REAL | IOD_ST2_TCP | 46919
ST2PMMVirBCurrent7 | REAL | IOD_ST2_TCP | 46921
ST2PMMVirBCurrent8 | REAL | IOD_ST2_TCP | 46923
ST2PMMVirBCurrent9 | REAL | IOD_ST2_TCP | 46925
ST2PMMVirB_fsys | REAL | IOD_ST2_TCP | 46927
ST2PMMVirB_Isys | REAL | IOD_ST2_TCP | 46929
ST2PMMVirB_NapakaOzemljitve | DIGITAL | IOD_ST2_TCP | 00098
ST2PMMVirB_PFsys | REAL | IOD_ST2_TCP | 46931
ST2PMMVirB_Psys | REAL | IOD_ST2_TCP | 46933
ST2PMMVirB_Qsys | REAL | IOD_ST2_TCP | 46935
ST2PMMVirB_Ssys | REAL | IOD_ST2_TCP | 46937
ST2PMMVirB_Usys | REAL | IOD_ST2_TCP | 46939
ST2PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_ST2_TCP | 46941
ST2PMMVirBActivePowerPhaseA_kW | REAL | IOD_ST2_TCP | 46943
ST2PMMVirBActivePowerPhaseB_kW | REAL | IOD_ST2_TCP | 46945
ST2PMMVirBActivePowerPhaseC_kW | REAL | IOD_ST2_TCP | 46947
ST2PMMVirBAlarmPhase_C01_16_60to80 | UINT | IOD_ST2_TCP | 48013
ST2PMMVirBAlarmPhase_C01_16_over80 | UINT | IOD_ST2_TCP | 48014
ST2PMMVirBAlarmPhase_C17_32_60to80 | UINT | IOD_ST2_TCP | 48015
ST2PMMVirBAlarmPhase_C17_32_over80 | UINT | IOD_ST2_TCP | 48016
ST2PMMVirBAlarmPhase_C33_44_60to80 | UINT | IOD_ST2_TCP | 48017
ST2PMMVirBAlarmPhase_C33_44_over80 | UINT | IOD_ST2_TCP | 48018
ST2PMMVirBAparentPowerPhaseA | REAL | IOD_ST2_TCP | 46949
ST2PMMVirBAparentPowerPhaseB | REAL | IOD_ST2_TCP | 46951
ST2PMMVirBAparentPowerPhaseC | REAL | IOD_ST2_TCP | 46953
ST2PMMVirBCurrentInPhaseA_A | REAL | IOD_ST2_TCP | 46955
ST2PMMVirBCurrentInPhaseB_A | REAL | IOD_ST2_TCP | 46957
ST2PMMVirBCurrentInPhaseC_A | REAL | IOD_ST2_TCP | 46959
ST2PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_ST2_TCP | 46961
ST2PMMVirBReactivePowerPhaseA | REAL | IOD_ST2_TCP | 46963
ST2PMMVirBReactivePowerPhaseB | REAL | IOD_ST2_TCP | 46965
ST2PMMVirBReactivePowerPhaseC | REAL | IOD_ST2_TCP | 46967
ST2PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_ST2_TCP | 46969
ST2PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_ST2_TCP | 46971
ST2PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_ST2_TCP | 46973
ST2PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_ST2_TCP | 46975
ST2PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_ST2_TCP | 46977
ST2PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_ST2_TCP | 46979
ST2PrevisokaTemp | DIGITAL | IOD_ST2_TCP | 00099
ST2razlitjeLAH1 | DIGITAL | IOD_ST2_TCP | 00100
ST2SetDateTime | DIGITAL | IOD_ST2_TCP | 00101
ST2SetDateTimeDemand | DIGITAL | IOD_ST2_TCP | 00102
ST2SetDateTimeError | DIGITAL | IOD_ST2_TCP | 00103
ST2SetDateTimeFinished | DIGITAL | IOD_ST2_TCP | 00104
ST2SlabaBaterijaPLC | DIGITAL | IOD_ST2_TCP | 00105
ST2TIA1_alarm | INT | IOD_ST2_TCP | 40024
ST2TIA1_previs_temp | DIGITAL | IOD_ST2_TCP | 00106
ST2TIA1_temp_s | INT | IOD_ST2_TCP | 40025
ST2TIA2_alarm | INT | IOD_ST2_TCP | 40026
ST2TIA2_previs_temp | DIGITAL | IOD_ST2_TCP | 00107
ST2TIA2_temp_s | INT | IOD_ST2_TCP | 40027
ST2TIA3_alarm | INT | IOD_ST2_TCP | 40028
ST2TIA3_previs_temp | DIGITAL | IOD_ST2_TCP | 00108
ST2TIA3_temp_s | INT | IOD_ST2_TCP | 40029
ST2TIA4_alarm | INT | IOD_ST2_TCP | 40030
ST2TIA4_previs_temp | DIGITAL | IOD_ST2_TCP | 00109
ST2TIA4_temp_s | INT | IOD_ST2_TCP | 40031
ST2TIA5_alarm | INT | IOD_ST2_TCP | 40032
ST2TIA5_previs_temp | DIGITAL | IOD_ST2_TCP | 00110
ST2TIA5_temp_s | INT | IOD_ST2_TCP | 40033
ST2TIA6_alarm | INT | IOD_ST2_TCP | 40034
ST2TIA6_previs_temp | DIGITAL | IOD_ST2_TCP | 00111
ST2TIA6_temp_s | INT | IOD_ST2_TCP | 40035
ST2TIA7_alarm | INT | IOD_ST2_TCP | 40036
ST2TIA7_previs_temp | DIGITAL | IOD_ST2_TCP | 00112
ST2TIA7_temp_s | INT | IOD_ST2_TCP | 40037
ST2TIA8_alarm | INT | IOD_ST2_TCP | 40038
ST2TIA8_previs_temp | DIGITAL | IOD_ST2_TCP | 00113
ST2TIA8_temp_s | INT | IOD_ST2_TCP | 40039
ST2ups_alarm | DIGITAL | IOD_ST2_TCP | 00114
ST2ups_baterijski_nac | DIGITAL | IOD_ST2_TCP | 00115
ST2ups_polnjenje | DIGITAL | IOD_ST2_TCP | 00116
ST2UserCurrentLevel | INT | IOD_ST2_TCP | 40040
ST2UserCurrentName | STRING | IOD_ST2_TCP | 47076[15]
ST2UserDisplay | STRING | IOD_ST2_TCP | 47091[15]
ST2UserLoggedIn | DIGITAL | IOD_ST2_TCP | 00117
ST2XVH_AlarmOn | DIGITAL | IOD_ST2_TCP | 00118
ST2Server_B_Izpad | DIGITAL | IOD_ST2_mem | D200
ST2Server_A_Izpad | DIGITAL | IOD_ST2_mem | D201
AST2_omogoci_sms | DIGITAL | IOD_ST2_disk | D1[100]
ST2NapakaSenzorVlagaHIA1_om | DIGITAL | IOD_ST2_disk | D102
ST2NapakaSenzorVlagaHIA2_om | DIGITAL | IOD_ST2_disk | D103
ST2NapakaSenzorVlagaHIA3_om | DIGITAL | IOD_ST2_disk | D104
ST2NapakaSenzorVlagaHIA4_om | DIGITAL | IOD_ST2_disk | D105
ST2NapakaSenzorVlagaHIA5_om | DIGITAL | IOD_ST2_disk | D106
ST2NapakaSenzorVlagaHIA6_om | DIGITAL | IOD_ST2_disk | D107
ST2NapakaSenzorVlagaHIA7_om | DIGITAL | IOD_ST2_disk | D108
ST2NapakaSenzorVlagaHIA8_om | DIGITAL | IOD_ST2_disk | D109
ST2NapakaTSTempTIA1_om | DIGITAL | IOD_ST2_disk | D110
ST2NapakaTSTempTIA2_om | DIGITAL | IOD_ST2_disk | D111
ST2NapakaTSTempTIA3_om | DIGITAL | IOD_ST2_disk | D112
ST2NapakaTSTempTIA4_om | DIGITAL | IOD_ST2_disk | D113
ST2NapakaTSTempTIA5_om | DIGITAL | IOD_ST2_disk | D114
ST2NapakaTSTempTIA6_om | DIGITAL | IOD_ST2_disk | D115
ST2NapakaTSTempTIA7_om | DIGITAL | IOD_ST2_disk | D116
ST2NapakaTSTempTIA8_om | DIGITAL | IOD_ST2_disk | D117
ST2TIA1_previs_temp_om | DIGITAL | IOD_ST2_disk | D118
ST2TIA2_previs_temp_om | DIGITAL | IOD_ST2_disk | D119
ST2TIA3_previs_temp_om | DIGITAL | IOD_ST2_disk | D120
ST2TIA4_previs_temp_om | DIGITAL | IOD_ST2_disk | D121
ST2TIA5_previs_temp_om | DIGITAL | IOD_ST2_disk | D122
ST2TIA6_previs_temp_om | DIGITAL | IOD_ST2_disk | D123
ST2TIA7_previs_temp_om | DIGITAL | IOD_ST2_disk | D124
ST2TIA8_previs_temp_om | DIGITAL | IOD_ST2_disk | D125
ST2razlitjeLAH1_om | DIGITAL | IOD_ST2_disk | D126
ST2Server_A_Izpad_om | DIGITAL | IOD_ST2_disk | D127
ST2Server_B_Izpad_om | DIGITAL | IOD_ST2_disk | D128
ST2napaka_kom_panel_om | DIGITAL | IOD_ST2_disk | D129
ST2SetDateTimeError_om | DIGITAL | IOD_ST2_disk | D130
ST2SlabaBaterijaPLC_om | DIGITAL | IOD_ST2_disk | D131
ST2ups_baterijski_nac_om | DIGITAL | IOD_ST2_disk | D132
ST2ups_alarm_om | DIGITAL | IOD_ST2_disk | D133
ST2ups_polnjenje_om | DIGITAL | IOD_ST2_disk | D134
ST2UserloggedIn_mem | INT | IOD_ST2_mem | I1
ST2_ComSCADA_stevec1 | INT | IOD_ST2_mem | I2
ST2_ComSCADA_stevec2 | INT | IOD_ST2_mem | I3
ST2_ComSCADA_stevec3 | INT | IOD_ST2_mem | I4
ST2_ComSCADA_stevec4 | INT | IOD_ST2_mem | I5
BST2_omogoci_sms | DIGITAL | IOD_ST2_disk | D200[100]
ST2PMMVirACurrent1_med60in80 | DIGITAL | IOD_ST2_disk | D302
ST2PMMVirACurrent2_med60in80 | DIGITAL | IOD_ST2_disk | D303
ST2PMMVirACurrent3_med60in80 | DIGITAL | IOD_ST2_disk | D304
ST2PMMVirACurrent4_med60in80 | DIGITAL | IOD_ST2_disk | D305
ST2PMMVirACurrent5_med60in80 | DIGITAL | IOD_ST2_disk | D306
ST2PMMVirACurrent6_med60in80 | DIGITAL | IOD_ST2_disk | D307
ST2PMMVirACurrent7_med60in80 | DIGITAL | IOD_ST2_disk | D308
ST2PMMVirACurrent8_med60in80 | DIGITAL | IOD_ST2_disk | D309
ST2PMMVirACurrent9_med60in80 | DIGITAL | IOD_ST2_disk | D310
ST2PMMVirACurrent10_med60in80 | DIGITAL | IOD_ST2_disk | D311
ST2PMMVirACurrent11_med60in80 | DIGITAL | IOD_ST2_disk | D312
ST2PMMVirACurrent12_med60in80 | DIGITAL | IOD_ST2_disk | D313
ST2PMMVirACurrent13_med60in80 | DIGITAL | IOD_ST2_disk | D314
ST2PMMVirACurrent14_med60in80 | DIGITAL | IOD_ST2_disk | D315
ST2PMMVirACurrent15_med60in80 | DIGITAL | IOD_ST2_disk | D316
ST2PMMVirACurrent16_med60in80 | DIGITAL | IOD_ST2_disk | D317
ST2PMMVirACurrent17_med60in80 | DIGITAL | IOD_ST2_disk | D318
ST2PMMVirACurrent18_med60in80 | DIGITAL | IOD_ST2_disk | D319
ST2PMMVirACurrent19_med60in80 | DIGITAL | IOD_ST2_disk | D320
ST2PMMVirACurrent20_med60in80 | DIGITAL | IOD_ST2_disk | D321
ST2PMMVirACurrent21_med60in80 | DIGITAL | IOD_ST2_disk | D322
ST2PMMVirACurrent22_med60in80 | DIGITAL | IOD_ST2_disk | D323
ST2PMMVirACurrent23_med60in80 | DIGITAL | IOD_ST2_disk | D324
ST2PMMVirACurrent24_med60in80 | DIGITAL | IOD_ST2_disk | D325
ST2PMMVirACurrent25_med60in80 | DIGITAL | IOD_ST2_disk | D326
ST2PMMVirACurrent26_med60in80 | DIGITAL | IOD_ST2_disk | D327
ST2PMMVirACurrent27_med60in80 | DIGITAL | IOD_ST2_disk | D328
ST2PMMVirACurrent28_med60in80 | DIGITAL | IOD_ST2_disk | D329
ST2PMMVirACurrent29_med60in80 | DIGITAL | IOD_ST2_disk | D330
ST2PMMVirACurrent30_med60in80 | DIGITAL | IOD_ST2_disk | D331
ST2PMMVirACurrent31_med60in80 | DIGITAL | IOD_ST2_disk | D332
ST2PMMVirACurrent32_med60in80 | DIGITAL | IOD_ST2_disk | D333
ST2PMMVirACurrent33_med60in80 | DIGITAL | IOD_ST2_disk | D334
ST2PMMVirACurrent34_med60in80 | DIGITAL | IOD_ST2_disk | D335
ST2PMMVirACurrent35_med60in80 | DIGITAL | IOD_ST2_disk | D336
ST2PMMVirACurrent36_med60in80 | DIGITAL | IOD_ST2_disk | D337
ST2PMMVirACurrent37_med60in80 | DIGITAL | IOD_ST2_disk | D338
ST2PMMVirACurrent38_med60in80 | DIGITAL | IOD_ST2_disk | D339
ST2PMMVirACurrent39_med60in80 | DIGITAL | IOD_ST2_disk | D340
ST2PMMVirACurrent40_med60in80 | DIGITAL | IOD_ST2_disk | D341
ST2PMMVirACurrent41_med60in80 | DIGITAL | IOD_ST2_disk | D342
ST2PMMVirACurrent42_med60in80 | DIGITAL | IOD_ST2_disk | D343
ST2PMMVirACurrent43_med60in80 | DIGITAL | IOD_ST2_disk | D344
ST2PMMVirACurrent44_med60in80 | DIGITAL | IOD_ST2_disk | D345
ST2PMMVirACurrent1_nad80 | DIGITAL | IOD_ST2_disk | D346
ST2PMMVirACurrent2_nad80 | DIGITAL | IOD_ST2_disk | D347
ST2PMMVirACurrent3_nad80 | DIGITAL | IOD_ST2_disk | D348
ST2PMMVirACurrent4_nad80 | DIGITAL | IOD_ST2_disk | D349
ST2PMMVirACurrent5_nad80 | DIGITAL | IOD_ST2_disk | D350
ST2PMMVirACurrent6_nad80 | DIGITAL | IOD_ST2_disk | D351
ST2PMMVirACurrent7_nad80 | DIGITAL | IOD_ST2_disk | D352
ST2PMMVirACurrent8_nad80 | DIGITAL | IOD_ST2_disk | D353
ST2PMMVirACurrent9_nad80 | DIGITAL | IOD_ST2_disk | D354
ST2PMMVirACurrent10_nad80 | DIGITAL | IOD_ST2_disk | D355
ST2PMMVirACurrent11_nad80 | DIGITAL | IOD_ST2_disk | D356
ST2PMMVirACurrent12_nad80 | DIGITAL | IOD_ST2_disk | D357
ST2PMMVirACurrent13_nad80 | DIGITAL | IOD_ST2_disk | D358
ST2PMMVirACurrent14_nad80 | DIGITAL | IOD_ST2_disk | D359
ST2PMMVirACurrent15_nad80 | DIGITAL | IOD_ST2_disk | D360
ST2PMMVirACurrent16_nad80 | DIGITAL | IOD_ST2_disk | D361
ST2PMMVirACurrent17_nad80 | DIGITAL | IOD_ST2_disk | D362
ST2PMMVirACurrent18_nad80 | DIGITAL | IOD_ST2_disk | D363
ST2PMMVirACurrent19_nad80 | DIGITAL | IOD_ST2_disk | D364
ST2PMMVirACurrent20_nad80 | DIGITAL | IOD_ST2_disk | D365
ST2PMMVirACurrent21_nad80 | DIGITAL | IOD_ST2_disk | D366
ST2PMMVirACurrent22_nad80 | DIGITAL | IOD_ST2_disk | D367
ST2PMMVirACurrent23_nad80 | DIGITAL | IOD_ST2_disk | D368
ST2PMMVirACurrent24_nad80 | DIGITAL | IOD_ST2_disk | D369
ST2PMMVirACurrent25_nad80 | DIGITAL | IOD_ST2_disk | D370
ST2PMMVirACurrent26_nad80 | DIGITAL | IOD_ST2_disk | D371
ST2PMMVirACurrent27_nad80 | DIGITAL | IOD_ST2_disk | D372
ST2PMMVirACurrent28_nad80 | DIGITAL | IOD_ST2_disk | D373
ST2PMMVirACurrent29_nad80 | DIGITAL | IOD_ST2_disk | D374
ST2PMMVirACurrent30_nad80 | DIGITAL | IOD_ST2_disk | D375
ST2PMMVirACurrent31_nad80 | DIGITAL | IOD_ST2_disk | D376
ST2PMMVirACurrent32_nad80 | DIGITAL | IOD_ST2_disk | D377
ST2PMMVirACurrent33_nad80 | DIGITAL | IOD_ST2_disk | D378
ST2PMMVirACurrent34_nad80 | DIGITAL | IOD_ST2_disk | D379
ST2PMMVirACurrent35_nad80 | DIGITAL | IOD_ST2_disk | D380
ST2PMMVirACurrent36_nad80 | DIGITAL | IOD_ST2_disk | D381
ST2PMMVirACurrent37_nad80 | DIGITAL | IOD_ST2_disk | D382
ST2PMMVirACurrent38_nad80 | DIGITAL | IOD_ST2_disk | D383
ST2PMMVirACurrent39_nad80 | DIGITAL | IOD_ST2_disk | D384
ST2PMMVirACurrent40_nad80 | DIGITAL | IOD_ST2_disk | D385
ST2PMMVirACurrent41_nad80 | DIGITAL | IOD_ST2_disk | D386
ST2PMMVirACurrent42_nad80 | DIGITAL | IOD_ST2_disk | D387
ST2PMMVirACurrent43_nad80 | DIGITAL | IOD_ST2_disk | D388
ST2PMMVirACurrent44_nad80 | DIGITAL | IOD_ST2_disk | D389
ST2PMMPoljeVirATok1_16_nad80 | DIGITAL | IOD_ST2_disk | D400[16]
ST2PMMPoljeVirATok17_32_nad80 | DIGITAL | IOD_ST2_disk | D417[16]
ST2PMMPoljeVirATok33_44_nad80 | DIGITAL | IOD_ST2_disk | D434[16]
ST2PMMPoljeVirBTok1_16_nad80 | DIGITAL | IOD_ST2_disk | D451[16]
ST2PMMPoljeVirBTok17_32_nad80 | DIGITAL | IOD_ST2_disk | D468[16]
ST2PMMPoljeVirBTok33_44_nad80 | DIGITAL | IOD_ST2_disk | D485[16]
ST2PMMPoljeVirATok1_16_med60_80 | DIGITAL | IOD_ST2_disk | D502[16]
ST2PMMPoljeVirATok17_32_med60_80 | DIGITAL | IOD_ST2_disk | D519[16]
ST2PMMPoljeVirATok33_44_med60_80 | DIGITAL | IOD_ST2_disk | D536[16]
ST2PMMPoljeVirBTok1_16_med60_80 | DIGITAL | IOD_ST2_disk | D553[16]
ST2PMMPoljeVirBTok17_32_med60_80 | DIGITAL | IOD_ST2_disk | D570[16]
ST2PMMPoljeVirBTok33_44_med60_80 | DIGITAL | IOD_ST2_disk | D587[16]
ST2PrikaziPMM | DIGITAL | IOD_ST2_disk | D603
ST2PMM_2x63_VirB_zavihek | DIGITAL | IOD_ST2_disk | D604
ST2PMM_2x63_VirA_zavihek | DIGITAL | IOD_ST2_disk | D605
ST2PMMOverCurrentBetw1_VirA | DIGITAL | IOD_ST2_disk | D606
ST2PMMOverCurrentBetw1_VirB | DIGITAL | IOD_ST2_disk | D607
ST2PMMOverCurrentOver1_VirA | DIGITAL | IOD_ST2_disk | D608
ST2PMMOverCurrentOver1_VirB | DIGITAL | IOD_ST2_disk | D609
ST2PMMOverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_ST2_disk | D610
ST2PMMOverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_ST2_disk | D611
ST2PMMOverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_ST2_disk | D612
ST2PMMOverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_ST2_disk | D613
ST2PMM1OverVoltage_Omogoci | DIGITAL | IOD_ST2_disk | D614
ST2ErrComPMM_Omogoci | DIGITAL | IOD_ST2_disk | D615
ST2PMMVirACurrent1_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D616
ST2PMMVirACurrent2_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D617
ST2PMMVirACurrent3_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D618
ST2PMMVirACurrent4_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D619
ST2PMMVirACurrent5_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D620
ST2PMMVirACurrent6_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D621
ST2PMMVirACurrent7_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D622
ST2PMMVirACurrent8_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D623
ST2PMMVirACurrent9_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D624
ST2PMMVirACurrent10_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D625
ST2PMMVirACurrent11_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D626
ST2PMMVirACurrent12_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D627
ST2PMMVirACurrent13_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D628
ST2PMMVirACurrent14_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D629
ST2PMMVirACurrent15_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D630
ST2PMMVirACurrent16_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D631
ST2PMMVirACurrent17_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D632
ST2PMMVirACurrent18_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D633
ST2PMMVirACurrent19_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D634
ST2PMMVirACurrent20_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D635
ST2PMMVirACurrent21_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D636
ST2PMMVirACurrent22_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D637
ST2PMMVirACurrent23_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D638
ST2PMMVirACurrent24_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D639
ST2PMMVirACurrent25_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D640
ST2PMMVirACurrent26_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D641
ST2PMMVirACurrent27_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D642
ST2PMMVirACurrent28_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D643
ST2PMMVirACurrent29_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D644
ST2PMMVirACurrent30_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D645
ST2PMMVirACurrent31_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D646
ST2PMMVirACurrent32_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D647
ST2PMMVirACurrent33_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D648
ST2PMMVirACurrent34_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D649
ST2PMMVirACurrent35_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D650
ST2PMMVirACurrent36_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D651
ST2PMMVirACurrent37_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D652
ST2PMMVirACurrent38_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D653
ST2PMMVirACurrent39_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D654
ST2PMMVirACurrent40_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D655
ST2PMMVirACurrent41_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D656
ST2PMMVirACurrent42_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D657
ST2PMMVirACurrent43_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D658
ST2PMMVirACurrent44_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D659
ST2PMMVirACurrent1_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D660
ST2PMMVirACurrent2_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D661
ST2PMMVirACurrent3_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D662
ST2PMMVirACurrent4_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D663
ST2PMMVirACurrent5_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D664
ST2PMMVirACurrent6_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D665
ST2PMMVirACurrent7_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D666
ST2PMMVirACurrent8_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D667
ST2PMMVirACurrent9_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D668
ST2PMMVirACurrent10_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D669
ST2PMMVirACurrent11_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D670
ST2PMMVirACurrent12_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D671
ST2PMMVirACurrent13_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D672
ST2PMMVirACurrent14_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D673
ST2PMMVirACurrent15_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D674
ST2PMMVirACurrent16_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D675
ST2PMMVirACurrent17_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D676
ST2PMMVirACurrent18_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D677
ST2PMMVirACurrent19_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D678
ST2PMMVirACurrent20_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D679
ST2PMMVirACurrent21_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D680
ST2PMMVirACurrent22_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D681
ST2PMMVirACurrent23_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D682
ST2PMMVirACurrent24_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D683
ST2PMMVirACurrent25_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D684
ST2PMMVirACurrent26_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D685
ST2PMMVirACurrent27_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D686
ST2PMMVirACurrent28_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D687
ST2PMMVirACurrent29_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D688
ST2PMMVirACurrent30_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D689
ST2PMMVirACurrent31_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D690
ST2PMMVirACurrent32_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D691
ST2PMMVirACurrent33_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D692
ST2PMMVirACurrent34_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D693
ST2PMMVirACurrent35_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D694
ST2PMMVirACurrent36_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D695
ST2PMMVirACurrent37_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D696
ST2PMMVirACurrent38_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D697
ST2PMMVirACurrent39_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D698
ST2PMMVirACurrent40_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D699
ST2PMMVirACurrent41_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D700
ST2PMMVirACurrent42_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D701
ST2PMMVirACurrent43_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D702
ST2PMMVirACurrent44_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D703
ST2PMMOverCurrentBetw1_VirB_1 | DIGITAL | IOD_ST2_disk | D704
ST2PMMOverCurrentBetw1_VirA_1 | DIGITAL | IOD_ST2_disk | D705
ST2PMMOverCurrentOver1_VirB_1 | DIGITAL | IOD_ST2_disk | D706
ST2PMMOverCurrentOver1_VirA_1 | DIGITAL | IOD_ST2_disk | D707
ST2PMMOverCurrentBetw1_VirB_2 | DIGITAL | IOD_ST2_disk | D708
ST2PMMOverCurrentBetw1_VirA_2 | DIGITAL | IOD_ST2_disk | D709
ST2PMMOverCurrentBetw1_VirB_3 | DIGITAL | IOD_ST2_disk | D710
ST2PMMOverCurrentBetw1_VirA_3 | DIGITAL | IOD_ST2_disk | D711
ST2PMMOverCurrentOver1_VirB_2 | DIGITAL | IOD_ST2_disk | D712
ST2PMMOverCurrentOver1_VirA_2 | DIGITAL | IOD_ST2_disk | D713
ST2PMMOverCurrentOver1_VirB_3 | DIGITAL | IOD_ST2_disk | D714
ST2PMMOverCurrentOver1_VirA_3 | DIGITAL | IOD_ST2_disk | D715
ST2VsotaVirB_1_16B_med | INT | IOD_ST2_disk | I6
ST2VsotaVirB_17_32B_med | INT | IOD_ST2_disk | I7
ST2VsotaVirB_33_44B_med | INT | IOD_ST2_disk | I8
ST2VsotaVirA_1_16A_med | INT | IOD_ST2_disk | I9
ST2VsotaVirA_17_32A_med | INT | IOD_ST2_disk | I10
ST2VsotaVirA_33_44A_med | INT | IOD_ST2_disk | I11
ST2VsotaVirB_1_16B_nad | INT | IOD_ST2_disk | I12
ST2VsotaVirB_17_32B_nad | INT | IOD_ST2_disk | I13
ST2VsotaVirB_33_44B_nad | INT | IOD_ST2_disk | I14
ST2VsotaVirA_1_16A_nad | INT | IOD_ST2_disk | I15
ST2VsotaVirA_17_32A_nad | INT | IOD_ST2_disk | I16
ST2VsotaVirA_33_44A_nad | INT | IOD_ST2_disk | I17
ST2PMMVirBCurrent1_med60in80 | DIGITAL | IOD_ST2_disk | D716
ST2PMMVirBCurrent2_med60in80 | DIGITAL | IOD_ST2_disk | D717
ST2PMMVirBCurrent3_med60in80 | DIGITAL | IOD_ST2_disk | D718
ST2PMMVirBCurrent4_med60in80 | DIGITAL | IOD_ST2_disk | D719
ST2PMMVirBCurrent5_med60in80 | DIGITAL | IOD_ST2_disk | D720
ST2PMMVirBCurrent6_med60in80 | DIGITAL | IOD_ST2_disk | D721
ST2PMMVirBCurrent7_med60in80 | DIGITAL | IOD_ST2_disk | D722
ST2PMMVirBCurrent8_med60in80 | DIGITAL | IOD_ST2_disk | D723
ST2PMMVirBCurrent9_med60in80 | DIGITAL | IOD_ST2_disk | D724
ST2PMMVirBCurrent10_med60in80 | DIGITAL | IOD_ST2_disk | D725
ST2PMMVirBCurrent11_med60in80 | DIGITAL | IOD_ST2_disk | D726
ST2PMMVirBCurrent12_med60in80 | DIGITAL | IOD_ST2_disk | D727
ST2PMMVirBCurrent13_med60in80 | DIGITAL | IOD_ST2_disk | D728
ST2PMMVirBCurrent14_med60in80 | DIGITAL | IOD_ST2_disk | D729
ST2PMMVirBCurrent15_med60in80 | DIGITAL | IOD_ST2_disk | D730
ST2PMMVirBCurrent16_med60in80 | DIGITAL | IOD_ST2_disk | D731
ST2PMMVirBCurrent17_med60in80 | DIGITAL | IOD_ST2_disk | D732
ST2PMMVirBCurrent18_med60in80 | DIGITAL | IOD_ST2_disk | D733
ST2PMMVirBCurrent19_med60in80 | DIGITAL | IOD_ST2_disk | D734
ST2PMMVirBCurrent20_med60in80 | DIGITAL | IOD_ST2_disk | D735
ST2PMMVirBCurrent21_med60in80 | DIGITAL | IOD_ST2_disk | D736
ST2PMMVirBCurrent22_med60in80 | DIGITAL | IOD_ST2_disk | D737
ST2PMMVirBCurrent23_med60in80 | DIGITAL | IOD_ST2_disk | D738
ST2PMMVirBCurrent24_med60in80 | DIGITAL | IOD_ST2_disk | D739
ST2PMMVirBCurrent25_med60in80 | DIGITAL | IOD_ST2_disk | D740
ST2PMMVirBCurrent26_med60in80 | DIGITAL | IOD_ST2_disk | D741
ST2PMMVirBCurrent27_med60in80 | DIGITAL | IOD_ST2_disk | D742
ST2PMMVirBCurrent28_med60in80 | DIGITAL | IOD_ST2_disk | D743
ST2PMMVirBCurrent29_med60in80 | DIGITAL | IOD_ST2_disk | D744
ST2PMMVirBCurrent30_med60in80 | DIGITAL | IOD_ST2_disk | D745
ST2PMMVirBCurrent31_med60in80 | DIGITAL | IOD_ST2_disk | D746
ST2PMMVirBCurrent32_med60in80 | DIGITAL | IOD_ST2_disk | D747
ST2PMMVirBCurrent33_med60in80 | DIGITAL | IOD_ST2_disk | D748
ST2PMMVirBCurrent34_med60in80 | DIGITAL | IOD_ST2_disk | D749
ST2PMMVirBCurrent35_med60in80 | DIGITAL | IOD_ST2_disk | D750
ST2PMMVirBCurrent36_med60in80 | DIGITAL | IOD_ST2_disk | D751
ST2PMMVirBCurrent37_med60in80 | DIGITAL | IOD_ST2_disk | D752
ST2PMMVirBCurrent38_med60in80 | DIGITAL | IOD_ST2_disk | D753
ST2PMMVirBCurrent39_med60in80 | DIGITAL | IOD_ST2_disk | D754
ST2PMMVirBCurrent40_med60in80 | DIGITAL | IOD_ST2_disk | D755
ST2PMMVirBCurrent41_med60in80 | DIGITAL | IOD_ST2_disk | D756
ST2PMMVirBCurrent42_med60in80 | DIGITAL | IOD_ST2_disk | D757
ST2PMMVirBCurrent43_med60in80 | DIGITAL | IOD_ST2_disk | D758
ST2PMMVirBCurrent44_med60in80 | DIGITAL | IOD_ST2_disk | D759
ST2PMMVirBCurrent1_nad80 | DIGITAL | IOD_ST2_disk | D760
ST2PMMVirBCurrent2_nad80 | DIGITAL | IOD_ST2_disk | D761
ST2PMMVirBCurrent3_nad80 | DIGITAL | IOD_ST2_disk | D762
ST2PMMVirBCurrent4_nad80 | DIGITAL | IOD_ST2_disk | D763
ST2PMMVirBCurrent5_nad80 | DIGITAL | IOD_ST2_disk | D764
ST2PMMVirBCurrent6_nad80 | DIGITAL | IOD_ST2_disk | D765
ST2PMMVirBCurrent7_nad80 | DIGITAL | IOD_ST2_disk | D766
ST2PMMVirBCurrent8_nad80 | DIGITAL | IOD_ST2_disk | D767
ST2PMMVirBCurrent9_nad80 | DIGITAL | IOD_ST2_disk | D768
ST2PMMVirBCurrent10_nad80 | DIGITAL | IOD_ST2_disk | D769
ST2PMMVirBCurrent11_nad80 | DIGITAL | IOD_ST2_disk | D770
ST2PMMVirBCurrent12_nad80 | DIGITAL | IOD_ST2_disk | D771
ST2PMMVirBCurrent13_nad80 | DIGITAL | IOD_ST2_disk | D772
ST2PMMVirBCurrent14_nad80 | DIGITAL | IOD_ST2_disk | D773
ST2PMMVirBCurrent15_nad80 | DIGITAL | IOD_ST2_disk | D774
ST2PMMVirBCurrent16_nad80 | DIGITAL | IOD_ST2_disk | D775
ST2PMMVirBCurrent17_nad80 | DIGITAL | IOD_ST2_disk | D776
ST2PMMVirBCurrent18_nad80 | DIGITAL | IOD_ST2_disk | D777
ST2PMMVirBCurrent19_nad80 | DIGITAL | IOD_ST2_disk | D778
ST2PMMVirBCurrent20_nad80 | DIGITAL | IOD_ST2_disk | D779
ST2PMMVirBCurrent21_nad80 | DIGITAL | IOD_ST2_disk | D780
ST2PMMVirBCurrent22_nad80 | DIGITAL | IOD_ST2_disk | D781
ST2PMMVirBCurrent23_nad80 | DIGITAL | IOD_ST2_disk | D782
ST2PMMVirBCurrent24_nad80 | DIGITAL | IOD_ST2_disk | D783
ST2PMMVirBCurrent25_nad80 | DIGITAL | IOD_ST2_disk | D784
ST2PMMVirBCurrent26_nad80 | DIGITAL | IOD_ST2_disk | D785
ST2PMMVirBCurrent27_nad80 | DIGITAL | IOD_ST2_disk | D786
ST2PMMVirBCurrent28_nad80 | DIGITAL | IOD_ST2_disk | D787
ST2PMMVirBCurrent29_nad80 | DIGITAL | IOD_ST2_disk | D788
ST2PMMVirBCurrent30_nad80 | DIGITAL | IOD_ST2_disk | D789
ST2PMMVirBCurrent31_nad80 | DIGITAL | IOD_ST2_disk | D790
ST2PMMVirBCurrent32_nad80 | DIGITAL | IOD_ST2_disk | D791
ST2PMMVirBCurrent33_nad80 | DIGITAL | IOD_ST2_disk | D792
ST2PMMVirBCurrent34_nad80 | DIGITAL | IOD_ST2_disk | D793
ST2PMMVirBCurrent35_nad80 | DIGITAL | IOD_ST2_disk | D794
ST2PMMVirBCurrent36_nad80 | DIGITAL | IOD_ST2_disk | D795
ST2PMMVirBCurrent37_nad80 | DIGITAL | IOD_ST2_disk | D796
ST2PMMVirBCurrent38_nad80 | DIGITAL | IOD_ST2_disk | D797
ST2PMMVirBCurrent39_nad80 | DIGITAL | IOD_ST2_disk | D798
ST2PMMVirBCurrent40_nad80 | DIGITAL | IOD_ST2_disk | D799
ST2PMMVirBCurrent41_nad80 | DIGITAL | IOD_ST2_disk | D800
ST2PMMVirBCurrent42_nad80 | DIGITAL | IOD_ST2_disk | D801
ST2PMMVirBCurrent43_nad80 | DIGITAL | IOD_ST2_disk | D802
ST2PMMVirBCurrent44_nad80 | DIGITAL | IOD_ST2_disk | D803
ST2PMMVirBCurrent1_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D804
ST2PMMVirBCurrent2_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D805
ST2PMMVirBCurrent3_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D806
ST2PMMVirBCurrent4_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D807
ST2PMMVirBCurrent5_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D808
ST2PMMVirBCurrent6_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D809
ST2PMMVirBCurrent7_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D810
ST2PMMVirBCurrent8_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D811
ST2PMMVirBCurrent9_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D812
ST2PMMVirBCurrent10_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D813
ST2PMMVirBCurrent11_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D814
ST2PMMVirBCurrent12_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D815
ST2PMMVirBCurrent13_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D816
ST2PMMVirBCurrent14_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D817
ST2PMMVirBCurrent15_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D818
ST2PMMVirBCurrent16_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D819
ST2PMMVirBCurrent17_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D820
ST2PMMVirBCurrent18_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D821
ST2PMMVirBCurrent19_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D822
ST2PMMVirBCurrent20_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D823
ST2PMMVirBCurrent21_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D824
ST2PMMVirBCurrent22_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D825
ST2PMMVirBCurrent23_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D826
ST2PMMVirBCurrent24_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D827
ST2PMMVirBCurrent25_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D828
ST2PMMVirBCurrent26_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D829
ST2PMMVirBCurrent27_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D830
ST2PMMVirBCurrent28_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D831
ST2PMMVirBCurrent29_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D832
ST2PMMVirBCurrent30_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D833
ST2PMMVirBCurrent31_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D834
ST2PMMVirBCurrent32_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D835
ST2PMMVirBCurrent33_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D836
ST2PMMVirBCurrent34_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D837
ST2PMMVirBCurrent35_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D838
ST2PMMVirBCurrent36_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D839
ST2PMMVirBCurrent37_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D840
ST2PMMVirBCurrent38_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D841
ST2PMMVirBCurrent39_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D842
ST2PMMVirBCurrent40_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D843
ST2PMMVirBCurrent41_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D844
ST2PMMVirBCurrent42_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D845
ST2PMMVirBCurrent43_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D846
ST2PMMVirBCurrent44_med60in80_Omogoci | DIGITAL | IOD_ST2_disk | D847
ST2PMMVirBCurrent1_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D848
ST2PMMVirBCurrent2_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D849
ST2PMMVirBCurrent3_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D850
ST2PMMVirBCurrent4_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D851
ST2PMMVirBCurrent5_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D852
ST2PMMVirBCurrent6_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D853
ST2PMMVirBCurrent7_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D854
ST2PMMVirBCurrent8_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D855
ST2PMMVirBCurrent9_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D856
ST2PMMVirBCurrent10_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D857
ST2PMMVirBCurrent11_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D858
ST2PMMVirBCurrent12_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D859
ST2PMMVirBCurrent13_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D860
ST2PMMVirBCurrent14_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D861
ST2PMMVirBCurrent15_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D862
ST2PMMVirBCurrent16_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D863
ST2PMMVirBCurrent17_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D864
ST2PMMVirBCurrent18_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D865
ST2PMMVirBCurrent19_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D866
ST2PMMVirBCurrent20_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D867
ST2PMMVirBCurrent21_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D868
ST2PMMVirBCurrent22_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D869
ST2PMMVirBCurrent23_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D870
ST2PMMVirBCurrent24_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D871
ST2PMMVirBCurrent25_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D872
ST2PMMVirBCurrent26_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D873
ST2PMMVirBCurrent27_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D874
ST2PMMVirBCurrent28_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D875
ST2PMMVirBCurrent29_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D876
ST2PMMVirBCurrent30_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D877
ST2PMMVirBCurrent31_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D878
ST2PMMVirBCurrent32_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D879
ST2PMMVirBCurrent33_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D880
ST2PMMVirBCurrent34_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D881
ST2PMMVirBCurrent35_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D882
ST2PMMVirBCurrent36_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D883
ST2PMMVirBCurrent37_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D884
ST2PMMVirBCurrent38_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D885
ST2PMMVirBCurrent39_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D886
ST2PMMVirBCurrent40_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D887
ST2PMMVirBCurrent41_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D888
ST2PMMVirBCurrent42_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D889
ST2PMMVirBCurrent43_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D890
ST2PMMVirBCurrent44_nad80_Omogoci | DIGITAL | IOD_ST2_disk | D891
ST2PLC_SB_IROGSM21_F2_2_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D892
ST2PLC_SB_IROGSM22_F2_2_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D893
ST2DI_SB_IROGSM21_Q0_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D894
ST2DI_SB_IROGSM21_Q0_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D895
ST2DI_SB_IROGSM21_Q11_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D896
ST2DI_SB_IROGSM21_Q11_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D897
ST2DI_SB_IROGSM21_Q12_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D898
ST2DI_SB_IROGSM21_Q12_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D899
ST2DI_SB_IROGSM21_Q13_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D900
ST2DI_SB_IROGSM21_Q13_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D901
ST2DI_SB_IROGSM21_Q14_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D902
ST2DI_SB_IROGSM21_Q14_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D903
ST2DI_SB_IROGSM21_Q15_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D904
ST2DI_SB_IROGSM21_Q15_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D905
ST2DI_SB_IROGSM22_Q0_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D906
ST2DI_SB_IROGSM22_Q0_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D907
ST2DI_SB_IROGSM22_Q11_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D908
ST2DI_SB_IROGSM22_Q11_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D909
ST2DI_SB_IROGSM22_Q12_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D910
ST2DI_SB_IROGSM22_Q12_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D911
ST2DI_SB_IROGSM22_Q13_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D912
ST2DI_SB_IROGSM22_Q13_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D913
ST2DI_SB_IROGSM22_Q14_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D914
ST2DI_SB_IROGSM22_Q14_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D915
ST2DI_SB_IROGSM22_Q15_Vkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D916
ST2DI_SB_IROGSM22_Q15_Izkljucen_Omogoci | DIGITAL | IOD_ST2_disk | D917
ST2NSX1StatusSwitch_Omogoci | INT | IOD_ST2_disk | I18
ST2NSX2StatusSwitch_Omogoci | INT | IOD_ST2_disk | I19
ST2NSX3StatusSwitch_Omogoci | INT | IOD_ST2_disk | I20
ST2NSX4StatusSwitch_Omogoci | INT | IOD_ST2_disk | I21
ST2NSX5StatusSwitch_Omogoci | INT | IOD_ST2_disk | I22
ST2NSX6StatusSwitch_Omogoci | INT | IOD_ST2_disk | I23
ST2DI_SBi_RAZS_AA_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D928
ST2DI_SBi_RAZS_AB_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_ST2_disk | D929
ST2_DanEnergNSX1 | LONG | IOD_ST2_disk | L0[30]
ST2_CasDDanEnergNSX1 | INT | IOD_ST2_disk | I30[30]
ST2_CasMDanEnergNSX1 | INT | IOD_ST2_disk | I60[30]
ST2_TedenEnergNSX1 | LONG | IOD_ST2_disk | L30[30]
ST2_CasDTedenEnergNSX1 | INT | IOD_ST2_disk | I90[30]
ST2_CasMTedenEnergNSX1 | INT | IOD_ST2_disk | I120[30]
ST2_MesecEnergNSX1 | LONG | IOD_ST2_disk | L90[30]
ST2_CasDMesecEnergNSX1 | INT | IOD_ST2_disk | I150[30]
ST2_CasMMesecEnergNSX1 | INT | IOD_ST2_disk | I180[30]
ST2_StSt_DanEnergNSX1 | LONG | IOD_ST2_disk | L121
ST2_StSt_TedenEnergNSX1 | LONG | IOD_ST2_disk | L122
ST2_StSt_MesecEnergNSX1 | LONG | IOD_ST2_disk | L123
ST2_StStCasDDanEnergNSX1 | INT | IOD_ST2_disk | I211
ST2_StStCasMDanEnergNSX1 | INT | IOD_ST2_disk | I212
ST2_StStCasDTedenEnergNSX1 | INT | IOD_ST2_disk | I213
ST2_StStCasMTedenEnergNSX1 | INT | IOD_ST2_disk | I214
ST2_StStCasDMesecEnergNSX1 | INT | IOD_ST2_disk | I215
ST2_StStCasMMesecEnergNSX1 | INT | IOD_ST2_disk | I216
ST2_MaxDnevnaEnergija1 | LONG | IOD_ST2_disk | L124 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija1 | LONG | IOD_ST2_disk | L125 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija1 | LONG | IOD_ST2_disk | L126 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX1 | LONG | IOD_ST2_disk | L127
ST2_Anali_razlika_tedenNSX1 | LONG | IOD_ST2_disk | L128
ST2_Anali_razlika_mesNSX1 | LONG | IOD_ST2_disk | L129
ST2Circ_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1002
ST2Circ_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1003
ST2Circ_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1004
ST2Circ_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1005
ST2Circ_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_ST2_mem | D1006
ST2Circ_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_ST2_mem | D1007
ST2_DanEnergNSX2 | LONG | IOD_ST2_disk | L130[30]
ST2_CasDDanEnergNSX2 | INT | IOD_ST2_disk | I220[30]
ST2_CasMDanEnergNSX2 | INT | IOD_ST2_disk | I250[30]
ST2_TedenEnergNSX2 | LONG | IOD_ST2_disk | L160[30]
ST2_CasDTedenEnergNSX2 | INT | IOD_ST2_disk | I280[30]
ST2_CasMTedenEnergNSX2 | INT | IOD_ST2_disk | I310[30]
ST2_MesecEnergNSX2 | LONG | IOD_ST2_disk | L190[30]
ST2_CasDMesecEnergNSX2 | INT | IOD_ST2_disk | I340[30]
ST2_CasMMesecEnergNSX2 | INT | IOD_ST2_disk | I370[30]
ST2_StSt_DanEnergNSX2 | LONG | IOD_ST2_disk | L221
ST2_StSt_TedenEnergNSX2 | LONG | IOD_ST2_disk | L222
ST2_StSt_MesecEnergNSX2 | LONG | IOD_ST2_disk | L223
ST2_StStCasDDanEnergNSX2 | INT | IOD_ST2_disk | I400
ST2_StStCasMDanEnergNSX2 | INT | IOD_ST2_disk | I401
ST2_StStCasDTedenEnergNSX2 | INT | IOD_ST2_disk | I402
ST2_StStCasMTedenEnergNSX2 | INT | IOD_ST2_disk | I403
ST2_StStCasDMesecEnergNSX2 | INT | IOD_ST2_disk | I404
ST2_StStCasMMesecEnergNSX2 | INT | IOD_ST2_disk | I405
ST2_MaxDnevnaEnergija2 | LONG | IOD_ST2_disk | L224 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija2 | LONG | IOD_ST2_disk | L225 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija2 | LONG | IOD_ST2_disk | L226 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX2 | LONG | IOD_ST2_disk | L227
ST2_Anali_razlika_tedenNSX2 | LONG | IOD_ST2_disk | L228
ST2_Anali_razlika_mesNSX2 | LONG | IOD_ST2_disk | L229
ST2_DanEnergNSX3 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX3 | INT | IOD_ST2_disk | I410[30]
ST2_CasMDanEnergNSX3 | INT | IOD_ST2_disk | I440[30]
ST2_TedenEnergNSX3 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX3 | INT | IOD_ST2_disk | I470[30]
ST2_CasMTedenEnergNSX3 | INT | IOD_ST2_disk | I500[30]
ST2_MesecEnergNSX3 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX3 | INT | IOD_ST2_disk | I530[30]
ST2_CasMMesecEnergNSX3 | INT | IOD_ST2_disk | I560[30]
ST2_StSt_DanEnergNSX3 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX3 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX3 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX3 | INT | IOD_ST2_disk | I590
ST2_StStCasMDanEnergNSX3 | INT | IOD_ST2_disk | I591
ST2_StStCasDTedenEnergNSX3 | INT | IOD_ST2_disk | I592
ST2_StStCasMTedenEnergNSX3 | INT | IOD_ST2_disk | I593
ST2_StStCasDMesecEnergNSX3 | INT | IOD_ST2_disk | I594
ST2_StStCasMMesecEnergNSX3 | INT | IOD_ST2_disk | I595
ST2_MaxDnevnaEnergija3 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija3 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija3 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX3 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX3 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX3 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX4 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX4 | INT | IOD_ST2_disk | I600[30]
ST2_CasMDanEnergNSX4 | INT | IOD_ST2_disk | I630[30]
ST2_TedenEnergNSX4 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX4 | INT | IOD_ST2_disk | I660[30]
ST2_CasMTedenEnergNSX4 | INT | IOD_ST2_disk | I690[30]
ST2_MesecEnergNSX4 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX4 | INT | IOD_ST2_disk | I720[30]
ST2_CasMMesecEnergNSX4 | INT | IOD_ST2_disk | I750[30]
ST2_StSt_DanEnergNSX4 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX4 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX4 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX4 | INT | IOD_ST2_disk | I780
ST2_StStCasMDanEnergNSX4 | INT | IOD_ST2_disk | I781
ST2_StStCasDTedenEnergNSX4 | INT | IOD_ST2_disk | I782
ST2_StStCasMTedenEnergNSX4 | INT | IOD_ST2_disk | I783
ST2_StStCasDMesecEnergNSX4 | INT | IOD_ST2_disk | I784
ST2_StStCasMMesecEnergNSX4 | INT | IOD_ST2_disk | I785
ST2_MaxDnevnaEnergija4 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija4 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija4 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX4 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX4 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX4 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX5 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX5 | INT | IOD_ST2_disk | I790[30]
ST2_CasMDanEnergNSX5 | INT | IOD_ST2_disk | I820[30]
ST2_TedenEnergNSX5 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX5 | INT | IOD_ST2_disk | I850[30]
ST2_CasMTedenEnergNSX5 | INT | IOD_ST2_disk | I880[30]
ST2_MesecEnergNSX5 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX5 | INT | IOD_ST2_disk | I910[30]
ST2_CasMMesecEnergNSX5 | INT | IOD_ST2_disk | I940[30]
ST2_StSt_DanEnergNSX5 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX5 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX5 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX5 | INT | IOD_ST2_disk | I970
ST2_StStCasMDanEnergNSX5 | INT | IOD_ST2_disk | I971
ST2_StStCasDTedenEnergNSX5 | INT | IOD_ST2_disk | I972
ST2_StStCasMTedenEnergNSX5 | INT | IOD_ST2_disk | I973
ST2_StStCasDMesecEnergNSX5 | INT | IOD_ST2_disk | I974
ST2_StStCasMMesecEnergNSX5 | INT | IOD_ST2_disk | I975
ST2_MaxDnevnaEnergija5 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija5 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija5 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX5 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX5 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX5 | LONG | IOD_ST2_disk | L329
ST2_DanEnergNSX6 | LONG | IOD_ST2_disk | L230[30]
ST2_CasDDanEnergNSX6 | INT | IOD_ST2_disk | I980[30]
ST2_CasMDanEnergNSX6 | INT | IOD_ST2_disk | I1010[30]
ST2_TedenEnergNSX6 | LONG | IOD_ST2_disk | L260[30]
ST2_CasDTedenEnergNSX6 | INT | IOD_ST2_disk | I1040[30]
ST2_CasMTedenEnergNSX6 | INT | IOD_ST2_disk | I1070[30]
ST2_MesecEnergNSX6 | LONG | IOD_ST2_disk | L290[30]
ST2_CasDMesecEnergNSX6 | INT | IOD_ST2_disk | I1100[30]
ST2_CasMMesecEnergNSX6 | INT | IOD_ST2_disk | I1130[30]
ST2_StSt_DanEnergNSX6 | LONG | IOD_ST2_disk | L321
ST2_StSt_TedenEnergNSX6 | LONG | IOD_ST2_disk | L322
ST2_StSt_MesecEnergNSX6 | LONG | IOD_ST2_disk | L323
ST2_StStCasDDanEnergNSX6 | INT | IOD_ST2_disk | I1160
ST2_StStCasMDanEnergNSX6 | INT | IOD_ST2_disk | I1161
ST2_StStCasDTedenEnergNSX6 | INT | IOD_ST2_disk | I1162
ST2_StStCasMTedenEnergNSX6 | INT | IOD_ST2_disk | I1163
ST2_StStCasDMesecEnergNSX6 | INT | IOD_ST2_disk | I1164
ST2_StStCasMMesecEnergNSX6 | INT | IOD_ST2_disk | I1165
ST2_MaxDnevnaEnergija6 | LONG | IOD_ST2_disk | L324 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxMesecnaEnergija6 | LONG | IOD_ST2_disk | L325 | 0 | 9999999 | 0 | 9999999 | #######
ST2_MaxTedenskaEnergija6 | LONG | IOD_ST2_disk | L326 | 0 | 9999999 | 0 | 9999999 | #######
ST2_Anali_razlika_dnevnaNSX6 | LONG | IOD_ST2_disk | L327
ST2_Anali_razlika_tedenNSX6 | LONG | IOD_ST2_disk | L328
ST2_Anali_razlika_mesNSX6 | LONG | IOD_ST2_disk | L329
ST2DI_SB_IROGSM21_Q13_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D930
ST2DI_SB_IROGSM21_Q14_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D931
ST2DI_SB_IROGSM21_Q15_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D932
ST2DI_SB_IROGSM22_Q13_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D933
ST2DI_SB_IROGSM22_Q14_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D934
ST2DI_SB_IROGSM22_Q15_Izpad_Omogoci | DIGITAL | IOD_ST2_disk | D935

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC) | mod_Write_dWord2(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Branje ULONG*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*) | (*Pisanje ULONG*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=Circ_Vpis_Dnevne_energija_scada1; | mind[0]:=DateTime.Dan; | mind[8000]:=NSX[1].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok1,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=7000); |  | 0:Circ_Vpis_Dnevne_energija_scada1:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 8000:NSX[1].StatusSwitch:=Word_01; |  | 4001:iPMM_VirA_Tok1:=Real_0; | 7000:Date_Time[0]:=String_0;
mind_bool[1]:=Circ_Vpis_Dnevne_energija_scada2; | mind[1]:=DateTime.Leto; | mind[8001]:=NSX[2].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok10,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=7015); |  | 1:Circ_Vpis_Dnevne_energija_scada2:=Bit_0; | 1:DateTime.Leto:=Byte_0; | 8001:NSX[2].StatusSwitch:=Word_01; |  | 4003:iPMM_VirA_Tok10:=Real_0; | 7015:Date_Time[1]:=String_0;
mind_bool[2]:=Circ_Vpis_Mesecna_energija_scada1; | mind[2]:=DateTime.Leto2; | mind[8002]:=NSX[3].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok11,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=7030); |  | 2:Circ_Vpis_Mesecna_energija_scada1:=Bit_0; | 2:DateTime.Leto2:=Word_01; | 8002:NSX[3].StatusSwitch:=Word_01; |  | 4005:iPMM_VirA_Tok11:=Real_0; | 7030:Date_Time[2]:=String_0;
mind_bool[3]:=Circ_Vpis_Mesecna_energija_scada2; | mind[3]:=DateTime.Mesec; | mind[8003]:=NSX[4].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok12,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=7045); |  | 3:Circ_Vpis_Mesecna_energija_scada2:=Bit_0; | 3:DateTime.Mesec:=Byte_0; | 8003:NSX[4].StatusSwitch:=Word_01; |  | 4007:iPMM_VirA_Tok12:=Real_0; | 7045:Date_Time[3]:=String_0;
mind_bool[4]:=Circ_Vpis_Tedenska_energija_scada1; | mind[4]:=DateTime.Minuta; | mind[8004]:=NSX[5].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok13,lo:=4008,hi:=4009); | Read_String(sVar:=kom_nast_cas_izpada,start:=7060); |  | 4:Circ_Vpis_Tedenska_energija_scada1:=Bit_0; | 4:DateTime.Minuta:=Byte_0; | 8004:NSX[5].StatusSwitch:=Word_01; |  | 4009:iPMM_VirA_Tok13:=Real_0; | 7060:kom_nast_cas_izpada:=String_0;
mind_bool[5]:=Circ_Vpis_Tedenska_energija_scada2; | mind[5]:=DateTime.PLC_Dan; | mind[8005]:=NSX[6].StatusSwitch; |  | Read_Real(rVar:=iPMM_VirA_Tok14,lo:=4010,hi:=4011); | Read_String(sVar:=UserCurrentName,start:=7075); |  | 5:Circ_Vpis_Tedenska_energija_scada2:=Bit_0; | 5:DateTime.PLC_Dan:=Byte_0; | 8005:NSX[6].StatusSwitch:=Word_01; |  | 4011:iPMM_VirA_Tok14:=Real_0; | 7075:UserCurrentName:=String_0;
mind_bool[6]:=ComError; | mind[6]:=DateTime.PLC_DanVTednu; | mind[8006]:=PMM.VirAAlarmPhase.C01_16_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok15,lo:=4012,hi:=4013); | Read_String(sVar:=UserDisplay,start:=7090); |  | 6:ComError:=Bit_0; | 6:DateTime.PLC_DanVTednu:=Byte_0; | 8006:PMM.VirAAlarmPhase.C01_16_60to80:=Word_01; |  | 4013:iPMM_VirA_Tok15:=Real_0; | 7090:UserDisplay:=String_0;
mind_bool[7]:=ComSCADA; | mind[7]:=DateTime.PLC_Leto; | mind[8007]:=PMM.VirAAlarmPhase.C01_16_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok16,lo:=4014,hi:=4015); |  |  | 7:ComSCADA:=Bit_0; | 7:DateTime.PLC_Leto:=Byte_0; | 8007:PMM.VirAAlarmPhase.C01_16_over80:=Word_01; |  | 4015:iPMM_VirA_Tok16:=Real_0;
mind_bool[8]:=ComSCADA1; | mind[8]:=DateTime.PLC_Mesec; | mind[8008]:=PMM.VirAAlarmPhase.C17_32_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok17,lo:=4016,hi:=4017); |  |  | 8:ComSCADA1:=Bit_0; | 8:DateTime.PLC_Mesec:=Byte_0; | 8008:PMM.VirAAlarmPhase.C17_32_60to80:=Word_01; |  | 4017:iPMM_VirA_Tok17:=Real_0;
mind_bool[9]:=ComSCADA2; | mind[9]:=DateTime.PLC_Minuta; | mind[8009]:=PMM.VirAAlarmPhase.C17_32_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok18,lo:=4018,hi:=4019); |  |  | 9:ComSCADA2:=Bit_0; | 9:DateTime.PLC_Minuta:=Byte_0; | 8009:PMM.VirAAlarmPhase.C17_32_over80:=Word_01; |  | 4019:iPMM_VirA_Tok18:=Real_0;
mind_bool[10]:=ComSCADA3; | mind[10]:=DateTime.PLC_Sekunda; | mind[8010]:=PMM.VirAAlarmPhase.C33_44_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok19,lo:=4020,hi:=4021); |  |  | 10:ComSCADA3:=Bit_0; | 10:DateTime.PLC_Sekunda:=Byte_0; | 8010:PMM.VirAAlarmPhase.C33_44_60to80:=Word_01; |  | 4021:iPMM_VirA_Tok19:=Real_0;
mind_bool[11]:=DI2_I10_Rezerva3; | mind[11]:=DateTime.PLC_Ura; | mind[8011]:=PMM.VirAAlarmPhase.C33_44_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok2,lo:=4022,hi:=4023); |  |  | 11:DI2_I10_Rezerva3:=Bit_0; | 11:DateTime.PLC_Ura:=Byte_0; | 8011:PMM.VirAAlarmPhase.C33_44_over80:=Word_01; |  | 4023:iPMM_VirA_Tok2:=Real_0;
mind_bool[12]:=DI2_I11_Rezerva4; | mind[12]:=DateTime.Sekunda; | mind[8012]:=PMM.VirBAlarmPhase.C01_16_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok20,lo:=4024,hi:=4025); |  |  | 12:DI2_I11_Rezerva4:=Bit_0; | 12:DateTime.Sekunda:=Byte_0; | 8012:PMM.VirBAlarmPhase.C01_16_60to80:=Word_01; |  | 4025:iPMM_VirA_Tok20:=Real_0;
mind_bool[13]:=DI2_I12_Rezerva5; | mind[13]:=DateTime.Ura; | mind[8013]:=PMM.VirBAlarmPhase.C01_16_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok21,lo:=4026,hi:=4027); |  |  | 13:DI2_I12_Rezerva5:=Bit_0; | 13:DateTime.Ura:=Byte_0; | 8013:PMM.VirBAlarmPhase.C01_16_over80:=Word_01; |  | 4027:iPMM_VirA_Tok21:=Real_0;
mind_bool[14]:=DI2_I13_Rezerva6; | mind[14]:=ErrorComPMM[1].Status; | mind[8014]:=PMM.VirBAlarmPhase.C17_32_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok22,lo:=4028,hi:=4029); |  |  | 14:DI2_I13_Rezerva6:=Bit_0; | 14:ErrorComPMM[1].Status:=Word_01; | 8014:PMM.VirBAlarmPhase.C17_32_60to80:=Word_01; |  | 4029:iPMM_VirA_Tok22:=Real_0;
mind_bool[15]:=DI2_I8_Rezerva1; | mind[15]:=HIA1_vlaga_s; | mind[8015]:=PMM.VirBAlarmPhase.C17_32_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok23,lo:=4030,hi:=4031); |  |  | 15:DI2_I8_Rezerva1:=Bit_0; | 15:HIA1_vlaga_s:=Word_01; | 8015:PMM.VirBAlarmPhase.C17_32_over80:=Word_01; |  | 4031:iPMM_VirA_Tok23:=Real_0;
mind_bool[16]:=DI2_I9_Rezerva2; | mind[16]:=HIA2_vlaga_s; | mind[8016]:=PMM.VirBAlarmPhase.C33_44_60to80; |  | Read_Real(rVar:=iPMM_VirA_Tok24,lo:=4032,hi:=4033); |  |  | 16:DI2_I9_Rezerva2:=Bit_0; | 16:HIA2_vlaga_s:=Word_01; | 8016:PMM.VirBAlarmPhase.C33_44_60to80:=Word_01; |  | 4033:iPMM_VirA_Tok24:=Real_0;
mind_bool[17]:=DI_SB_IROGSM21_Q0_Izkljucen; | mind[17]:=HIA3_vlaga_s; | mind[8017]:=PMM.VirBAlarmPhase.C33_44_over80; |  | Read_Real(rVar:=iPMM_VirA_Tok25,lo:=4034,hi:=4035); |  |  | 17:DI_SB_IROGSM21_Q0_Izkljucen:=Bit_0; | 17:HIA3_vlaga_s:=Word_01; | 8017:PMM.VirBAlarmPhase.C33_44_over80:=Word_01; |  | 4035:iPMM_VirA_Tok25:=Real_0;
mind_bool[18]:=DI_SB_IROGSM21_Q0_Vkljucen; | mind[18]:=HIA4_vlaga_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok26,lo:=4036,hi:=4037); |  |  | 18:DI_SB_IROGSM21_Q0_Vkljucen:=Bit_0; | 18:HIA4_vlaga_s:=Word_01; |  |  | 4037:iPMM_VirA_Tok26:=Real_0;
mind_bool[19]:=DI_SB_IROGSM21_Q11_Izkljucen; | mind[19]:=HIA5_vlaga_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok27,lo:=4038,hi:=4039); |  |  | 19:DI_SB_IROGSM21_Q11_Izkljucen:=Bit_0; | 19:HIA5_vlaga_s:=Word_01; |  |  | 4039:iPMM_VirA_Tok27:=Real_0;
mind_bool[20]:=DI_SB_IROGSM21_Q11_Vkljucen; | mind[20]:=HIA6_vlaga_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok28,lo:=4040,hi:=4041); |  |  | 20:DI_SB_IROGSM21_Q11_Vkljucen:=Bit_0; | 20:HIA6_vlaga_s:=Word_01; |  |  | 4041:iPMM_VirA_Tok28:=Real_0;
mind_bool[21]:=DI_SB_IROGSM21_Q12_Izkljucen; | mind[21]:=HIA7_vlaga_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok29,lo:=4042,hi:=4043); |  |  | 21:DI_SB_IROGSM21_Q12_Izkljucen:=Bit_0; | 21:HIA7_vlaga_s:=Word_01; |  |  | 4043:iPMM_VirA_Tok29:=Real_0;
mind_bool[22]:=DI_SB_IROGSM21_Q12_Vkljucen; | mind[22]:=HIA8_vlaga_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok3,lo:=4044,hi:=4045); |  |  | 22:DI_SB_IROGSM21_Q12_Vkljucen:=Bit_0; | 22:HIA8_vlaga_s:=Word_01; |  |  | 4045:iPMM_VirA_Tok3:=Real_0;
mind_bool[23]:=DI_SB_IROGSM21_Q13_Izpad; | mind[23]:=TIA1_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok30,lo:=4046,hi:=4047); |  |  | 23:DI_SB_IROGSM21_Q13_Izpad:=Bit_0; | 23:TIA1_alarm:=Word_01; |  |  | 4047:iPMM_VirA_Tok30:=Real_0;
mind_bool[24]:=DI_SB_IROGSM21_Q13_Vkljucen; | mind[24]:=TIA1_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok31,lo:=4048,hi:=4049); |  |  | 24:DI_SB_IROGSM21_Q13_Vkljucen:=Bit_0; | 24:TIA1_temp_s:=Word_01; |  |  | 4049:iPMM_VirA_Tok31:=Real_0;
mind_bool[25]:=DI_SB_IROGSM21_Q14_Izpad; | mind[25]:=TIA2_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok32,lo:=4050,hi:=4051); |  |  | 25:DI_SB_IROGSM21_Q14_Izpad:=Bit_0; | 25:TIA2_alarm:=Word_01; |  |  | 4051:iPMM_VirA_Tok32:=Real_0;
mind_bool[26]:=DI_SB_IROGSM21_Q14_Vkljucen; | mind[26]:=TIA2_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok33,lo:=4052,hi:=4053); |  |  | 26:DI_SB_IROGSM21_Q14_Vkljucen:=Bit_0; | 26:TIA2_temp_s:=Word_01; |  |  | 4053:iPMM_VirA_Tok33:=Real_0;
mind_bool[27]:=DI_SB_IROGSM21_Q15_Izpad; | mind[27]:=TIA3_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok34,lo:=4054,hi:=4055); |  |  | 27:DI_SB_IROGSM21_Q15_Izpad:=Bit_0; | 27:TIA3_alarm:=Word_01; |  |  | 4055:iPMM_VirA_Tok34:=Real_0;
mind_bool[28]:=DI_SB_IROGSM21_Q15_Vkljucen; | mind[28]:=TIA3_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok35,lo:=4056,hi:=4057); |  |  | 28:DI_SB_IROGSM21_Q15_Vkljucen:=Bit_0; | 28:TIA3_temp_s:=Word_01; |  |  | 4057:iPMM_VirA_Tok35:=Real_0;
mind_bool[29]:=DI_SB_IROGSM21_SkupnaNapaka; | mind[29]:=TIA4_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok36,lo:=4058,hi:=4059); |  |  | 29:DI_SB_IROGSM21_SkupnaNapaka:=Bit_0; | 29:TIA4_alarm:=Word_01; |  |  | 4059:iPMM_VirA_Tok36:=Real_0;
mind_bool[30]:=DI_SB_IROGSM22_Q0_Izkljucen; | mind[30]:=TIA4_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok37,lo:=4060,hi:=4061); |  |  | 30:DI_SB_IROGSM22_Q0_Izkljucen:=Bit_0; | 30:TIA4_temp_s:=Word_01; |  |  | 4061:iPMM_VirA_Tok37:=Real_0;
mind_bool[31]:=DI_SB_IROGSM22_Q0_Vkljucen; | mind[31]:=TIA5_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok38,lo:=4062,hi:=4063); |  |  | 31:DI_SB_IROGSM22_Q0_Vkljucen:=Bit_0; | 31:TIA5_alarm:=Word_01; |  |  | 4063:iPMM_VirA_Tok38:=Real_0;
mind_bool[32]:=DI_SB_IROGSM22_Q11_Izkljucen; | mind[32]:=TIA5_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok39,lo:=4064,hi:=4065); |  |  | 32:DI_SB_IROGSM22_Q11_Izkljucen:=Bit_0; | 32:TIA5_temp_s:=Word_01; |  |  | 4065:iPMM_VirA_Tok39:=Real_0;
mind_bool[33]:=DI_SB_IROGSM22_Q11_Vkljucen; | mind[33]:=TIA6_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok4,lo:=4066,hi:=4067); |  |  | 33:DI_SB_IROGSM22_Q11_Vkljucen:=Bit_0; | 33:TIA6_alarm:=Word_01; |  |  | 4067:iPMM_VirA_Tok4:=Real_0;
mind_bool[34]:=DI_SB_IROGSM22_Q12_Izkljucen; | mind[34]:=TIA6_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok40,lo:=4068,hi:=4069); |  |  | 34:DI_SB_IROGSM22_Q12_Izkljucen:=Bit_0; | 34:TIA6_temp_s:=Word_01; |  |  | 4069:iPMM_VirA_Tok40:=Real_0;
mind_bool[35]:=DI_SB_IROGSM22_Q12_Vkljucen; | mind[35]:=TIA7_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok41,lo:=4070,hi:=4071); |  |  | 35:DI_SB_IROGSM22_Q12_Vkljucen:=Bit_0; | 35:TIA7_alarm:=Word_01; |  |  | 4071:iPMM_VirA_Tok41:=Real_0;
mind_bool[36]:=DI_SB_IROGSM22_Q13_Izpad; | mind[36]:=TIA7_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok42,lo:=4072,hi:=4073); |  |  | 36:DI_SB_IROGSM22_Q13_Izpad:=Bit_0; | 36:TIA7_temp_s:=Word_01; |  |  | 4073:iPMM_VirA_Tok42:=Real_0;
mind_bool[37]:=DI_SB_IROGSM22_Q13_Vkljucen; | mind[37]:=TIA8_alarm; |  |  | Read_Real(rVar:=iPMM_VirA_Tok43,lo:=4074,hi:=4075); |  |  | 37:DI_SB_IROGSM22_Q13_Vkljucen:=Bit_0; | 37:TIA8_alarm:=Word_01; |  |  | 4075:iPMM_VirA_Tok43:=Real_0;
mind_bool[38]:=DI_SB_IROGSM22_Q14_Izpad; | mind[38]:=TIA8_temp_s; |  |  | Read_Real(rVar:=iPMM_VirA_Tok44,lo:=4076,hi:=4077); |  |  | 38:DI_SB_IROGSM22_Q14_Izpad:=Bit_0; | 38:TIA8_temp_s:=Word_01; |  |  | 4077:iPMM_VirA_Tok44:=Real_0;
mind_bool[39]:=DI_SB_IROGSM22_Q14_Vkljucen; | mind[39]:=UserCurrentLevel; |  |  | Read_Real(rVar:=iPMM_VirA_Tok5,lo:=4078,hi:=4079); |  |  | 39:DI_SB_IROGSM22_Q14_Vkljucen:=Bit_0; | 39:UserCurrentLevel:=Byte_0; |  |  | 4079:iPMM_VirA_Tok5:=Real_0;
mind_bool[40]:=DI_SB_IROGSM22_Q15_Izpad; |  |  |  | Read_Real(rVar:=iPMM_VirA_Tok6,lo:=4080,hi:=4081); |  |  | 40:DI_SB_IROGSM22_Q15_Izpad:=Bit_0; |  |  |  | 4081:iPMM_VirA_Tok6:=Real_0;
mind_bool[41]:=DI_SB_IROGSM22_Q15_Vkljucen; |  |  |  | Read_Real(rVar:=iPMM_VirA_Tok7,lo:=4082,hi:=4083); |  |  | 41:DI_SB_IROGSM22_Q15_Vkljucen:=Bit_0; |  |  |  | 4083:iPMM_VirA_Tok7:=Real_0;
mind_bool[42]:=DI_SB_IROGSM22_SkupnaNapaka; |  |  |  | Read_Real(rVar:=iPMM_VirA_Tok8,lo:=4084,hi:=4085); |  |  | 42:DI_SB_IROGSM22_SkupnaNapaka:=Bit_0; |  |  |  | 4085:iPMM_VirA_Tok8:=Real_0;
mind_bool[43]:=DI_SBi_RAZS_AA_Izolacija_NOT_OK; |  |  |  | Read_Real(rVar:=iPMM_VirA_Tok9,lo:=4086,hi:=4087); |  |  | 43:DI_SBi_RAZS_AA_Izolacija_NOT_OK:=Bit_0; |  |  |  | 4087:iPMM_VirA_Tok9:=Real_0;
mind_bool[44]:=DI_SBi_RAZS_AB_Izolacija_NOT_OK; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok1,lo:=4088,hi:=4089); |  |  | 44:DI_SBi_RAZS_AB_Izolacija_NOT_OK:=Bit_0; |  |  |  | 4089:iPMM_VirB_Tok1:=Real_0;
mind_bool[45]:=ErrComNSX[1]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok10,lo:=4090,hi:=4091); |  |  | 45:ErrComNSX[1]:=Bit_0; |  |  |  | 4091:iPMM_VirB_Tok10:=Real_0;
mind_bool[46]:=ErrComNSX[2]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok11,lo:=4092,hi:=4093); |  |  | 46:ErrComNSX[2]:=Bit_0; |  |  |  | 4093:iPMM_VirB_Tok11:=Real_0;
mind_bool[47]:=ErrComNSX[3]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok12,lo:=4094,hi:=4095); |  |  | 47:ErrComNSX[3]:=Bit_0; |  |  |  | 4095:iPMM_VirB_Tok12:=Real_0;
mind_bool[48]:=ErrComNSX[4]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok13,lo:=4096,hi:=4097); |  |  | 48:ErrComNSX[4]:=Bit_0; |  |  |  | 4097:iPMM_VirB_Tok13:=Real_0;
mind_bool[49]:=ErrComNSX[5]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok14,lo:=4098,hi:=4099); |  |  | 49:ErrComNSX[5]:=Bit_0; |  |  |  | 4099:iPMM_VirB_Tok14:=Real_0;
mind_bool[50]:=ErrComNSX[6]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok15,lo:=4100,hi:=4101); |  |  | 50:ErrComNSX[6]:=Bit_0; |  |  |  | 4101:iPMM_VirB_Tok15:=Real_0;
mind_bool[51]:=ErrComPMM[1]; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok16,lo:=4102,hi:=4103); |  |  | 51:ErrComPMM[1]:=Bit_0; |  |  |  | 4103:iPMM_VirB_Tok16:=Real_0;
mind_bool[52]:=ErrComPort2; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok17,lo:=4104,hi:=4105); |  |  | 52:ErrComPort2:=Bit_0; |  |  |  | 4105:iPMM_VirB_Tok17:=Real_0;
mind_bool[53]:=ErrorComPMM[1].Error; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok18,lo:=4106,hi:=4107); |  |  | 53:ErrorComPMM[1].Error:=Bit_0; |  |  |  | 4107:iPMM_VirB_Tok18:=Real_0;
mind_bool[54]:=napaka_kom_panel; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok19,lo:=4108,hi:=4109); |  |  | 54:napaka_kom_panel:=Bit_0; |  |  |  | 4109:iPMM_VirB_Tok19:=Real_0;
mind_bool[55]:=napaka_kom_scada; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok2,lo:=4110,hi:=4111); |  |  | 55:napaka_kom_scada:=Bit_0; |  |  |  | 4111:iPMM_VirB_Tok2:=Real_0;
mind_bool[56]:=napaka_kom_scada2; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok20,lo:=4112,hi:=4113); |  |  | 56:napaka_kom_scada2:=Bit_0; |  |  |  | 4113:iPMM_VirB_Tok20:=Real_0;
mind_bool[57]:=NapakaSenzorSkupno; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok21,lo:=4114,hi:=4115); |  |  | 57:NapakaSenzorSkupno:=Bit_0; |  |  |  | 4115:iPMM_VirB_Tok21:=Real_0;
mind_bool[58]:=NapakaSenzorVlagaHIA1; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok22,lo:=4116,hi:=4117); |  |  | 58:NapakaSenzorVlagaHIA1:=Bit_0; |  |  |  | 4117:iPMM_VirB_Tok22:=Real_0;
mind_bool[59]:=NapakaSenzorVlagaHIA2; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok23,lo:=4118,hi:=4119); |  |  | 59:NapakaSenzorVlagaHIA2:=Bit_0; |  |  |  | 4119:iPMM_VirB_Tok23:=Real_0;
mind_bool[60]:=NapakaSenzorVlagaHIA3; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok24,lo:=4120,hi:=4121); |  |  | 60:NapakaSenzorVlagaHIA3:=Bit_0; |  |  |  | 4121:iPMM_VirB_Tok24:=Real_0;
mind_bool[61]:=NapakaSenzorVlagaHIA4; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok25,lo:=4122,hi:=4123); |  |  | 61:NapakaSenzorVlagaHIA4:=Bit_0; |  |  |  | 4123:iPMM_VirB_Tok25:=Real_0;
mind_bool[62]:=NapakaSenzorVlagaHIA5; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok26,lo:=4124,hi:=4125); |  |  | 62:NapakaSenzorVlagaHIA5:=Bit_0; |  |  |  | 4125:iPMM_VirB_Tok26:=Real_0;
mind_bool[63]:=NapakaSenzorVlagaHIA6; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok27,lo:=4126,hi:=4127); |  |  | 63:NapakaSenzorVlagaHIA6:=Bit_0; |  |  |  | 4127:iPMM_VirB_Tok27:=Real_0;
mind_bool[64]:=NapakaSenzorVlagaHIA7; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok28,lo:=4128,hi:=4129); |  |  | 64:NapakaSenzorVlagaHIA7:=Bit_0; |  |  |  | 4129:iPMM_VirB_Tok28:=Real_0;
mind_bool[65]:=NapakaSenzorVlagaHIA8; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok29,lo:=4130,hi:=4131); |  |  | 65:NapakaSenzorVlagaHIA8:=Bit_0; |  |  |  | 4131:iPMM_VirB_Tok29:=Real_0;
mind_bool[66]:=NapakaTSTempTIA1; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok3,lo:=4132,hi:=4133); |  |  | 66:NapakaTSTempTIA1:=Bit_0; |  |  |  | 4133:iPMM_VirB_Tok3:=Real_0;
mind_bool[67]:=NapakaTSTempTIA2; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok30,lo:=4134,hi:=4135); |  |  | 67:NapakaTSTempTIA2:=Bit_0; |  |  |  | 4135:iPMM_VirB_Tok30:=Real_0;
mind_bool[68]:=NapakaTSTempTIA3; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok31,lo:=4136,hi:=4137); |  |  | 68:NapakaTSTempTIA3:=Bit_0; |  |  |  | 4137:iPMM_VirB_Tok31:=Real_0;
mind_bool[69]:=NapakaTSTempTIA4; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok32,lo:=4138,hi:=4139); |  |  | 69:NapakaTSTempTIA4:=Bit_0; |  |  |  | 4139:iPMM_VirB_Tok32:=Real_0;
mind_bool[70]:=NapakaTSTempTIA5; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok33,lo:=4140,hi:=4141); |  |  | 70:NapakaTSTempTIA5:=Bit_0; |  |  |  | 4141:iPMM_VirB_Tok33:=Real_0;
mind_bool[71]:=NapakaTSTempTIA6; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok34,lo:=4142,hi:=4143); |  |  | 71:NapakaTSTempTIA6:=Bit_0; |  |  |  | 4143:iPMM_VirB_Tok34:=Real_0;
mind_bool[72]:=NapakaTSTempTIA7; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok35,lo:=4144,hi:=4145); |  |  | 72:NapakaTSTempTIA7:=Bit_0; |  |  |  | 4145:iPMM_VirB_Tok35:=Real_0;
mind_bool[73]:=NapakaTSTempTIA8; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok36,lo:=4146,hi:=4147); |  |  | 73:NapakaTSTempTIA8:=Bit_0; |  |  |  | 4147:iPMM_VirB_Tok36:=Real_0;
mind_bool[74]:=NSX[1].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok37,lo:=4148,hi:=4149); |  |  | 74:NSX[1].ResetMAX:=Bit_0; |  |  |  | 4149:iPMM_VirB_Tok37:=Real_0;
mind_bool[75]:=NSX[1].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok38,lo:=4150,hi:=4151); |  |  | 75:NSX[1].ResetMIN:=Bit_0; |  |  |  | 4151:iPMM_VirB_Tok38:=Real_0;
mind_bool[76]:=NSX[2].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok39,lo:=4152,hi:=4153); |  |  | 76:NSX[2].ResetMAX:=Bit_0; |  |  |  | 4153:iPMM_VirB_Tok39:=Real_0;
mind_bool[77]:=NSX[2].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok4,lo:=4154,hi:=4155); |  |  | 77:NSX[2].ResetMIN:=Bit_0; |  |  |  | 4155:iPMM_VirB_Tok4:=Real_0;
mind_bool[78]:=NSX[3].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok40,lo:=4156,hi:=4157); |  |  | 78:NSX[3].ResetMAX:=Bit_0; |  |  |  | 4157:iPMM_VirB_Tok40:=Real_0;
mind_bool[79]:=NSX[3].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok41,lo:=4158,hi:=4159); |  |  | 79:NSX[3].ResetMIN:=Bit_0; |  |  |  | 4159:iPMM_VirB_Tok41:=Real_0;
mind_bool[80]:=NSX[4].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok42,lo:=4160,hi:=4161); |  |  | 80:NSX[4].ResetMAX:=Bit_0; |  |  |  | 4161:iPMM_VirB_Tok42:=Real_0;
mind_bool[81]:=NSX[4].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok43,lo:=4162,hi:=4163); |  |  | 81:NSX[4].ResetMIN:=Bit_0; |  |  |  | 4163:iPMM_VirB_Tok43:=Real_0;
mind_bool[82]:=NSX[5].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok44,lo:=4164,hi:=4165); |  |  | 82:NSX[5].ResetMAX:=Bit_0; |  |  |  | 4165:iPMM_VirB_Tok44:=Real_0;
mind_bool[83]:=NSX[5].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok5,lo:=4166,hi:=4167); |  |  | 83:NSX[5].ResetMIN:=Bit_0; |  |  |  | 4167:iPMM_VirB_Tok5:=Real_0;
mind_bool[84]:=NSX[6].ResetMAX; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok6,lo:=4168,hi:=4169); |  |  | 84:NSX[6].ResetMAX:=Bit_0; |  |  |  | 4169:iPMM_VirB_Tok6:=Real_0;
mind_bool[85]:=NSX[6].ResetMIN; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok7,lo:=4170,hi:=4171); |  |  | 85:NSX[6].ResetMIN:=Bit_0; |  |  |  | 4171:iPMM_VirB_Tok7:=Real_0;
mind_bool[86]:=PLC_SB_IROGSM21_F2_2_NOT_OK; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok8,lo:=4172,hi:=4173); |  |  | 86:PLC_SB_IROGSM21_F2_2_NOT_OK:=Bit_0; |  |  |  | 4173:iPMM_VirB_Tok8:=Real_0;
mind_bool[87]:=PLC_SB_IROGSM22_F2_2_NOT_OK; |  |  |  | Read_Real(rVar:=iPMM_VirB_Tok9,lo:=4174,hi:=4175); |  |  | 87:PLC_SB_IROGSM22_F2_2_NOT_OK:=Bit_0; |  |  |  | 4175:iPMM_VirB_Tok9:=Real_0;
mind_bool[88]:=PMM.QA1_GlStik_IZKLOP_IZPAD; |  |  |  | Read_Real(rVar:=NSX[1].ActiveEnergy_kWh,lo:=4176,hi:=4177); |  |  | 88:PMM.QA1_GlStik_IZKLOP_IZPAD:=Bit_0; |  |  |  | 4177:NSX[1].ActiveEnergy_kWh:=Real_0;
mind_bool[89]:=PMM.QB1_GlStik_IZKLOP_IZPAD; |  |  |  | Read_Real(rVar:=NSX[1].ActiveNegativeEnergy_kWh,lo:=4178,hi:=4179); |  |  | 89:PMM.QB1_GlStik_IZKLOP_IZPAD:=Bit_0; |  |  |  | 4179:NSX[1].ActiveNegativeEnergy_kWh:=Real_0;
mind_bool[90]:=PMM.SkNapaka_med60in80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePositiveEnergy_kWh,lo:=4180,hi:=4181); |  |  | 90:PMM.SkNapaka_med60in80:=Bit_0; |  |  |  | 4181:NSX[1].ActivePositiveEnergy_kWh:=Real_0;
mind_bool[91]:=PMM.SkNapaka_nad80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerDemand_kW,lo:=4182,hi:=4183); |  |  | 91:PMM.SkNapaka_nad80:=Bit_0; |  |  |  | 4183:NSX[1].ActivePowerDemand_kW:=Real_0;
mind_bool[92]:=PMM.SkNapakaVirA_med60in80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerL1_kW,lo:=4184,hi:=4185); |  |  | 92:PMM.SkNapakaVirA_med60in80:=Bit_0; |  |  |  | 4185:NSX[1].ActivePowerL1_kW:=Real_0;
mind_bool[93]:=PMM.SkNapakaVirA_nad80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerL2_kW,lo:=4186,hi:=4187); |  |  | 93:PMM.SkNapakaVirA_nad80:=Bit_0; |  |  |  | 4187:NSX[1].ActivePowerL2_kW:=Real_0;
mind_bool[94]:=PMM.SkNapakaVirB_med60in80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerL3_kW,lo:=4188,hi:=4189); |  |  | 94:PMM.SkNapakaVirB_med60in80:=Bit_0; |  |  |  | 4189:NSX[1].ActivePowerL3_kW:=Real_0;
mind_bool[95]:=PMM.SkNapakaVirB_nad80; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerMaxDemand_kW,lo:=4190,hi:=4191); |  |  | 95:PMM.SkNapakaVirB_nad80:=Bit_0; |  |  |  | 4191:NSX[1].ActivePowerMaxDemand_kW:=Real_0;
mind_bool[96]:=PMM.VirA_NapakaOzemljitve; |  |  |  | Read_Real(rVar:=NSX[1].ActivePowerTotal_kW,lo:=4192,hi:=4193); |  |  | 96:PMM.VirA_NapakaOzemljitve:=Bit_0; |  |  |  | 4193:NSX[1].ActivePowerTotal_kW:=Real_0;
mind_bool[97]:=PMM.VirB_NapakaOzemljitve; |  |  |  | Read_Real(rVar:=NSX[1].ApparentEnergy_kVAh,lo:=4194,hi:=4195); |  |  | 97:PMM.VirB_NapakaOzemljitve:=Bit_0; |  |  |  | 4195:NSX[1].ApparentEnergy_kVAh:=Real_0;
mind_bool[98]:=PrevisokaTemp; |  |  |  | Read_Real(rVar:=NSX[1].ApparentPowerDemand_kVA,lo:=4196,hi:=4197); |  |  | 98:PrevisokaTemp:=Bit_0; |  |  |  | 4197:NSX[1].ApparentPowerDemand_kVA:=Real_0;
mind_bool[99]:=razlitjeLAH1; |  |  |  | Read_Real(rVar:=NSX[1].ApparentPowerMaxDemand_kVA,lo:=4198,hi:=4199); |  |  | 99:razlitjeLAH1:=Bit_0; |  |  |  | 4199:NSX[1].ApparentPowerMaxDemand_kVA:=Real_0;
mind_bool[100]:=SetDateTime; |  |  |  | Read_Real(rVar:=NSX[1].ApparetnPowerL1_kVA,lo:=4200,hi:=4201); |  |  | 100:SetDateTime:=Bit_0; |  |  |  | 4201:NSX[1].ApparetnPowerL1_kVA:=Real_0;
mind_bool[101]:=SetDateTimeDemand; |  |  |  | Read_Real(rVar:=NSX[1].ApparetnPowerL2_kVA,lo:=4202,hi:=4203); |  |  | 101:SetDateTimeDemand:=Bit_0; |  |  |  | 4203:NSX[1].ApparetnPowerL2_kVA:=Real_0;
mind_bool[102]:=SetDateTimeError; |  |  |  | Read_Real(rVar:=NSX[1].ApparetnPowerL3_kVA,lo:=4204,hi:=4205); |  |  | 102:SetDateTimeError:=Bit_0; |  |  |  | 4205:NSX[1].ApparetnPowerL3_kVA:=Real_0;
mind_bool[103]:=SetDateTimeFinished; |  |  |  | Read_Real(rVar:=NSX[1].ApparetnPowerTotal_kVA,lo:=4206,hi:=4207); |  |  | 103:SetDateTimeFinished:=Bit_0; |  |  |  | 4207:NSX[1].ApparetnPowerTotal_kVA:=Real_0;
mind_bool[104]:=SlabaBaterijaPLC; |  |  |  | Read_Real(rVar:=NSX[1].CosFL1,lo:=4208,hi:=4209); |  |  | 104:SlabaBaterijaPLC:=Bit_0; |  |  |  | 4209:NSX[1].CosFL1:=Real_0;
mind_bool[105]:=TIA1_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CosFL2,lo:=4210,hi:=4211); |  |  | 105:TIA1_previs_temp:=Bit_0; |  |  |  | 4211:NSX[1].CosFL2:=Real_0;
mind_bool[106]:=TIA2_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CosFL3,lo:=4212,hi:=4213); |  |  | 106:TIA2_previs_temp:=Bit_0; |  |  |  | 4213:NSX[1].CosFL3:=Real_0;
mind_bool[107]:=TIA3_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CosFTotal,lo:=4214,hi:=4215); |  |  | 107:TIA3_previs_temp:=Bit_0; |  |  |  | 4215:NSX[1].CosFTotal:=Real_0;
mind_bool[108]:=TIA4_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CumulNegativeActiveEnergy_kWh,lo:=4216,hi:=4217); |  |  | 108:TIA4_previs_temp:=Bit_0; |  |  |  | 4217:NSX[1].CumulNegativeActiveEnergy_kWh:=Real_0;
mind_bool[109]:=TIA5_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CumulPositiveActiveEnergy_kWh,lo:=4218,hi:=4219); |  |  | 109:TIA5_previs_temp:=Bit_0; |  |  |  | 4219:NSX[1].CumulPositiveActiveEnergy_kWh:=Real_0;
mind_bool[110]:=TIA6_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CurrentAvgI1I2I3_A,lo:=4220,hi:=4221); |  |  | 110:TIA6_previs_temp:=Bit_0; |  |  |  | 4221:NSX[1].CurrentAvgI1I2I3_A:=Real_0;
mind_bool[111]:=TIA7_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandL1_A,lo:=4222,hi:=4223); |  |  | 111:TIA7_previs_temp:=Bit_0; |  |  |  | 4223:NSX[1].CurrentDemandL1_A:=Real_0;
mind_bool[112]:=TIA8_previs_temp; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandL2_A,lo:=4224,hi:=4225); |  |  | 112:TIA8_previs_temp:=Bit_0; |  |  |  | 4225:NSX[1].CurrentDemandL2_A:=Real_0;
mind_bool[113]:=ups_alarm; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandL3_A,lo:=4226,hi:=4227); |  |  | 113:ups_alarm:=Bit_0; |  |  |  | 4227:NSX[1].CurrentDemandL3_A:=Real_0;
mind_bool[114]:=ups_baterijski_nac; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandMaxL1_A,lo:=4228,hi:=4229); |  |  | 114:ups_baterijski_nac:=Bit_0; |  |  |  | 4229:NSX[1].CurrentDemandMaxL1_A:=Real_0;
mind_bool[115]:=ups_polnjenje; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandMaxL2_A,lo:=4230,hi:=4231); |  |  | 115:ups_polnjenje:=Bit_0; |  |  |  | 4231:NSX[1].CurrentDemandMaxL2_A:=Real_0;
mind_bool[116]:=UserLoggedIn; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandMaxL3_A,lo:=4232,hi:=4233); |  |  | 116:UserLoggedIn:=Bit_0; |  |  |  | 4233:NSX[1].CurrentDemandMaxL3_A:=Real_0;
mind_bool[117]:=XVH_AlarmOn; |  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandMaxN_A,lo:=4234,hi:=4235); |  |  | 117:XVH_AlarmOn:=Bit_0; |  |  |  | 4235:NSX[1].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentDemandN_A,lo:=4236,hi:=4237); | [6 empty] | 4237:NSX[1].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentL1_A,lo:=4238,hi:=4239); | [6 empty] | 4239:NSX[1].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentL2_A,lo:=4240,hi:=4241); | [6 empty] | 4241:NSX[1].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentL3_A,lo:=4242,hi:=4243); | [6 empty] | 4243:NSX[1].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentN_A,lo:=4244,hi:=4245); | [6 empty] | 4245:NSX[1].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentUnbI1_P,lo:=4246,hi:=4247); | [6 empty] | 4247:NSX[1].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentUnbI2_P,lo:=4248,hi:=4249); | [6 empty] | 4249:NSX[1].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentUnbI3_P,lo:=4250,hi:=4251); | [6 empty] | 4251:NSX[1].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].CurrentUnbN_P,lo:=4252,hi:=4253); | [6 empty] | 4253:NSX[1].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].DelovnaEnergija_TEMP,lo:=4254,hi:=4255); | [6 empty] | 4255:NSX[1].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].DistortionPowerL1_kVAr,lo:=4256,hi:=4257); | [6 empty] | 4257:NSX[1].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].DistortionPowerL2_kVAr,lo:=4258,hi:=4259); | [6 empty] | 4259:NSX[1].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].DistortionPowerL3_kVAr,lo:=4260,hi:=4261); | [6 empty] | 4261:NSX[1].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].DistortionPowerTotal_kVAr,lo:=4262,hi:=4263); | [6 empty] | 4263:NSX[1].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].Frequency_Hz,lo:=4264,hi:=4265); | [6 empty] | 4265:NSX[1].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].FunReactivePowerL1_kVAr,lo:=4266,hi:=4267); | [6 empty] | 4267:NSX[1].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].FunReactivePowerL2_kVAr,lo:=4268,hi:=4269); | [6 empty] | 4269:NSX[1].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].FunReactivePowerL3_kVAr,lo:=4270,hi:=4271); | [6 empty] | 4271:NSX[1].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].FunReactivePowerTotal_kVAr,lo:=4272,hi:=4273); | [6 empty] | 4273:NSX[1].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ActivePowerL1_kW,lo:=4274,hi:=4275); | [6 empty] | 4275:NSX[1].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ActivePowerL2_kW,lo:=4276,hi:=4277); | [6 empty] | 4277:NSX[1].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ActivePowerL3_kW,lo:=4278,hi:=4279); | [6 empty] | 4279:NSX[1].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ActivePowerTotal_kW,lo:=4280,hi:=4281); | [6 empty] | 4281:NSX[1].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL1_kVA,lo:=4282,hi:=4283); | [6 empty] | 4283:NSX[1].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL2_kVA,lo:=4284,hi:=4285); | [6 empty] | 4285:NSX[1].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL3_kVA,lo:=4286,hi:=4287); | [6 empty] | 4287:NSX[1].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ApparetnPowerTotal_kVA,lo:=4288,hi:=4289); | [6 empty] | 4289:NSX[1].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CosFL1,lo:=4290,hi:=4291); | [6 empty] | 4291:NSX[1].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CosFL2,lo:=4292,hi:=4293); | [6 empty] | 4293:NSX[1].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CosFL3,lo:=4294,hi:=4295); | [6 empty] | 4295:NSX[1].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CosFTotal,lo:=4296,hi:=4297); | [6 empty] | 4297:NSX[1].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentAvgI1I2I3_A,lo:=4298,hi:=4299); | [6 empty] | 4299:NSX[1].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentL1_A,lo:=4300,hi:=4301); | [6 empty] | 4301:NSX[1].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentL2_A,lo:=4302,hi:=4303); | [6 empty] | 4303:NSX[1].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentL3_A,lo:=4304,hi:=4305); | [6 empty] | 4305:NSX[1].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentMaxL1L2L3N_A,lo:=4306,hi:=4307); | [6 empty] | 4307:NSX[1].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_CurrentN_A,lo:=4308,hi:=4309); | [6 empty] | 4309:NSX[1].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_DistortionPowerL1_kVAr,lo:=4310,hi:=4311); | [6 empty] | 4311:NSX[1].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_DistortionPowerL2_kVAr,lo:=4312,hi:=4313); | [6 empty] | 4313:NSX[1].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_DistortionPowerL3_kVAr,lo:=4314,hi:=4315); | [6 empty] | 4315:NSX[1].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_DistortionPowerTotal_kVAr,lo:=4316,hi:=4317); | [6 empty] | 4317:NSX[1].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_Frequency_Hz,lo:=4318,hi:=4319); | [6 empty] | 4319:NSX[1].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL1_kVAr,lo:=4320,hi:=4321); | [6 empty] | 4321:NSX[1].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL2_kVAr,lo:=4322,hi:=4323); | [6 empty] | 4323:NSX[1].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL3_kVAr,lo:=4324,hi:=4325); | [6 empty] | 4325:NSX[1].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_FunReactivePowerTotal_kVAr,lo:=4326,hi:=4327); | [6 empty] | 4327:NSX[1].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_PowerFactorL1,lo:=4328,hi:=4329); | [6 empty] | 4329:NSX[1].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_PowerFactorL2,lo:=4330,hi:=4331); | [6 empty] | 4331:NSX[1].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_PowerFactorL3,lo:=4332,hi:=4333); | [6 empty] | 4333:NSX[1].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_PowerFactorTotal,lo:=4334,hi:=4335); | [6 empty] | 4335:NSX[1].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ReactivePowerL1_kVAr,lo:=4336,hi:=4337); | [6 empty] | 4337:NSX[1].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ReactivePowerL2_kVAr,lo:=4338,hi:=4339); | [6 empty] | 4339:NSX[1].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ReactivePowerL3_kVAr,lo:=4340,hi:=4341); | [6 empty] | 4341:NSX[1].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_ReactivePowerTotal_kVAr,lo:=4342,hi:=4343); | [6 empty] | 4343:NSX[1].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDI1_P,lo:=4344,hi:=4345); | [6 empty] | 4345:NSX[1].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDI2_P,lo:=4346,hi:=4347); | [6 empty] | 4347:NSX[1].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDI3_P,lo:=4348,hi:=4349); | [6 empty] | 4349:NSX[1].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV12_P,lo:=4350,hi:=4351); | [6 empty] | 4351:NSX[1].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV1N_P,lo:=4352,hi:=4353); | [6 empty] | 4353:NSX[1].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV23_P,lo:=4354,hi:=4355); | [6 empty] | 4355:NSX[1].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV2N_P,lo:=4356,hi:=4357); | [6 empty] | 4357:NSX[1].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV31_P,lo:=4358,hi:=4359); | [6 empty] | 4359:NSX[1].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_THDV3N_P,lo:=4360,hi:=4361); | [6 empty] | 4361:NSX[1].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageAvgPhToN_V,lo:=4362,hi:=4363); | [6 empty] | 4363:NSX[1].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageAvgPhToPh_V,lo:=4364,hi:=4365); | [6 empty] | 4365:NSX[1].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV12_P,lo:=4366,hi:=4367); | [6 empty] | 4367:NSX[1].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV1N_P,lo:=4368,hi:=4369); | [6 empty] | 4369:NSX[1].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV23_P,lo:=4370,hi:=4371); | [6 empty] | 4371:NSX[1].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV2N_P,lo:=4372,hi:=4373); | [6 empty] | 4373:NSX[1].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV31_P,lo:=4374,hi:=4375); | [6 empty] | 4375:NSX[1].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageUnbV3N_P,lo:=4376,hi:=4377); | [6 empty] | 4377:NSX[1].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV12_V,lo:=4378,hi:=4379); | [6 empty] | 4379:NSX[1].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV1N_V,lo:=4380,hi:=4381); | [6 empty] | 4381:NSX[1].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV23_V,lo:=4382,hi:=4383); | [6 empty] | 4383:NSX[1].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV2N_V,lo:=4384,hi:=4385); | [6 empty] | 4385:NSX[1].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV31_V,lo:=4386,hi:=4387); | [6 empty] | 4387:NSX[1].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MAX_VoltageV3N_V,lo:=4388,hi:=4389); | [6 empty] | 4389:NSX[1].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ActivePowerL1_kW,lo:=4390,hi:=4391); | [6 empty] | 4391:NSX[1].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ActivePowerL2_kW,lo:=4392,hi:=4393); | [6 empty] | 4393:NSX[1].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ActivePowerL3_kW,lo:=4394,hi:=4395); | [6 empty] | 4395:NSX[1].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ActivePowerTotal_kW,lo:=4396,hi:=4397); | [6 empty] | 4397:NSX[1].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL1_kVA,lo:=4398,hi:=4399); | [6 empty] | 4399:NSX[1].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL2_kVA,lo:=4400,hi:=4401); | [6 empty] | 4401:NSX[1].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL3_kVA,lo:=4402,hi:=4403); | [6 empty] | 4403:NSX[1].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ApparetnPowerTotal_kVA,lo:=4404,hi:=4405); | [6 empty] | 4405:NSX[1].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CosFL1,lo:=4406,hi:=4407); | [6 empty] | 4407:NSX[1].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CosFL2,lo:=4408,hi:=4409); | [6 empty] | 4409:NSX[1].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CosFL3,lo:=4410,hi:=4411); | [6 empty] | 4411:NSX[1].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CosFTotal,lo:=4412,hi:=4413); | [6 empty] | 4413:NSX[1].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentAvgI1I2I3_A,lo:=4414,hi:=4415); | [6 empty] | 4415:NSX[1].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentL1_A,lo:=4416,hi:=4417); | [6 empty] | 4417:NSX[1].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentL2_A,lo:=4418,hi:=4419); | [6 empty] | 4419:NSX[1].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentL3_A,lo:=4420,hi:=4421); | [6 empty] | 4421:NSX[1].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentMaxL1L2L3N_A,lo:=4422,hi:=4423); | [6 empty] | 4423:NSX[1].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_CurrentN_A,lo:=4424,hi:=4425); | [6 empty] | 4425:NSX[1].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_DistortionPowerL1_kVAr,lo:=4426,hi:=4427); | [6 empty] | 4427:NSX[1].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_DistortionPowerL2_kVAr,lo:=4428,hi:=4429); | [6 empty] | 4429:NSX[1].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_DistortionPowerL3_kVAr,lo:=4430,hi:=4431); | [6 empty] | 4431:NSX[1].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_DistortionPowerTotal_kVAr,lo:=4432,hi:=4433); | [6 empty] | 4433:NSX[1].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_Frequency_Hz,lo:=4434,hi:=4435); | [6 empty] | 4435:NSX[1].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL1_kVAr,lo:=4436,hi:=4437); | [6 empty] | 4437:NSX[1].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL2_kVAr,lo:=4438,hi:=4439); | [6 empty] | 4439:NSX[1].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL3_kVAr,lo:=4440,hi:=4441); | [6 empty] | 4441:NSX[1].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_FunReactivePowerTotal_kVAr,lo:=4442,hi:=4443); | [6 empty] | 4443:NSX[1].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_PowerFactorL1,lo:=4444,hi:=4445); | [6 empty] | 4445:NSX[1].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_PowerFactorL2,lo:=4446,hi:=4447); | [6 empty] | 4447:NSX[1].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_PowerFactorL3,lo:=4448,hi:=4449); | [6 empty] | 4449:NSX[1].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_PowerFactorTotal,lo:=4450,hi:=4451); | [6 empty] | 4451:NSX[1].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ReactivePowerL1_kVAr,lo:=4452,hi:=4453); | [6 empty] | 4453:NSX[1].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ReactivePowerL2_kVAr,lo:=4454,hi:=4455); | [6 empty] | 4455:NSX[1].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ReactivePowerL3_kVAr,lo:=4456,hi:=4457); | [6 empty] | 4457:NSX[1].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_ReactivePowerTotal_kVAr,lo:=4458,hi:=4459); | [6 empty] | 4459:NSX[1].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDI1_P,lo:=4460,hi:=4461); | [6 empty] | 4461:NSX[1].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDI2_P,lo:=4462,hi:=4463); | [6 empty] | 4463:NSX[1].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDI3_P,lo:=4464,hi:=4465); | [6 empty] | 4465:NSX[1].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV12_P,lo:=4466,hi:=4467); | [6 empty] | 4467:NSX[1].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV1N_P,lo:=4468,hi:=4469); | [6 empty] | 4469:NSX[1].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV23_P,lo:=4470,hi:=4471); | [6 empty] | 4471:NSX[1].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV2N_P,lo:=4472,hi:=4473); | [6 empty] | 4473:NSX[1].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV31_P,lo:=4474,hi:=4475); | [6 empty] | 4475:NSX[1].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_THDV3N_P,lo:=4476,hi:=4477); | [6 empty] | 4477:NSX[1].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageAvgPhToN_V,lo:=4478,hi:=4479); | [6 empty] | 4479:NSX[1].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageAvgPhToPh_V,lo:=4480,hi:=4481); | [6 empty] | 4481:NSX[1].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV12_P,lo:=4482,hi:=4483); | [6 empty] | 4483:NSX[1].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV1N_P,lo:=4484,hi:=4485); | [6 empty] | 4485:NSX[1].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV23_P,lo:=4486,hi:=4487); | [6 empty] | 4487:NSX[1].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV2N_P,lo:=4488,hi:=4489); | [6 empty] | 4489:NSX[1].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV31_P,lo:=4490,hi:=4491); | [6 empty] | 4491:NSX[1].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageUnbV3N_P,lo:=4492,hi:=4493); | [6 empty] | 4493:NSX[1].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV12_V,lo:=4494,hi:=4495); | [6 empty] | 4495:NSX[1].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV1N_V,lo:=4496,hi:=4497); | [6 empty] | 4497:NSX[1].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV23_V,lo:=4498,hi:=4499); | [6 empty] | 4499:NSX[1].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV2N_V,lo:=4500,hi:=4501); | [6 empty] | 4501:NSX[1].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV31_V,lo:=4502,hi:=4503); | [6 empty] | 4503:NSX[1].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].MIN_VoltageV3N_V,lo:=4504,hi:=4505); | [6 empty] | 4505:NSX[1].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].PowerFactorL1,lo:=4506,hi:=4507); | [6 empty] | 4507:NSX[1].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].PowerFactorL2,lo:=4508,hi:=4509); | [6 empty] | 4509:NSX[1].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].PowerFactorL3,lo:=4510,hi:=4511); | [6 empty] | 4511:NSX[1].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].PowerFactorTotal,lo:=4512,hi:=4513); | [6 empty] | 4513:NSX[1].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_D,lo:=4514,hi:=4515); | [6 empty] | 4515:NSX[1].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_D_SCADA,lo:=4516,hi:=4517); | [6 empty] | 4517:NSX[1].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_D_TEMP,lo:=4518,hi:=4519); | [6 empty] | 4519:NSX[1].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_M,lo:=4520,hi:=4521); | [6 empty] | 4521:NSX[1].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_M_SCADA,lo:=4522,hi:=4523); | [6 empty] | 4523:NSX[1].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_M_TEMP,lo:=4524,hi:=4525); | [6 empty] | 4525:NSX[1].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_T,lo:=4526,hi:=4527); | [6 empty] | 4527:NSX[1].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_T_SCADA,lo:=4528,hi:=4529); | [6 empty] | 4529:NSX[1].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].RazEner_T_TEMP,lo:=4530,hi:=4531); | [6 empty] | 4531:NSX[1].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactiveEnergy_kVArh,lo:=4532,hi:=4533); | [6 empty] | 4533:NSX[1].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactiveNegativeEnergy_kVArh,lo:=4534,hi:=4535); | [6 empty] | 4535:NSX[1].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePositiveEnergy_kVArh,lo:=4536,hi:=4537); | [6 empty] | 4537:NSX[1].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerDemand_kVAr,lo:=4538,hi:=4539); | [6 empty] | 4539:NSX[1].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerL1_kVAr,lo:=4540,hi:=4541); | [6 empty] | 4541:NSX[1].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerL2_kVAr,lo:=4542,hi:=4543); | [6 empty] | 4543:NSX[1].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerL3_kVAr,lo:=4544,hi:=4545); | [6 empty] | 4545:NSX[1].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerMaxDemand_kVAr,lo:=4546,hi:=4547); | [6 empty] | 4547:NSX[1].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].ReactivePowerTotal_kVAr,lo:=4548,hi:=4549); | [6 empty] | 4549:NSX[1].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDI1_P,lo:=4550,hi:=4551); | [6 empty] | 4551:NSX[1].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDI2_P,lo:=4552,hi:=4553); | [6 empty] | 4553:NSX[1].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDI3_P,lo:=4554,hi:=4555); | [6 empty] | 4555:NSX[1].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV12_P,lo:=4556,hi:=4557); | [6 empty] | 4557:NSX[1].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV1N_P,lo:=4558,hi:=4559); | [6 empty] | 4559:NSX[1].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV23_P,lo:=4560,hi:=4561); | [6 empty] | 4561:NSX[1].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV2N_P,lo:=4562,hi:=4563); | [6 empty] | 4563:NSX[1].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV31_P,lo:=4564,hi:=4565); | [6 empty] | 4565:NSX[1].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].THDV3N_P,lo:=4566,hi:=4567); | [6 empty] | 4567:NSX[1].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageAvgPhToN_V,lo:=4568,hi:=4569); | [6 empty] | 4569:NSX[1].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageAvgPhToPh_V,lo:=4570,hi:=4571); | [6 empty] | 4571:NSX[1].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV12_P,lo:=4572,hi:=4573); | [6 empty] | 4573:NSX[1].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV1N_P,lo:=4574,hi:=4575); | [6 empty] | 4575:NSX[1].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV23_P,lo:=4576,hi:=4577); | [6 empty] | 4577:NSX[1].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV2N_P,lo:=4578,hi:=4579); | [6 empty] | 4579:NSX[1].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV31_P,lo:=4580,hi:=4581); | [6 empty] | 4581:NSX[1].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageUnbV3N_P,lo:=4582,hi:=4583); | [6 empty] | 4583:NSX[1].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV12_V,lo:=4584,hi:=4585); | [6 empty] | 4585:NSX[1].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV1N_V,lo:=4586,hi:=4587); | [6 empty] | 4587:NSX[1].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV23_V,lo:=4588,hi:=4589); | [6 empty] | 4589:NSX[1].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV2N_V,lo:=4590,hi:=4591); | [6 empty] | 4591:NSX[1].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV31_V,lo:=4592,hi:=4593); | [6 empty] | 4593:NSX[1].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[1].VoltageV3N_V,lo:=4594,hi:=4595); | [6 empty] | 4595:NSX[1].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActiveEnergy_kWh,lo:=4596,hi:=4597); | [6 empty] | 4597:NSX[2].ActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActiveNegativeEnergy_kWh,lo:=4598,hi:=4599); | [6 empty] | 4599:NSX[2].ActiveNegativeEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePositiveEnergy_kWh,lo:=4600,hi:=4601); | [6 empty] | 4601:NSX[2].ActivePositiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerDemand_kW,lo:=4602,hi:=4603); | [6 empty] | 4603:NSX[2].ActivePowerDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerL1_kW,lo:=4604,hi:=4605); | [6 empty] | 4605:NSX[2].ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerL2_kW,lo:=4606,hi:=4607); | [6 empty] | 4607:NSX[2].ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerL3_kW,lo:=4608,hi:=4609); | [6 empty] | 4609:NSX[2].ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerMaxDemand_kW,lo:=4610,hi:=4611); | [6 empty] | 4611:NSX[2].ActivePowerMaxDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ActivePowerTotal_kW,lo:=4612,hi:=4613); | [6 empty] | 4613:NSX[2].ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparentEnergy_kVAh,lo:=4614,hi:=4615); | [6 empty] | 4615:NSX[2].ApparentEnergy_kVAh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparentPowerDemand_kVA,lo:=4616,hi:=4617); | [6 empty] | 4617:NSX[2].ApparentPowerDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparentPowerMaxDemand_kVA,lo:=4618,hi:=4619); | [6 empty] | 4619:NSX[2].ApparentPowerMaxDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparetnPowerL1_kVA,lo:=4620,hi:=4621); | [6 empty] | 4621:NSX[2].ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparetnPowerL2_kVA,lo:=4622,hi:=4623); | [6 empty] | 4623:NSX[2].ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparetnPowerL3_kVA,lo:=4624,hi:=4625); | [6 empty] | 4625:NSX[2].ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ApparetnPowerTotal_kVA,lo:=4626,hi:=4627); | [6 empty] | 4627:NSX[2].ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CosFL1,lo:=4628,hi:=4629); | [6 empty] | 4629:NSX[2].CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CosFL2,lo:=4630,hi:=4631); | [6 empty] | 4631:NSX[2].CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CosFL3,lo:=4632,hi:=4633); | [6 empty] | 4633:NSX[2].CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CosFTotal,lo:=4634,hi:=4635); | [6 empty] | 4635:NSX[2].CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CumulNegativeActiveEnergy_kWh,lo:=4636,hi:=4637); | [6 empty] | 4637:NSX[2].CumulNegativeActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CumulPositiveActiveEnergy_kWh,lo:=4638,hi:=4639); | [6 empty] | 4639:NSX[2].CumulPositiveActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentAvgI1I2I3_A,lo:=4640,hi:=4641); | [6 empty] | 4641:NSX[2].CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandL1_A,lo:=4642,hi:=4643); | [6 empty] | 4643:NSX[2].CurrentDemandL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandL2_A,lo:=4644,hi:=4645); | [6 empty] | 4645:NSX[2].CurrentDemandL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandL3_A,lo:=4646,hi:=4647); | [6 empty] | 4647:NSX[2].CurrentDemandL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandMaxL1_A,lo:=4648,hi:=4649); | [6 empty] | 4649:NSX[2].CurrentDemandMaxL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandMaxL2_A,lo:=4650,hi:=4651); | [6 empty] | 4651:NSX[2].CurrentDemandMaxL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandMaxL3_A,lo:=4652,hi:=4653); | [6 empty] | 4653:NSX[2].CurrentDemandMaxL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandMaxN_A,lo:=4654,hi:=4655); | [6 empty] | 4655:NSX[2].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentDemandN_A,lo:=4656,hi:=4657); | [6 empty] | 4657:NSX[2].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentL1_A,lo:=4658,hi:=4659); | [6 empty] | 4659:NSX[2].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentL2_A,lo:=4660,hi:=4661); | [6 empty] | 4661:NSX[2].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentL3_A,lo:=4662,hi:=4663); | [6 empty] | 4663:NSX[2].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentN_A,lo:=4664,hi:=4665); | [6 empty] | 4665:NSX[2].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentUnbI1_P,lo:=4666,hi:=4667); | [6 empty] | 4667:NSX[2].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentUnbI2_P,lo:=4668,hi:=4669); | [6 empty] | 4669:NSX[2].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentUnbI3_P,lo:=4670,hi:=4671); | [6 empty] | 4671:NSX[2].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].CurrentUnbN_P,lo:=4672,hi:=4673); | [6 empty] | 4673:NSX[2].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].DelovnaEnergija_TEMP,lo:=4674,hi:=4675); | [6 empty] | 4675:NSX[2].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].DistortionPowerL1_kVAr,lo:=4676,hi:=4677); | [6 empty] | 4677:NSX[2].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].DistortionPowerL2_kVAr,lo:=4678,hi:=4679); | [6 empty] | 4679:NSX[2].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].DistortionPowerL3_kVAr,lo:=4680,hi:=4681); | [6 empty] | 4681:NSX[2].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].DistortionPowerTotal_kVAr,lo:=4682,hi:=4683); | [6 empty] | 4683:NSX[2].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].Frequency_Hz,lo:=4684,hi:=4685); | [6 empty] | 4685:NSX[2].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].FunReactivePowerL1_kVAr,lo:=4686,hi:=4687); | [6 empty] | 4687:NSX[2].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].FunReactivePowerL2_kVAr,lo:=4688,hi:=4689); | [6 empty] | 4689:NSX[2].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].FunReactivePowerL3_kVAr,lo:=4690,hi:=4691); | [6 empty] | 4691:NSX[2].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].FunReactivePowerTotal_kVAr,lo:=4692,hi:=4693); | [6 empty] | 4693:NSX[2].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ActivePowerL1_kW,lo:=4694,hi:=4695); | [6 empty] | 4695:NSX[2].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ActivePowerL2_kW,lo:=4696,hi:=4697); | [6 empty] | 4697:NSX[2].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ActivePowerL3_kW,lo:=4698,hi:=4699); | [6 empty] | 4699:NSX[2].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ActivePowerTotal_kW,lo:=4700,hi:=4701); | [6 empty] | 4701:NSX[2].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL1_kVA,lo:=4702,hi:=4703); | [6 empty] | 4703:NSX[2].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL2_kVA,lo:=4704,hi:=4705); | [6 empty] | 4705:NSX[2].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL3_kVA,lo:=4706,hi:=4707); | [6 empty] | 4707:NSX[2].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ApparetnPowerTotal_kVA,lo:=4708,hi:=4709); | [6 empty] | 4709:NSX[2].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CosFL1,lo:=4710,hi:=4711); | [6 empty] | 4711:NSX[2].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CosFL2,lo:=4712,hi:=4713); | [6 empty] | 4713:NSX[2].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CosFL3,lo:=4714,hi:=4715); | [6 empty] | 4715:NSX[2].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CosFTotal,lo:=4716,hi:=4717); | [6 empty] | 4717:NSX[2].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentAvgI1I2I3_A,lo:=4718,hi:=4719); | [6 empty] | 4719:NSX[2].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentL1_A,lo:=4720,hi:=4721); | [6 empty] | 4721:NSX[2].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentL2_A,lo:=4722,hi:=4723); | [6 empty] | 4723:NSX[2].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentL3_A,lo:=4724,hi:=4725); | [6 empty] | 4725:NSX[2].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentMaxL1L2L3N_A,lo:=4726,hi:=4727); | [6 empty] | 4727:NSX[2].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_CurrentN_A,lo:=4728,hi:=4729); | [6 empty] | 4729:NSX[2].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_DistortionPowerL1_kVAr,lo:=4730,hi:=4731); | [6 empty] | 4731:NSX[2].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_DistortionPowerL2_kVAr,lo:=4732,hi:=4733); | [6 empty] | 4733:NSX[2].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_DistortionPowerL3_kVAr,lo:=4734,hi:=4735); | [6 empty] | 4735:NSX[2].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_DistortionPowerTotal_kVAr,lo:=4736,hi:=4737); | [6 empty] | 4737:NSX[2].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_Frequency_Hz,lo:=4738,hi:=4739); | [6 empty] | 4739:NSX[2].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL1_kVAr,lo:=4740,hi:=4741); | [6 empty] | 4741:NSX[2].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL2_kVAr,lo:=4742,hi:=4743); | [6 empty] | 4743:NSX[2].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL3_kVAr,lo:=4744,hi:=4745); | [6 empty] | 4745:NSX[2].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_FunReactivePowerTotal_kVAr,lo:=4746,hi:=4747); | [6 empty] | 4747:NSX[2].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_PowerFactorL1,lo:=4748,hi:=4749); | [6 empty] | 4749:NSX[2].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_PowerFactorL2,lo:=4750,hi:=4751); | [6 empty] | 4751:NSX[2].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_PowerFactorL3,lo:=4752,hi:=4753); | [6 empty] | 4753:NSX[2].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_PowerFactorTotal,lo:=4754,hi:=4755); | [6 empty] | 4755:NSX[2].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ReactivePowerL1_kVAr,lo:=4756,hi:=4757); | [6 empty] | 4757:NSX[2].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ReactivePowerL2_kVAr,lo:=4758,hi:=4759); | [6 empty] | 4759:NSX[2].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ReactivePowerL3_kVAr,lo:=4760,hi:=4761); | [6 empty] | 4761:NSX[2].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_ReactivePowerTotal_kVAr,lo:=4762,hi:=4763); | [6 empty] | 4763:NSX[2].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDI1_P,lo:=4764,hi:=4765); | [6 empty] | 4765:NSX[2].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDI2_P,lo:=4766,hi:=4767); | [6 empty] | 4767:NSX[2].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDI3_P,lo:=4768,hi:=4769); | [6 empty] | 4769:NSX[2].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV12_P,lo:=4770,hi:=4771); | [6 empty] | 4771:NSX[2].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV1N_P,lo:=4772,hi:=4773); | [6 empty] | 4773:NSX[2].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV23_P,lo:=4774,hi:=4775); | [6 empty] | 4775:NSX[2].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV2N_P,lo:=4776,hi:=4777); | [6 empty] | 4777:NSX[2].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV31_P,lo:=4778,hi:=4779); | [6 empty] | 4779:NSX[2].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_THDV3N_P,lo:=4780,hi:=4781); | [6 empty] | 4781:NSX[2].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageAvgPhToN_V,lo:=4782,hi:=4783); | [6 empty] | 4783:NSX[2].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageAvgPhToPh_V,lo:=4784,hi:=4785); | [6 empty] | 4785:NSX[2].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV12_P,lo:=4786,hi:=4787); | [6 empty] | 4787:NSX[2].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV1N_P,lo:=4788,hi:=4789); | [6 empty] | 4789:NSX[2].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV23_P,lo:=4790,hi:=4791); | [6 empty] | 4791:NSX[2].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV2N_P,lo:=4792,hi:=4793); | [6 empty] | 4793:NSX[2].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV31_P,lo:=4794,hi:=4795); | [6 empty] | 4795:NSX[2].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageUnbV3N_P,lo:=4796,hi:=4797); | [6 empty] | 4797:NSX[2].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV12_V,lo:=4798,hi:=4799); | [6 empty] | 4799:NSX[2].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV1N_V,lo:=4800,hi:=4801); | [6 empty] | 4801:NSX[2].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV23_V,lo:=4802,hi:=4803); | [6 empty] | 4803:NSX[2].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV2N_V,lo:=4804,hi:=4805); | [6 empty] | 4805:NSX[2].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV31_V,lo:=4806,hi:=4807); | [6 empty] | 4807:NSX[2].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MAX_VoltageV3N_V,lo:=4808,hi:=4809); | [6 empty] | 4809:NSX[2].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ActivePowerL1_kW,lo:=4810,hi:=4811); | [6 empty] | 4811:NSX[2].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ActivePowerL2_kW,lo:=4812,hi:=4813); | [6 empty] | 4813:NSX[2].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ActivePowerL3_kW,lo:=4814,hi:=4815); | [6 empty] | 4815:NSX[2].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ActivePowerTotal_kW,lo:=4816,hi:=4817); | [6 empty] | 4817:NSX[2].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL1_kVA,lo:=4818,hi:=4819); | [6 empty] | 4819:NSX[2].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL2_kVA,lo:=4820,hi:=4821); | [6 empty] | 4821:NSX[2].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL3_kVA,lo:=4822,hi:=4823); | [6 empty] | 4823:NSX[2].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ApparetnPowerTotal_kVA,lo:=4824,hi:=4825); | [6 empty] | 4825:NSX[2].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CosFL1,lo:=4826,hi:=4827); | [6 empty] | 4827:NSX[2].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CosFL2,lo:=4828,hi:=4829); | [6 empty] | 4829:NSX[2].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CosFL3,lo:=4830,hi:=4831); | [6 empty] | 4831:NSX[2].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CosFTotal,lo:=4832,hi:=4833); | [6 empty] | 4833:NSX[2].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentAvgI1I2I3_A,lo:=4834,hi:=4835); | [6 empty] | 4835:NSX[2].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentL1_A,lo:=4836,hi:=4837); | [6 empty] | 4837:NSX[2].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentL2_A,lo:=4838,hi:=4839); | [6 empty] | 4839:NSX[2].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentL3_A,lo:=4840,hi:=4841); | [6 empty] | 4841:NSX[2].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentMaxL1L2L3N_A,lo:=4842,hi:=4843); | [6 empty] | 4843:NSX[2].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_CurrentN_A,lo:=4844,hi:=4845); | [6 empty] | 4845:NSX[2].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_DistortionPowerL1_kVAr,lo:=4846,hi:=4847); | [6 empty] | 4847:NSX[2].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_DistortionPowerL2_kVAr,lo:=4848,hi:=4849); | [6 empty] | 4849:NSX[2].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_DistortionPowerL3_kVAr,lo:=4850,hi:=4851); | [6 empty] | 4851:NSX[2].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_DistortionPowerTotal_kVAr,lo:=4852,hi:=4853); | [6 empty] | 4853:NSX[2].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_Frequency_Hz,lo:=4854,hi:=4855); | [6 empty] | 4855:NSX[2].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL1_kVAr,lo:=4856,hi:=4857); | [6 empty] | 4857:NSX[2].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL2_kVAr,lo:=4858,hi:=4859); | [6 empty] | 4859:NSX[2].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL3_kVAr,lo:=4860,hi:=4861); | [6 empty] | 4861:NSX[2].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_FunReactivePowerTotal_kVAr,lo:=4862,hi:=4863); | [6 empty] | 4863:NSX[2].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_PowerFactorL1,lo:=4864,hi:=4865); | [6 empty] | 4865:NSX[2].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_PowerFactorL2,lo:=4866,hi:=4867); | [6 empty] | 4867:NSX[2].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_PowerFactorL3,lo:=4868,hi:=4869); | [6 empty] | 4869:NSX[2].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_PowerFactorTotal,lo:=4870,hi:=4871); | [6 empty] | 4871:NSX[2].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ReactivePowerL1_kVAr,lo:=4872,hi:=4873); | [6 empty] | 4873:NSX[2].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ReactivePowerL2_kVAr,lo:=4874,hi:=4875); | [6 empty] | 4875:NSX[2].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ReactivePowerL3_kVAr,lo:=4876,hi:=4877); | [6 empty] | 4877:NSX[2].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_ReactivePowerTotal_kVAr,lo:=4878,hi:=4879); | [6 empty] | 4879:NSX[2].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDI1_P,lo:=4880,hi:=4881); | [6 empty] | 4881:NSX[2].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDI2_P,lo:=4882,hi:=4883); | [6 empty] | 4883:NSX[2].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDI3_P,lo:=4884,hi:=4885); | [6 empty] | 4885:NSX[2].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV12_P,lo:=4886,hi:=4887); | [6 empty] | 4887:NSX[2].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV1N_P,lo:=4888,hi:=4889); | [6 empty] | 4889:NSX[2].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV23_P,lo:=4890,hi:=4891); | [6 empty] | 4891:NSX[2].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV2N_P,lo:=4892,hi:=4893); | [6 empty] | 4893:NSX[2].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV31_P,lo:=4894,hi:=4895); | [6 empty] | 4895:NSX[2].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_THDV3N_P,lo:=4896,hi:=4897); | [6 empty] | 4897:NSX[2].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageAvgPhToN_V,lo:=4898,hi:=4899); | [6 empty] | 4899:NSX[2].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageAvgPhToPh_V,lo:=4900,hi:=4901); | [6 empty] | 4901:NSX[2].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV12_P,lo:=4902,hi:=4903); | [6 empty] | 4903:NSX[2].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV1N_P,lo:=4904,hi:=4905); | [6 empty] | 4905:NSX[2].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV23_P,lo:=4906,hi:=4907); | [6 empty] | 4907:NSX[2].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV2N_P,lo:=4908,hi:=4909); | [6 empty] | 4909:NSX[2].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV31_P,lo:=4910,hi:=4911); | [6 empty] | 4911:NSX[2].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageUnbV3N_P,lo:=4912,hi:=4913); | [6 empty] | 4913:NSX[2].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV12_V,lo:=4914,hi:=4915); | [6 empty] | 4915:NSX[2].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV1N_V,lo:=4916,hi:=4917); | [6 empty] | 4917:NSX[2].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV23_V,lo:=4918,hi:=4919); | [6 empty] | 4919:NSX[2].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV2N_V,lo:=4920,hi:=4921); | [6 empty] | 4921:NSX[2].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV31_V,lo:=4922,hi:=4923); | [6 empty] | 4923:NSX[2].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].MIN_VoltageV3N_V,lo:=4924,hi:=4925); | [6 empty] | 4925:NSX[2].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].PowerFactorL1,lo:=4926,hi:=4927); | [6 empty] | 4927:NSX[2].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].PowerFactorL2,lo:=4928,hi:=4929); | [6 empty] | 4929:NSX[2].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].PowerFactorL3,lo:=4930,hi:=4931); | [6 empty] | 4931:NSX[2].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].PowerFactorTotal,lo:=4932,hi:=4933); | [6 empty] | 4933:NSX[2].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_D,lo:=4934,hi:=4935); | [6 empty] | 4935:NSX[2].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_D_SCADA,lo:=4936,hi:=4937); | [6 empty] | 4937:NSX[2].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_D_TEMP,lo:=4938,hi:=4939); | [6 empty] | 4939:NSX[2].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_M,lo:=4940,hi:=4941); | [6 empty] | 4941:NSX[2].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_M_SCADA,lo:=4942,hi:=4943); | [6 empty] | 4943:NSX[2].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_M_TEMP,lo:=4944,hi:=4945); | [6 empty] | 4945:NSX[2].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_T,lo:=4946,hi:=4947); | [6 empty] | 4947:NSX[2].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_T_SCADA,lo:=4948,hi:=4949); | [6 empty] | 4949:NSX[2].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].RazEner_T_TEMP,lo:=4950,hi:=4951); | [6 empty] | 4951:NSX[2].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactiveEnergy_kVArh,lo:=4952,hi:=4953); | [6 empty] | 4953:NSX[2].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactiveNegativeEnergy_kVArh,lo:=4954,hi:=4955); | [6 empty] | 4955:NSX[2].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePositiveEnergy_kVArh,lo:=4956,hi:=4957); | [6 empty] | 4957:NSX[2].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerDemand_kVAr,lo:=4958,hi:=4959); | [6 empty] | 4959:NSX[2].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerL1_kVAr,lo:=4960,hi:=4961); | [6 empty] | 4961:NSX[2].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerL2_kVAr,lo:=4962,hi:=4963); | [6 empty] | 4963:NSX[2].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerL3_kVAr,lo:=4964,hi:=4965); | [6 empty] | 4965:NSX[2].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerMaxDemand_kVAr,lo:=4966,hi:=4967); | [6 empty] | 4967:NSX[2].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].ReactivePowerTotal_kVAr,lo:=4968,hi:=4969); | [6 empty] | 4969:NSX[2].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDI1_P,lo:=4970,hi:=4971); | [6 empty] | 4971:NSX[2].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDI2_P,lo:=4972,hi:=4973); | [6 empty] | 4973:NSX[2].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDI3_P,lo:=4974,hi:=4975); | [6 empty] | 4975:NSX[2].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV12_P,lo:=4976,hi:=4977); | [6 empty] | 4977:NSX[2].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV1N_P,lo:=4978,hi:=4979); | [6 empty] | 4979:NSX[2].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV23_P,lo:=4980,hi:=4981); | [6 empty] | 4981:NSX[2].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV2N_P,lo:=4982,hi:=4983); | [6 empty] | 4983:NSX[2].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV31_P,lo:=4984,hi:=4985); | [6 empty] | 4985:NSX[2].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].THDV3N_P,lo:=4986,hi:=4987); | [6 empty] | 4987:NSX[2].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageAvgPhToN_V,lo:=4988,hi:=4989); | [6 empty] | 4989:NSX[2].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageAvgPhToPh_V,lo:=4990,hi:=4991); | [6 empty] | 4991:NSX[2].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV12_P,lo:=4992,hi:=4993); | [6 empty] | 4993:NSX[2].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV1N_P,lo:=4994,hi:=4995); | [6 empty] | 4995:NSX[2].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV23_P,lo:=4996,hi:=4997); | [6 empty] | 4997:NSX[2].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV2N_P,lo:=4998,hi:=4999); | [6 empty] | 4999:NSX[2].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV31_P,lo:=5000,hi:=5001); | [6 empty] | 5001:NSX[2].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageUnbV3N_P,lo:=5002,hi:=5003); | [6 empty] | 5003:NSX[2].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV12_V,lo:=5004,hi:=5005); | [6 empty] | 5005:NSX[2].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV1N_V,lo:=5006,hi:=5007); | [6 empty] | 5007:NSX[2].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV23_V,lo:=5008,hi:=5009); | [6 empty] | 5009:NSX[2].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV2N_V,lo:=5010,hi:=5011); | [6 empty] | 5011:NSX[2].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV31_V,lo:=5012,hi:=5013); | [6 empty] | 5013:NSX[2].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[2].VoltageV3N_V,lo:=5014,hi:=5015); | [6 empty] | 5015:NSX[2].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActiveEnergy_kWh,lo:=5016,hi:=5017); | [6 empty] | 5017:NSX[3].ActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActiveNegativeEnergy_kWh,lo:=5018,hi:=5019); | [6 empty] | 5019:NSX[3].ActiveNegativeEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePositiveEnergy_kWh,lo:=5020,hi:=5021); | [6 empty] | 5021:NSX[3].ActivePositiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerDemand_kW,lo:=5022,hi:=5023); | [6 empty] | 5023:NSX[3].ActivePowerDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerL1_kW,lo:=5024,hi:=5025); | [6 empty] | 5025:NSX[3].ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerL2_kW,lo:=5026,hi:=5027); | [6 empty] | 5027:NSX[3].ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerL3_kW,lo:=5028,hi:=5029); | [6 empty] | 5029:NSX[3].ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerMaxDemand_kW,lo:=5030,hi:=5031); | [6 empty] | 5031:NSX[3].ActivePowerMaxDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ActivePowerTotal_kW,lo:=5032,hi:=5033); | [6 empty] | 5033:NSX[3].ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparentEnergy_kVAh,lo:=5034,hi:=5035); | [6 empty] | 5035:NSX[3].ApparentEnergy_kVAh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparentPowerDemand_kVA,lo:=5036,hi:=5037); | [6 empty] | 5037:NSX[3].ApparentPowerDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparentPowerMaxDemand_kVA,lo:=5038,hi:=5039); | [6 empty] | 5039:NSX[3].ApparentPowerMaxDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparetnPowerL1_kVA,lo:=5040,hi:=5041); | [6 empty] | 5041:NSX[3].ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparetnPowerL2_kVA,lo:=5042,hi:=5043); | [6 empty] | 5043:NSX[3].ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparetnPowerL3_kVA,lo:=5044,hi:=5045); | [6 empty] | 5045:NSX[3].ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ApparetnPowerTotal_kVA,lo:=5046,hi:=5047); | [6 empty] | 5047:NSX[3].ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CosFL1,lo:=5048,hi:=5049); | [6 empty] | 5049:NSX[3].CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CosFL2,lo:=5050,hi:=5051); | [6 empty] | 5051:NSX[3].CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CosFL3,lo:=5052,hi:=5053); | [6 empty] | 5053:NSX[3].CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CosFTotal,lo:=5054,hi:=5055); | [6 empty] | 5055:NSX[3].CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CumulNegativeActiveEnergy_kWh,lo:=5056,hi:=5057); | [6 empty] | 5057:NSX[3].CumulNegativeActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CumulPositiveActiveEnergy_kWh,lo:=5058,hi:=5059); | [6 empty] | 5059:NSX[3].CumulPositiveActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentAvgI1I2I3_A,lo:=5060,hi:=5061); | [6 empty] | 5061:NSX[3].CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandL1_A,lo:=5062,hi:=5063); | [6 empty] | 5063:NSX[3].CurrentDemandL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandL2_A,lo:=5064,hi:=5065); | [6 empty] | 5065:NSX[3].CurrentDemandL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandL3_A,lo:=5066,hi:=5067); | [6 empty] | 5067:NSX[3].CurrentDemandL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandMaxL1_A,lo:=5068,hi:=5069); | [6 empty] | 5069:NSX[3].CurrentDemandMaxL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandMaxL2_A,lo:=5070,hi:=5071); | [6 empty] | 5071:NSX[3].CurrentDemandMaxL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandMaxL3_A,lo:=5072,hi:=5073); | [6 empty] | 5073:NSX[3].CurrentDemandMaxL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandMaxN_A,lo:=5074,hi:=5075); | [6 empty] | 5075:NSX[3].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentDemandN_A,lo:=5076,hi:=5077); | [6 empty] | 5077:NSX[3].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentL1_A,lo:=5078,hi:=5079); | [6 empty] | 5079:NSX[3].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentL2_A,lo:=5080,hi:=5081); | [6 empty] | 5081:NSX[3].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentL3_A,lo:=5082,hi:=5083); | [6 empty] | 5083:NSX[3].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentN_A,lo:=5084,hi:=5085); | [6 empty] | 5085:NSX[3].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentUnbI1_P,lo:=5086,hi:=5087); | [6 empty] | 5087:NSX[3].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentUnbI2_P,lo:=5088,hi:=5089); | [6 empty] | 5089:NSX[3].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentUnbI3_P,lo:=5090,hi:=5091); | [6 empty] | 5091:NSX[3].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].CurrentUnbN_P,lo:=5092,hi:=5093); | [6 empty] | 5093:NSX[3].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].DelovnaEnergija_TEMP,lo:=5094,hi:=5095); | [6 empty] | 5095:NSX[3].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].DistortionPowerL1_kVAr,lo:=5096,hi:=5097); | [6 empty] | 5097:NSX[3].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].DistortionPowerL2_kVAr,lo:=5098,hi:=5099); | [6 empty] | 5099:NSX[3].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].DistortionPowerL3_kVAr,lo:=5100,hi:=5101); | [6 empty] | 5101:NSX[3].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].DistortionPowerTotal_kVAr,lo:=5102,hi:=5103); | [6 empty] | 5103:NSX[3].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].Frequency_Hz,lo:=5104,hi:=5105); | [6 empty] | 5105:NSX[3].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].FunReactivePowerL1_kVAr,lo:=5106,hi:=5107); | [6 empty] | 5107:NSX[3].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].FunReactivePowerL2_kVAr,lo:=5108,hi:=5109); | [6 empty] | 5109:NSX[3].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].FunReactivePowerL3_kVAr,lo:=5110,hi:=5111); | [6 empty] | 5111:NSX[3].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].FunReactivePowerTotal_kVAr,lo:=5112,hi:=5113); | [6 empty] | 5113:NSX[3].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ActivePowerL1_kW,lo:=5114,hi:=5115); | [6 empty] | 5115:NSX[3].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ActivePowerL2_kW,lo:=5116,hi:=5117); | [6 empty] | 5117:NSX[3].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ActivePowerL3_kW,lo:=5118,hi:=5119); | [6 empty] | 5119:NSX[3].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ActivePowerTotal_kW,lo:=5120,hi:=5121); | [6 empty] | 5121:NSX[3].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL1_kVA,lo:=5122,hi:=5123); | [6 empty] | 5123:NSX[3].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL2_kVA,lo:=5124,hi:=5125); | [6 empty] | 5125:NSX[3].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL3_kVA,lo:=5126,hi:=5127); | [6 empty] | 5127:NSX[3].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ApparetnPowerTotal_kVA,lo:=5128,hi:=5129); | [6 empty] | 5129:NSX[3].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CosFL1,lo:=5130,hi:=5131); | [6 empty] | 5131:NSX[3].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CosFL2,lo:=5132,hi:=5133); | [6 empty] | 5133:NSX[3].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CosFL3,lo:=5134,hi:=5135); | [6 empty] | 5135:NSX[3].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CosFTotal,lo:=5136,hi:=5137); | [6 empty] | 5137:NSX[3].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentAvgI1I2I3_A,lo:=5138,hi:=5139); | [6 empty] | 5139:NSX[3].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentL1_A,lo:=5140,hi:=5141); | [6 empty] | 5141:NSX[3].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentL2_A,lo:=5142,hi:=5143); | [6 empty] | 5143:NSX[3].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentL3_A,lo:=5144,hi:=5145); | [6 empty] | 5145:NSX[3].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentMaxL1L2L3N_A,lo:=5146,hi:=5147); | [6 empty] | 5147:NSX[3].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_CurrentN_A,lo:=5148,hi:=5149); | [6 empty] | 5149:NSX[3].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_DistortionPowerL1_kVAr,lo:=5150,hi:=5151); | [6 empty] | 5151:NSX[3].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_DistortionPowerL2_kVAr,lo:=5152,hi:=5153); | [6 empty] | 5153:NSX[3].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_DistortionPowerL3_kVAr,lo:=5154,hi:=5155); | [6 empty] | 5155:NSX[3].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_DistortionPowerTotal_kVAr,lo:=5156,hi:=5157); | [6 empty] | 5157:NSX[3].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_Frequency_Hz,lo:=5158,hi:=5159); | [6 empty] | 5159:NSX[3].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL1_kVAr,lo:=5160,hi:=5161); | [6 empty] | 5161:NSX[3].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL2_kVAr,lo:=5162,hi:=5163); | [6 empty] | 5163:NSX[3].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL3_kVAr,lo:=5164,hi:=5165); | [6 empty] | 5165:NSX[3].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_FunReactivePowerTotal_kVAr,lo:=5166,hi:=5167); | [6 empty] | 5167:NSX[3].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_PowerFactorL1,lo:=5168,hi:=5169); | [6 empty] | 5169:NSX[3].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_PowerFactorL2,lo:=5170,hi:=5171); | [6 empty] | 5171:NSX[3].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_PowerFactorL3,lo:=5172,hi:=5173); | [6 empty] | 5173:NSX[3].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_PowerFactorTotal,lo:=5174,hi:=5175); | [6 empty] | 5175:NSX[3].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ReactivePowerL1_kVAr,lo:=5176,hi:=5177); | [6 empty] | 5177:NSX[3].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ReactivePowerL2_kVAr,lo:=5178,hi:=5179); | [6 empty] | 5179:NSX[3].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ReactivePowerL3_kVAr,lo:=5180,hi:=5181); | [6 empty] | 5181:NSX[3].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_ReactivePowerTotal_kVAr,lo:=5182,hi:=5183); | [6 empty] | 5183:NSX[3].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDI1_P,lo:=5184,hi:=5185); | [6 empty] | 5185:NSX[3].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDI2_P,lo:=5186,hi:=5187); | [6 empty] | 5187:NSX[3].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDI3_P,lo:=5188,hi:=5189); | [6 empty] | 5189:NSX[3].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV12_P,lo:=5190,hi:=5191); | [6 empty] | 5191:NSX[3].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV1N_P,lo:=5192,hi:=5193); | [6 empty] | 5193:NSX[3].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV23_P,lo:=5194,hi:=5195); | [6 empty] | 5195:NSX[3].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV2N_P,lo:=5196,hi:=5197); | [6 empty] | 5197:NSX[3].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV31_P,lo:=5198,hi:=5199); | [6 empty] | 5199:NSX[3].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_THDV3N_P,lo:=5200,hi:=5201); | [6 empty] | 5201:NSX[3].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageAvgPhToN_V,lo:=5202,hi:=5203); | [6 empty] | 5203:NSX[3].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageAvgPhToPh_V,lo:=5204,hi:=5205); | [6 empty] | 5205:NSX[3].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV12_P,lo:=5206,hi:=5207); | [6 empty] | 5207:NSX[3].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV1N_P,lo:=5208,hi:=5209); | [6 empty] | 5209:NSX[3].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV23_P,lo:=5210,hi:=5211); | [6 empty] | 5211:NSX[3].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV2N_P,lo:=5212,hi:=5213); | [6 empty] | 5213:NSX[3].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV31_P,lo:=5214,hi:=5215); | [6 empty] | 5215:NSX[3].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageUnbV3N_P,lo:=5216,hi:=5217); | [6 empty] | 5217:NSX[3].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV12_V,lo:=5218,hi:=5219); | [6 empty] | 5219:NSX[3].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV1N_V,lo:=5220,hi:=5221); | [6 empty] | 5221:NSX[3].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV23_V,lo:=5222,hi:=5223); | [6 empty] | 5223:NSX[3].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV2N_V,lo:=5224,hi:=5225); | [6 empty] | 5225:NSX[3].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV31_V,lo:=5226,hi:=5227); | [6 empty] | 5227:NSX[3].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MAX_VoltageV3N_V,lo:=5228,hi:=5229); | [6 empty] | 5229:NSX[3].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ActivePowerL1_kW,lo:=5230,hi:=5231); | [6 empty] | 5231:NSX[3].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ActivePowerL2_kW,lo:=5232,hi:=5233); | [6 empty] | 5233:NSX[3].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ActivePowerL3_kW,lo:=5234,hi:=5235); | [6 empty] | 5235:NSX[3].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ActivePowerTotal_kW,lo:=5236,hi:=5237); | [6 empty] | 5237:NSX[3].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL1_kVA,lo:=5238,hi:=5239); | [6 empty] | 5239:NSX[3].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL2_kVA,lo:=5240,hi:=5241); | [6 empty] | 5241:NSX[3].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL3_kVA,lo:=5242,hi:=5243); | [6 empty] | 5243:NSX[3].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ApparetnPowerTotal_kVA,lo:=5244,hi:=5245); | [6 empty] | 5245:NSX[3].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CosFL1,lo:=5246,hi:=5247); | [6 empty] | 5247:NSX[3].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CosFL2,lo:=5248,hi:=5249); | [6 empty] | 5249:NSX[3].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CosFL3,lo:=5250,hi:=5251); | [6 empty] | 5251:NSX[3].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CosFTotal,lo:=5252,hi:=5253); | [6 empty] | 5253:NSX[3].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentAvgI1I2I3_A,lo:=5254,hi:=5255); | [6 empty] | 5255:NSX[3].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentL1_A,lo:=5256,hi:=5257); | [6 empty] | 5257:NSX[3].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentL2_A,lo:=5258,hi:=5259); | [6 empty] | 5259:NSX[3].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentL3_A,lo:=5260,hi:=5261); | [6 empty] | 5261:NSX[3].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentMaxL1L2L3N_A,lo:=5262,hi:=5263); | [6 empty] | 5263:NSX[3].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_CurrentN_A,lo:=5264,hi:=5265); | [6 empty] | 5265:NSX[3].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_DistortionPowerL1_kVAr,lo:=5266,hi:=5267); | [6 empty] | 5267:NSX[3].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_DistortionPowerL2_kVAr,lo:=5268,hi:=5269); | [6 empty] | 5269:NSX[3].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_DistortionPowerL3_kVAr,lo:=5270,hi:=5271); | [6 empty] | 5271:NSX[3].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_DistortionPowerTotal_kVAr,lo:=5272,hi:=5273); | [6 empty] | 5273:NSX[3].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_Frequency_Hz,lo:=5274,hi:=5275); | [6 empty] | 5275:NSX[3].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL1_kVAr,lo:=5276,hi:=5277); | [6 empty] | 5277:NSX[3].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL2_kVAr,lo:=5278,hi:=5279); | [6 empty] | 5279:NSX[3].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL3_kVAr,lo:=5280,hi:=5281); | [6 empty] | 5281:NSX[3].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_FunReactivePowerTotal_kVAr,lo:=5282,hi:=5283); | [6 empty] | 5283:NSX[3].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_PowerFactorL1,lo:=5284,hi:=5285); | [6 empty] | 5285:NSX[3].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_PowerFactorL2,lo:=5286,hi:=5287); | [6 empty] | 5287:NSX[3].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_PowerFactorL3,lo:=5288,hi:=5289); | [6 empty] | 5289:NSX[3].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_PowerFactorTotal,lo:=5290,hi:=5291); | [6 empty] | 5291:NSX[3].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ReactivePowerL1_kVAr,lo:=5292,hi:=5293); | [6 empty] | 5293:NSX[3].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ReactivePowerL2_kVAr,lo:=5294,hi:=5295); | [6 empty] | 5295:NSX[3].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ReactivePowerL3_kVAr,lo:=5296,hi:=5297); | [6 empty] | 5297:NSX[3].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_ReactivePowerTotal_kVAr,lo:=5298,hi:=5299); | [6 empty] | 5299:NSX[3].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDI1_P,lo:=5300,hi:=5301); | [6 empty] | 5301:NSX[3].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDI2_P,lo:=5302,hi:=5303); | [6 empty] | 5303:NSX[3].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDI3_P,lo:=5304,hi:=5305); | [6 empty] | 5305:NSX[3].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV12_P,lo:=5306,hi:=5307); | [6 empty] | 5307:NSX[3].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV1N_P,lo:=5308,hi:=5309); | [6 empty] | 5309:NSX[3].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV23_P,lo:=5310,hi:=5311); | [6 empty] | 5311:NSX[3].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV2N_P,lo:=5312,hi:=5313); | [6 empty] | 5313:NSX[3].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV31_P,lo:=5314,hi:=5315); | [6 empty] | 5315:NSX[3].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_THDV3N_P,lo:=5316,hi:=5317); | [6 empty] | 5317:NSX[3].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageAvgPhToN_V,lo:=5318,hi:=5319); | [6 empty] | 5319:NSX[3].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageAvgPhToPh_V,lo:=5320,hi:=5321); | [6 empty] | 5321:NSX[3].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV12_P,lo:=5322,hi:=5323); | [6 empty] | 5323:NSX[3].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV1N_P,lo:=5324,hi:=5325); | [6 empty] | 5325:NSX[3].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV23_P,lo:=5326,hi:=5327); | [6 empty] | 5327:NSX[3].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV2N_P,lo:=5328,hi:=5329); | [6 empty] | 5329:NSX[3].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV31_P,lo:=5330,hi:=5331); | [6 empty] | 5331:NSX[3].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageUnbV3N_P,lo:=5332,hi:=5333); | [6 empty] | 5333:NSX[3].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV12_V,lo:=5334,hi:=5335); | [6 empty] | 5335:NSX[3].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV1N_V,lo:=5336,hi:=5337); | [6 empty] | 5337:NSX[3].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV23_V,lo:=5338,hi:=5339); | [6 empty] | 5339:NSX[3].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV2N_V,lo:=5340,hi:=5341); | [6 empty] | 5341:NSX[3].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV31_V,lo:=5342,hi:=5343); | [6 empty] | 5343:NSX[3].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].MIN_VoltageV3N_V,lo:=5344,hi:=5345); | [6 empty] | 5345:NSX[3].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].PowerFactorL1,lo:=5346,hi:=5347); | [6 empty] | 5347:NSX[3].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].PowerFactorL2,lo:=5348,hi:=5349); | [6 empty] | 5349:NSX[3].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].PowerFactorL3,lo:=5350,hi:=5351); | [6 empty] | 5351:NSX[3].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].PowerFactorTotal,lo:=5352,hi:=5353); | [6 empty] | 5353:NSX[3].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_D,lo:=5354,hi:=5355); | [6 empty] | 5355:NSX[3].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_D_SCADA,lo:=5356,hi:=5357); | [6 empty] | 5357:NSX[3].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_D_TEMP,lo:=5358,hi:=5359); | [6 empty] | 5359:NSX[3].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_M,lo:=5360,hi:=5361); | [6 empty] | 5361:NSX[3].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_M_SCADA,lo:=5362,hi:=5363); | [6 empty] | 5363:NSX[3].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_M_TEMP,lo:=5364,hi:=5365); | [6 empty] | 5365:NSX[3].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_T,lo:=5366,hi:=5367); | [6 empty] | 5367:NSX[3].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_T_SCADA,lo:=5368,hi:=5369); | [6 empty] | 5369:NSX[3].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].RazEner_T_TEMP,lo:=5370,hi:=5371); | [6 empty] | 5371:NSX[3].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactiveEnergy_kVArh,lo:=5372,hi:=5373); | [6 empty] | 5373:NSX[3].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactiveNegativeEnergy_kVArh,lo:=5374,hi:=5375); | [6 empty] | 5375:NSX[3].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePositiveEnergy_kVArh,lo:=5376,hi:=5377); | [6 empty] | 5377:NSX[3].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerDemand_kVAr,lo:=5378,hi:=5379); | [6 empty] | 5379:NSX[3].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerL1_kVAr,lo:=5380,hi:=5381); | [6 empty] | 5381:NSX[3].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerL2_kVAr,lo:=5382,hi:=5383); | [6 empty] | 5383:NSX[3].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerL3_kVAr,lo:=5384,hi:=5385); | [6 empty] | 5385:NSX[3].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerMaxDemand_kVAr,lo:=5386,hi:=5387); | [6 empty] | 5387:NSX[3].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].ReactivePowerTotal_kVAr,lo:=5388,hi:=5389); | [6 empty] | 5389:NSX[3].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDI1_P,lo:=5390,hi:=5391); | [6 empty] | 5391:NSX[3].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDI2_P,lo:=5392,hi:=5393); | [6 empty] | 5393:NSX[3].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDI3_P,lo:=5394,hi:=5395); | [6 empty] | 5395:NSX[3].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV12_P,lo:=5396,hi:=5397); | [6 empty] | 5397:NSX[3].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV1N_P,lo:=5398,hi:=5399); | [6 empty] | 5399:NSX[3].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV23_P,lo:=5400,hi:=5401); | [6 empty] | 5401:NSX[3].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV2N_P,lo:=5402,hi:=5403); | [6 empty] | 5403:NSX[3].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV31_P,lo:=5404,hi:=5405); | [6 empty] | 5405:NSX[3].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].THDV3N_P,lo:=5406,hi:=5407); | [6 empty] | 5407:NSX[3].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageAvgPhToN_V,lo:=5408,hi:=5409); | [6 empty] | 5409:NSX[3].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageAvgPhToPh_V,lo:=5410,hi:=5411); | [6 empty] | 5411:NSX[3].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV12_P,lo:=5412,hi:=5413); | [6 empty] | 5413:NSX[3].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV1N_P,lo:=5414,hi:=5415); | [6 empty] | 5415:NSX[3].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV23_P,lo:=5416,hi:=5417); | [6 empty] | 5417:NSX[3].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV2N_P,lo:=5418,hi:=5419); | [6 empty] | 5419:NSX[3].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV31_P,lo:=5420,hi:=5421); | [6 empty] | 5421:NSX[3].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageUnbV3N_P,lo:=5422,hi:=5423); | [6 empty] | 5423:NSX[3].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV12_V,lo:=5424,hi:=5425); | [6 empty] | 5425:NSX[3].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV1N_V,lo:=5426,hi:=5427); | [6 empty] | 5427:NSX[3].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV23_V,lo:=5428,hi:=5429); | [6 empty] | 5429:NSX[3].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV2N_V,lo:=5430,hi:=5431); | [6 empty] | 5431:NSX[3].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV31_V,lo:=5432,hi:=5433); | [6 empty] | 5433:NSX[3].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[3].VoltageV3N_V,lo:=5434,hi:=5435); | [6 empty] | 5435:NSX[3].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActiveEnergy_kWh,lo:=5436,hi:=5437); | [6 empty] | 5437:NSX[4].ActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActiveNegativeEnergy_kWh,lo:=5438,hi:=5439); | [6 empty] | 5439:NSX[4].ActiveNegativeEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePositiveEnergy_kWh,lo:=5440,hi:=5441); | [6 empty] | 5441:NSX[4].ActivePositiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerDemand_kW,lo:=5442,hi:=5443); | [6 empty] | 5443:NSX[4].ActivePowerDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerL1_kW,lo:=5444,hi:=5445); | [6 empty] | 5445:NSX[4].ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerL2_kW,lo:=5446,hi:=5447); | [6 empty] | 5447:NSX[4].ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerL3_kW,lo:=5448,hi:=5449); | [6 empty] | 5449:NSX[4].ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerMaxDemand_kW,lo:=5450,hi:=5451); | [6 empty] | 5451:NSX[4].ActivePowerMaxDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ActivePowerTotal_kW,lo:=5452,hi:=5453); | [6 empty] | 5453:NSX[4].ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparentEnergy_kVAh,lo:=5454,hi:=5455); | [6 empty] | 5455:NSX[4].ApparentEnergy_kVAh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparentPowerDemand_kVA,lo:=5456,hi:=5457); | [6 empty] | 5457:NSX[4].ApparentPowerDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparentPowerMaxDemand_kVA,lo:=5458,hi:=5459); | [6 empty] | 5459:NSX[4].ApparentPowerMaxDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparetnPowerL1_kVA,lo:=5460,hi:=5461); | [6 empty] | 5461:NSX[4].ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparetnPowerL2_kVA,lo:=5462,hi:=5463); | [6 empty] | 5463:NSX[4].ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparetnPowerL3_kVA,lo:=5464,hi:=5465); | [6 empty] | 5465:NSX[4].ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ApparetnPowerTotal_kVA,lo:=5466,hi:=5467); | [6 empty] | 5467:NSX[4].ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CosFL1,lo:=5468,hi:=5469); | [6 empty] | 5469:NSX[4].CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CosFL2,lo:=5470,hi:=5471); | [6 empty] | 5471:NSX[4].CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CosFL3,lo:=5472,hi:=5473); | [6 empty] | 5473:NSX[4].CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CosFTotal,lo:=5474,hi:=5475); | [6 empty] | 5475:NSX[4].CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CumulNegativeActiveEnergy_kWh,lo:=5476,hi:=5477); | [6 empty] | 5477:NSX[4].CumulNegativeActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CumulPositiveActiveEnergy_kWh,lo:=5478,hi:=5479); | [6 empty] | 5479:NSX[4].CumulPositiveActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentAvgI1I2I3_A,lo:=5480,hi:=5481); | [6 empty] | 5481:NSX[4].CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandL1_A,lo:=5482,hi:=5483); | [6 empty] | 5483:NSX[4].CurrentDemandL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandL2_A,lo:=5484,hi:=5485); | [6 empty] | 5485:NSX[4].CurrentDemandL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandL3_A,lo:=5486,hi:=5487); | [6 empty] | 5487:NSX[4].CurrentDemandL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandMaxL1_A,lo:=5488,hi:=5489); | [6 empty] | 5489:NSX[4].CurrentDemandMaxL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandMaxL2_A,lo:=5490,hi:=5491); | [6 empty] | 5491:NSX[4].CurrentDemandMaxL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandMaxL3_A,lo:=5492,hi:=5493); | [6 empty] | 5493:NSX[4].CurrentDemandMaxL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandMaxN_A,lo:=5494,hi:=5495); | [6 empty] | 5495:NSX[4].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentDemandN_A,lo:=5496,hi:=5497); | [6 empty] | 5497:NSX[4].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentL1_A,lo:=5498,hi:=5499); | [6 empty] | 5499:NSX[4].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentL2_A,lo:=5500,hi:=5501); | [6 empty] | 5501:NSX[4].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentL3_A,lo:=5502,hi:=5503); | [6 empty] | 5503:NSX[4].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentN_A,lo:=5504,hi:=5505); | [6 empty] | 5505:NSX[4].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentUnbI1_P,lo:=5506,hi:=5507); | [6 empty] | 5507:NSX[4].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentUnbI2_P,lo:=5508,hi:=5509); | [6 empty] | 5509:NSX[4].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentUnbI3_P,lo:=5510,hi:=5511); | [6 empty] | 5511:NSX[4].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].CurrentUnbN_P,lo:=5512,hi:=5513); | [6 empty] | 5513:NSX[4].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].DelovnaEnergija_TEMP,lo:=5514,hi:=5515); | [6 empty] | 5515:NSX[4].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].DistortionPowerL1_kVAr,lo:=5516,hi:=5517); | [6 empty] | 5517:NSX[4].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].DistortionPowerL2_kVAr,lo:=5518,hi:=5519); | [6 empty] | 5519:NSX[4].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].DistortionPowerL3_kVAr,lo:=5520,hi:=5521); | [6 empty] | 5521:NSX[4].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].DistortionPowerTotal_kVAr,lo:=5522,hi:=5523); | [6 empty] | 5523:NSX[4].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].Frequency_Hz,lo:=5524,hi:=5525); | [6 empty] | 5525:NSX[4].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].FunReactivePowerL1_kVAr,lo:=5526,hi:=5527); | [6 empty] | 5527:NSX[4].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].FunReactivePowerL2_kVAr,lo:=5528,hi:=5529); | [6 empty] | 5529:NSX[4].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].FunReactivePowerL3_kVAr,lo:=5530,hi:=5531); | [6 empty] | 5531:NSX[4].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].FunReactivePowerTotal_kVAr,lo:=5532,hi:=5533); | [6 empty] | 5533:NSX[4].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ActivePowerL1_kW,lo:=5534,hi:=5535); | [6 empty] | 5535:NSX[4].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ActivePowerL2_kW,lo:=5536,hi:=5537); | [6 empty] | 5537:NSX[4].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ActivePowerL3_kW,lo:=5538,hi:=5539); | [6 empty] | 5539:NSX[4].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ActivePowerTotal_kW,lo:=5540,hi:=5541); | [6 empty] | 5541:NSX[4].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL1_kVA,lo:=5542,hi:=5543); | [6 empty] | 5543:NSX[4].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL2_kVA,lo:=5544,hi:=5545); | [6 empty] | 5545:NSX[4].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL3_kVA,lo:=5546,hi:=5547); | [6 empty] | 5547:NSX[4].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ApparetnPowerTotal_kVA,lo:=5548,hi:=5549); | [6 empty] | 5549:NSX[4].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CosFL1,lo:=5550,hi:=5551); | [6 empty] | 5551:NSX[4].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CosFL2,lo:=5552,hi:=5553); | [6 empty] | 5553:NSX[4].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CosFL3,lo:=5554,hi:=5555); | [6 empty] | 5555:NSX[4].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CosFTotal,lo:=5556,hi:=5557); | [6 empty] | 5557:NSX[4].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentAvgI1I2I3_A,lo:=5558,hi:=5559); | [6 empty] | 5559:NSX[4].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentL1_A,lo:=5560,hi:=5561); | [6 empty] | 5561:NSX[4].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentL2_A,lo:=5562,hi:=5563); | [6 empty] | 5563:NSX[4].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentL3_A,lo:=5564,hi:=5565); | [6 empty] | 5565:NSX[4].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentMaxL1L2L3N_A,lo:=5566,hi:=5567); | [6 empty] | 5567:NSX[4].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_CurrentN_A,lo:=5568,hi:=5569); | [6 empty] | 5569:NSX[4].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_DistortionPowerL1_kVAr,lo:=5570,hi:=5571); | [6 empty] | 5571:NSX[4].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_DistortionPowerL2_kVAr,lo:=5572,hi:=5573); | [6 empty] | 5573:NSX[4].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_DistortionPowerL3_kVAr,lo:=5574,hi:=5575); | [6 empty] | 5575:NSX[4].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_DistortionPowerTotal_kVAr,lo:=5576,hi:=5577); | [6 empty] | 5577:NSX[4].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_Frequency_Hz,lo:=5578,hi:=5579); | [6 empty] | 5579:NSX[4].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL1_kVAr,lo:=5580,hi:=5581); | [6 empty] | 5581:NSX[4].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL2_kVAr,lo:=5582,hi:=5583); | [6 empty] | 5583:NSX[4].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL3_kVAr,lo:=5584,hi:=5585); | [6 empty] | 5585:NSX[4].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_FunReactivePowerTotal_kVAr,lo:=5586,hi:=5587); | [6 empty] | 5587:NSX[4].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_PowerFactorL1,lo:=5588,hi:=5589); | [6 empty] | 5589:NSX[4].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_PowerFactorL2,lo:=5590,hi:=5591); | [6 empty] | 5591:NSX[4].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_PowerFactorL3,lo:=5592,hi:=5593); | [6 empty] | 5593:NSX[4].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_PowerFactorTotal,lo:=5594,hi:=5595); | [6 empty] | 5595:NSX[4].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ReactivePowerL1_kVAr,lo:=5596,hi:=5597); | [6 empty] | 5597:NSX[4].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ReactivePowerL2_kVAr,lo:=5598,hi:=5599); | [6 empty] | 5599:NSX[4].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ReactivePowerL3_kVAr,lo:=5600,hi:=5601); | [6 empty] | 5601:NSX[4].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_ReactivePowerTotal_kVAr,lo:=5602,hi:=5603); | [6 empty] | 5603:NSX[4].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDI1_P,lo:=5604,hi:=5605); | [6 empty] | 5605:NSX[4].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDI2_P,lo:=5606,hi:=5607); | [6 empty] | 5607:NSX[4].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDI3_P,lo:=5608,hi:=5609); | [6 empty] | 5609:NSX[4].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV12_P,lo:=5610,hi:=5611); | [6 empty] | 5611:NSX[4].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV1N_P,lo:=5612,hi:=5613); | [6 empty] | 5613:NSX[4].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV23_P,lo:=5614,hi:=5615); | [6 empty] | 5615:NSX[4].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV2N_P,lo:=5616,hi:=5617); | [6 empty] | 5617:NSX[4].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV31_P,lo:=5618,hi:=5619); | [6 empty] | 5619:NSX[4].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_THDV3N_P,lo:=5620,hi:=5621); | [6 empty] | 5621:NSX[4].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageAvgPhToN_V,lo:=5622,hi:=5623); | [6 empty] | 5623:NSX[4].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageAvgPhToPh_V,lo:=5624,hi:=5625); | [6 empty] | 5625:NSX[4].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV12_P,lo:=5626,hi:=5627); | [6 empty] | 5627:NSX[4].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV1N_P,lo:=5628,hi:=5629); | [6 empty] | 5629:NSX[4].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV23_P,lo:=5630,hi:=5631); | [6 empty] | 5631:NSX[4].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV2N_P,lo:=5632,hi:=5633); | [6 empty] | 5633:NSX[4].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV31_P,lo:=5634,hi:=5635); | [6 empty] | 5635:NSX[4].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageUnbV3N_P,lo:=5636,hi:=5637); | [6 empty] | 5637:NSX[4].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV12_V,lo:=5638,hi:=5639); | [6 empty] | 5639:NSX[4].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV1N_V,lo:=5640,hi:=5641); | [6 empty] | 5641:NSX[4].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV23_V,lo:=5642,hi:=5643); | [6 empty] | 5643:NSX[4].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV2N_V,lo:=5644,hi:=5645); | [6 empty] | 5645:NSX[4].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV31_V,lo:=5646,hi:=5647); | [6 empty] | 5647:NSX[4].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MAX_VoltageV3N_V,lo:=5648,hi:=5649); | [6 empty] | 5649:NSX[4].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ActivePowerL1_kW,lo:=5650,hi:=5651); | [6 empty] | 5651:NSX[4].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ActivePowerL2_kW,lo:=5652,hi:=5653); | [6 empty] | 5653:NSX[4].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ActivePowerL3_kW,lo:=5654,hi:=5655); | [6 empty] | 5655:NSX[4].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ActivePowerTotal_kW,lo:=5656,hi:=5657); | [6 empty] | 5657:NSX[4].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL1_kVA,lo:=5658,hi:=5659); | [6 empty] | 5659:NSX[4].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL2_kVA,lo:=5660,hi:=5661); | [6 empty] | 5661:NSX[4].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL3_kVA,lo:=5662,hi:=5663); | [6 empty] | 5663:NSX[4].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ApparetnPowerTotal_kVA,lo:=5664,hi:=5665); | [6 empty] | 5665:NSX[4].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CosFL1,lo:=5666,hi:=5667); | [6 empty] | 5667:NSX[4].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CosFL2,lo:=5668,hi:=5669); | [6 empty] | 5669:NSX[4].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CosFL3,lo:=5670,hi:=5671); | [6 empty] | 5671:NSX[4].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CosFTotal,lo:=5672,hi:=5673); | [6 empty] | 5673:NSX[4].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentAvgI1I2I3_A,lo:=5674,hi:=5675); | [6 empty] | 5675:NSX[4].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentL1_A,lo:=5676,hi:=5677); | [6 empty] | 5677:NSX[4].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentL2_A,lo:=5678,hi:=5679); | [6 empty] | 5679:NSX[4].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentL3_A,lo:=5680,hi:=5681); | [6 empty] | 5681:NSX[4].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentMaxL1L2L3N_A,lo:=5682,hi:=5683); | [6 empty] | 5683:NSX[4].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_CurrentN_A,lo:=5684,hi:=5685); | [6 empty] | 5685:NSX[4].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_DistortionPowerL1_kVAr,lo:=5686,hi:=5687); | [6 empty] | 5687:NSX[4].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_DistortionPowerL2_kVAr,lo:=5688,hi:=5689); | [6 empty] | 5689:NSX[4].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_DistortionPowerL3_kVAr,lo:=5690,hi:=5691); | [6 empty] | 5691:NSX[4].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_DistortionPowerTotal_kVAr,lo:=5692,hi:=5693); | [6 empty] | 5693:NSX[4].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_Frequency_Hz,lo:=5694,hi:=5695); | [6 empty] | 5695:NSX[4].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL1_kVAr,lo:=5696,hi:=5697); | [6 empty] | 5697:NSX[4].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL2_kVAr,lo:=5698,hi:=5699); | [6 empty] | 5699:NSX[4].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL3_kVAr,lo:=5700,hi:=5701); | [6 empty] | 5701:NSX[4].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_FunReactivePowerTotal_kVAr,lo:=5702,hi:=5703); | [6 empty] | 5703:NSX[4].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_PowerFactorL1,lo:=5704,hi:=5705); | [6 empty] | 5705:NSX[4].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_PowerFactorL2,lo:=5706,hi:=5707); | [6 empty] | 5707:NSX[4].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_PowerFactorL3,lo:=5708,hi:=5709); | [6 empty] | 5709:NSX[4].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_PowerFactorTotal,lo:=5710,hi:=5711); | [6 empty] | 5711:NSX[4].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ReactivePowerL1_kVAr,lo:=5712,hi:=5713); | [6 empty] | 5713:NSX[4].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ReactivePowerL2_kVAr,lo:=5714,hi:=5715); | [6 empty] | 5715:NSX[4].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ReactivePowerL3_kVAr,lo:=5716,hi:=5717); | [6 empty] | 5717:NSX[4].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_ReactivePowerTotal_kVAr,lo:=5718,hi:=5719); | [6 empty] | 5719:NSX[4].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDI1_P,lo:=5720,hi:=5721); | [6 empty] | 5721:NSX[4].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDI2_P,lo:=5722,hi:=5723); | [6 empty] | 5723:NSX[4].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDI3_P,lo:=5724,hi:=5725); | [6 empty] | 5725:NSX[4].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV12_P,lo:=5726,hi:=5727); | [6 empty] | 5727:NSX[4].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV1N_P,lo:=5728,hi:=5729); | [6 empty] | 5729:NSX[4].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV23_P,lo:=5730,hi:=5731); | [6 empty] | 5731:NSX[4].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV2N_P,lo:=5732,hi:=5733); | [6 empty] | 5733:NSX[4].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV31_P,lo:=5734,hi:=5735); | [6 empty] | 5735:NSX[4].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_THDV3N_P,lo:=5736,hi:=5737); | [6 empty] | 5737:NSX[4].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageAvgPhToN_V,lo:=5738,hi:=5739); | [6 empty] | 5739:NSX[4].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageAvgPhToPh_V,lo:=5740,hi:=5741); | [6 empty] | 5741:NSX[4].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV12_P,lo:=5742,hi:=5743); | [6 empty] | 5743:NSX[4].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV1N_P,lo:=5744,hi:=5745); | [6 empty] | 5745:NSX[4].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV23_P,lo:=5746,hi:=5747); | [6 empty] | 5747:NSX[4].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV2N_P,lo:=5748,hi:=5749); | [6 empty] | 5749:NSX[4].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV31_P,lo:=5750,hi:=5751); | [6 empty] | 5751:NSX[4].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageUnbV3N_P,lo:=5752,hi:=5753); | [6 empty] | 5753:NSX[4].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV12_V,lo:=5754,hi:=5755); | [6 empty] | 5755:NSX[4].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV1N_V,lo:=5756,hi:=5757); | [6 empty] | 5757:NSX[4].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV23_V,lo:=5758,hi:=5759); | [6 empty] | 5759:NSX[4].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV2N_V,lo:=5760,hi:=5761); | [6 empty] | 5761:NSX[4].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV31_V,lo:=5762,hi:=5763); | [6 empty] | 5763:NSX[4].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].MIN_VoltageV3N_V,lo:=5764,hi:=5765); | [6 empty] | 5765:NSX[4].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].PowerFactorL1,lo:=5766,hi:=5767); | [6 empty] | 5767:NSX[4].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].PowerFactorL2,lo:=5768,hi:=5769); | [6 empty] | 5769:NSX[4].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].PowerFactorL3,lo:=5770,hi:=5771); | [6 empty] | 5771:NSX[4].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].PowerFactorTotal,lo:=5772,hi:=5773); | [6 empty] | 5773:NSX[4].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_D,lo:=5774,hi:=5775); | [6 empty] | 5775:NSX[4].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_D_SCADA,lo:=5776,hi:=5777); | [6 empty] | 5777:NSX[4].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_D_TEMP,lo:=5778,hi:=5779); | [6 empty] | 5779:NSX[4].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_M,lo:=5780,hi:=5781); | [6 empty] | 5781:NSX[4].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_M_SCADA,lo:=5782,hi:=5783); | [6 empty] | 5783:NSX[4].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_M_TEMP,lo:=5784,hi:=5785); | [6 empty] | 5785:NSX[4].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_T,lo:=5786,hi:=5787); | [6 empty] | 5787:NSX[4].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_T_SCADA,lo:=5788,hi:=5789); | [6 empty] | 5789:NSX[4].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].RazEner_T_TEMP,lo:=5790,hi:=5791); | [6 empty] | 5791:NSX[4].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactiveEnergy_kVArh,lo:=5792,hi:=5793); | [6 empty] | 5793:NSX[4].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactiveNegativeEnergy_kVArh,lo:=5794,hi:=5795); | [6 empty] | 5795:NSX[4].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePositiveEnergy_kVArh,lo:=5796,hi:=5797); | [6 empty] | 5797:NSX[4].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerDemand_kVAr,lo:=5798,hi:=5799); | [6 empty] | 5799:NSX[4].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerL1_kVAr,lo:=5800,hi:=5801); | [6 empty] | 5801:NSX[4].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerL2_kVAr,lo:=5802,hi:=5803); | [6 empty] | 5803:NSX[4].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerL3_kVAr,lo:=5804,hi:=5805); | [6 empty] | 5805:NSX[4].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerMaxDemand_kVAr,lo:=5806,hi:=5807); | [6 empty] | 5807:NSX[4].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].ReactivePowerTotal_kVAr,lo:=5808,hi:=5809); | [6 empty] | 5809:NSX[4].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDI1_P,lo:=5810,hi:=5811); | [6 empty] | 5811:NSX[4].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDI2_P,lo:=5812,hi:=5813); | [6 empty] | 5813:NSX[4].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDI3_P,lo:=5814,hi:=5815); | [6 empty] | 5815:NSX[4].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV12_P,lo:=5816,hi:=5817); | [6 empty] | 5817:NSX[4].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV1N_P,lo:=5818,hi:=5819); | [6 empty] | 5819:NSX[4].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV23_P,lo:=5820,hi:=5821); | [6 empty] | 5821:NSX[4].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV2N_P,lo:=5822,hi:=5823); | [6 empty] | 5823:NSX[4].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV31_P,lo:=5824,hi:=5825); | [6 empty] | 5825:NSX[4].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].THDV3N_P,lo:=5826,hi:=5827); | [6 empty] | 5827:NSX[4].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageAvgPhToN_V,lo:=5828,hi:=5829); | [6 empty] | 5829:NSX[4].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageAvgPhToPh_V,lo:=5830,hi:=5831); | [6 empty] | 5831:NSX[4].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV12_P,lo:=5832,hi:=5833); | [6 empty] | 5833:NSX[4].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV1N_P,lo:=5834,hi:=5835); | [6 empty] | 5835:NSX[4].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV23_P,lo:=5836,hi:=5837); | [6 empty] | 5837:NSX[4].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV2N_P,lo:=5838,hi:=5839); | [6 empty] | 5839:NSX[4].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV31_P,lo:=5840,hi:=5841); | [6 empty] | 5841:NSX[4].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageUnbV3N_P,lo:=5842,hi:=5843); | [6 empty] | 5843:NSX[4].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV12_V,lo:=5844,hi:=5845); | [6 empty] | 5845:NSX[4].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV1N_V,lo:=5846,hi:=5847); | [6 empty] | 5847:NSX[4].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV23_V,lo:=5848,hi:=5849); | [6 empty] | 5849:NSX[4].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV2N_V,lo:=5850,hi:=5851); | [6 empty] | 5851:NSX[4].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV31_V,lo:=5852,hi:=5853); | [6 empty] | 5853:NSX[4].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[4].VoltageV3N_V,lo:=5854,hi:=5855); | [6 empty] | 5855:NSX[4].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActiveEnergy_kWh,lo:=5856,hi:=5857); | [6 empty] | 5857:NSX[5].ActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActiveNegativeEnergy_kWh,lo:=5858,hi:=5859); | [6 empty] | 5859:NSX[5].ActiveNegativeEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePositiveEnergy_kWh,lo:=5860,hi:=5861); | [6 empty] | 5861:NSX[5].ActivePositiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerDemand_kW,lo:=5862,hi:=5863); | [6 empty] | 5863:NSX[5].ActivePowerDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerL1_kW,lo:=5864,hi:=5865); | [6 empty] | 5865:NSX[5].ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerL2_kW,lo:=5866,hi:=5867); | [6 empty] | 5867:NSX[5].ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerL3_kW,lo:=5868,hi:=5869); | [6 empty] | 5869:NSX[5].ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerMaxDemand_kW,lo:=5870,hi:=5871); | [6 empty] | 5871:NSX[5].ActivePowerMaxDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ActivePowerTotal_kW,lo:=5872,hi:=5873); | [6 empty] | 5873:NSX[5].ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparentEnergy_kVAh,lo:=5874,hi:=5875); | [6 empty] | 5875:NSX[5].ApparentEnergy_kVAh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparentPowerDemand_kVA,lo:=5876,hi:=5877); | [6 empty] | 5877:NSX[5].ApparentPowerDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparentPowerMaxDemand_kVA,lo:=5878,hi:=5879); | [6 empty] | 5879:NSX[5].ApparentPowerMaxDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparetnPowerL1_kVA,lo:=5880,hi:=5881); | [6 empty] | 5881:NSX[5].ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparetnPowerL2_kVA,lo:=5882,hi:=5883); | [6 empty] | 5883:NSX[5].ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparetnPowerL3_kVA,lo:=5884,hi:=5885); | [6 empty] | 5885:NSX[5].ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ApparetnPowerTotal_kVA,lo:=5886,hi:=5887); | [6 empty] | 5887:NSX[5].ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CosFL1,lo:=5888,hi:=5889); | [6 empty] | 5889:NSX[5].CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CosFL2,lo:=5890,hi:=5891); | [6 empty] | 5891:NSX[5].CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CosFL3,lo:=5892,hi:=5893); | [6 empty] | 5893:NSX[5].CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CosFTotal,lo:=5894,hi:=5895); | [6 empty] | 5895:NSX[5].CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CumulNegativeActiveEnergy_kWh,lo:=5896,hi:=5897); | [6 empty] | 5897:NSX[5].CumulNegativeActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CumulPositiveActiveEnergy_kWh,lo:=5898,hi:=5899); | [6 empty] | 5899:NSX[5].CumulPositiveActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentAvgI1I2I3_A,lo:=5900,hi:=5901); | [6 empty] | 5901:NSX[5].CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandL1_A,lo:=5902,hi:=5903); | [6 empty] | 5903:NSX[5].CurrentDemandL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandL2_A,lo:=5904,hi:=5905); | [6 empty] | 5905:NSX[5].CurrentDemandL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandL3_A,lo:=5906,hi:=5907); | [6 empty] | 5907:NSX[5].CurrentDemandL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandMaxL1_A,lo:=5908,hi:=5909); | [6 empty] | 5909:NSX[5].CurrentDemandMaxL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandMaxL2_A,lo:=5910,hi:=5911); | [6 empty] | 5911:NSX[5].CurrentDemandMaxL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandMaxL3_A,lo:=5912,hi:=5913); | [6 empty] | 5913:NSX[5].CurrentDemandMaxL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandMaxN_A,lo:=5914,hi:=5915); | [6 empty] | 5915:NSX[5].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentDemandN_A,lo:=5916,hi:=5917); | [6 empty] | 5917:NSX[5].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentL1_A,lo:=5918,hi:=5919); | [6 empty] | 5919:NSX[5].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentL2_A,lo:=5920,hi:=5921); | [6 empty] | 5921:NSX[5].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentL3_A,lo:=5922,hi:=5923); | [6 empty] | 5923:NSX[5].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentN_A,lo:=5924,hi:=5925); | [6 empty] | 5925:NSX[5].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentUnbI1_P,lo:=5926,hi:=5927); | [6 empty] | 5927:NSX[5].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentUnbI2_P,lo:=5928,hi:=5929); | [6 empty] | 5929:NSX[5].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentUnbI3_P,lo:=5930,hi:=5931); | [6 empty] | 5931:NSX[5].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].CurrentUnbN_P,lo:=5932,hi:=5933); | [6 empty] | 5933:NSX[5].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].DelovnaEnergija_TEMP,lo:=5934,hi:=5935); | [6 empty] | 5935:NSX[5].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].DistortionPowerL1_kVAr,lo:=5936,hi:=5937); | [6 empty] | 5937:NSX[5].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].DistortionPowerL2_kVAr,lo:=5938,hi:=5939); | [6 empty] | 5939:NSX[5].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].DistortionPowerL3_kVAr,lo:=5940,hi:=5941); | [6 empty] | 5941:NSX[5].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].DistortionPowerTotal_kVAr,lo:=5942,hi:=5943); | [6 empty] | 5943:NSX[5].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].Frequency_Hz,lo:=5944,hi:=5945); | [6 empty] | 5945:NSX[5].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].FunReactivePowerL1_kVAr,lo:=5946,hi:=5947); | [6 empty] | 5947:NSX[5].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].FunReactivePowerL2_kVAr,lo:=5948,hi:=5949); | [6 empty] | 5949:NSX[5].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].FunReactivePowerL3_kVAr,lo:=5950,hi:=5951); | [6 empty] | 5951:NSX[5].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].FunReactivePowerTotal_kVAr,lo:=5952,hi:=5953); | [6 empty] | 5953:NSX[5].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ActivePowerL1_kW,lo:=5954,hi:=5955); | [6 empty] | 5955:NSX[5].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ActivePowerL2_kW,lo:=5956,hi:=5957); | [6 empty] | 5957:NSX[5].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ActivePowerL3_kW,lo:=5958,hi:=5959); | [6 empty] | 5959:NSX[5].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ActivePowerTotal_kW,lo:=5960,hi:=5961); | [6 empty] | 5961:NSX[5].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL1_kVA,lo:=5962,hi:=5963); | [6 empty] | 5963:NSX[5].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL2_kVA,lo:=5964,hi:=5965); | [6 empty] | 5965:NSX[5].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL3_kVA,lo:=5966,hi:=5967); | [6 empty] | 5967:NSX[5].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ApparetnPowerTotal_kVA,lo:=5968,hi:=5969); | [6 empty] | 5969:NSX[5].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CosFL1,lo:=5970,hi:=5971); | [6 empty] | 5971:NSX[5].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CosFL2,lo:=5972,hi:=5973); | [6 empty] | 5973:NSX[5].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CosFL3,lo:=5974,hi:=5975); | [6 empty] | 5975:NSX[5].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CosFTotal,lo:=5976,hi:=5977); | [6 empty] | 5977:NSX[5].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentAvgI1I2I3_A,lo:=5978,hi:=5979); | [6 empty] | 5979:NSX[5].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentL1_A,lo:=5980,hi:=5981); | [6 empty] | 5981:NSX[5].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentL2_A,lo:=5982,hi:=5983); | [6 empty] | 5983:NSX[5].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentL3_A,lo:=5984,hi:=5985); | [6 empty] | 5985:NSX[5].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentMaxL1L2L3N_A,lo:=5986,hi:=5987); | [6 empty] | 5987:NSX[5].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_CurrentN_A,lo:=5988,hi:=5989); | [6 empty] | 5989:NSX[5].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_DistortionPowerL1_kVAr,lo:=5990,hi:=5991); | [6 empty] | 5991:NSX[5].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_DistortionPowerL2_kVAr,lo:=5992,hi:=5993); | [6 empty] | 5993:NSX[5].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_DistortionPowerL3_kVAr,lo:=5994,hi:=5995); | [6 empty] | 5995:NSX[5].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_DistortionPowerTotal_kVAr,lo:=5996,hi:=5997); | [6 empty] | 5997:NSX[5].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_Frequency_Hz,lo:=5998,hi:=5999); | [6 empty] | 5999:NSX[5].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL1_kVAr,lo:=6000,hi:=6001); | [6 empty] | 6001:NSX[5].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL2_kVAr,lo:=6002,hi:=6003); | [6 empty] | 6003:NSX[5].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL3_kVAr,lo:=6004,hi:=6005); | [6 empty] | 6005:NSX[5].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_FunReactivePowerTotal_kVAr,lo:=6006,hi:=6007); | [6 empty] | 6007:NSX[5].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_PowerFactorL1,lo:=6008,hi:=6009); | [6 empty] | 6009:NSX[5].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_PowerFactorL2,lo:=6010,hi:=6011); | [6 empty] | 6011:NSX[5].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_PowerFactorL3,lo:=6012,hi:=6013); | [6 empty] | 6013:NSX[5].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_PowerFactorTotal,lo:=6014,hi:=6015); | [6 empty] | 6015:NSX[5].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ReactivePowerL1_kVAr,lo:=6016,hi:=6017); | [6 empty] | 6017:NSX[5].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ReactivePowerL2_kVAr,lo:=6018,hi:=6019); | [6 empty] | 6019:NSX[5].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ReactivePowerL3_kVAr,lo:=6020,hi:=6021); | [6 empty] | 6021:NSX[5].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_ReactivePowerTotal_kVAr,lo:=6022,hi:=6023); | [6 empty] | 6023:NSX[5].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDI1_P,lo:=6024,hi:=6025); | [6 empty] | 6025:NSX[5].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDI2_P,lo:=6026,hi:=6027); | [6 empty] | 6027:NSX[5].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDI3_P,lo:=6028,hi:=6029); | [6 empty] | 6029:NSX[5].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV12_P,lo:=6030,hi:=6031); | [6 empty] | 6031:NSX[5].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV1N_P,lo:=6032,hi:=6033); | [6 empty] | 6033:NSX[5].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV23_P,lo:=6034,hi:=6035); | [6 empty] | 6035:NSX[5].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV2N_P,lo:=6036,hi:=6037); | [6 empty] | 6037:NSX[5].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV31_P,lo:=6038,hi:=6039); | [6 empty] | 6039:NSX[5].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_THDV3N_P,lo:=6040,hi:=6041); | [6 empty] | 6041:NSX[5].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageAvgPhToN_V,lo:=6042,hi:=6043); | [6 empty] | 6043:NSX[5].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageAvgPhToPh_V,lo:=6044,hi:=6045); | [6 empty] | 6045:NSX[5].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV12_P,lo:=6046,hi:=6047); | [6 empty] | 6047:NSX[5].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV1N_P,lo:=6048,hi:=6049); | [6 empty] | 6049:NSX[5].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV23_P,lo:=6050,hi:=6051); | [6 empty] | 6051:NSX[5].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV2N_P,lo:=6052,hi:=6053); | [6 empty] | 6053:NSX[5].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV31_P,lo:=6054,hi:=6055); | [6 empty] | 6055:NSX[5].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageUnbV3N_P,lo:=6056,hi:=6057); | [6 empty] | 6057:NSX[5].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV12_V,lo:=6058,hi:=6059); | [6 empty] | 6059:NSX[5].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV1N_V,lo:=6060,hi:=6061); | [6 empty] | 6061:NSX[5].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV23_V,lo:=6062,hi:=6063); | [6 empty] | 6063:NSX[5].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV2N_V,lo:=6064,hi:=6065); | [6 empty] | 6065:NSX[5].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV31_V,lo:=6066,hi:=6067); | [6 empty] | 6067:NSX[5].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MAX_VoltageV3N_V,lo:=6068,hi:=6069); | [6 empty] | 6069:NSX[5].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ActivePowerL1_kW,lo:=6070,hi:=6071); | [6 empty] | 6071:NSX[5].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ActivePowerL2_kW,lo:=6072,hi:=6073); | [6 empty] | 6073:NSX[5].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ActivePowerL3_kW,lo:=6074,hi:=6075); | [6 empty] | 6075:NSX[5].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ActivePowerTotal_kW,lo:=6076,hi:=6077); | [6 empty] | 6077:NSX[5].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL1_kVA,lo:=6078,hi:=6079); | [6 empty] | 6079:NSX[5].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL2_kVA,lo:=6080,hi:=6081); | [6 empty] | 6081:NSX[5].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL3_kVA,lo:=6082,hi:=6083); | [6 empty] | 6083:NSX[5].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ApparetnPowerTotal_kVA,lo:=6084,hi:=6085); | [6 empty] | 6085:NSX[5].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CosFL1,lo:=6086,hi:=6087); | [6 empty] | 6087:NSX[5].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CosFL2,lo:=6088,hi:=6089); | [6 empty] | 6089:NSX[5].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CosFL3,lo:=6090,hi:=6091); | [6 empty] | 6091:NSX[5].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CosFTotal,lo:=6092,hi:=6093); | [6 empty] | 6093:NSX[5].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentAvgI1I2I3_A,lo:=6094,hi:=6095); | [6 empty] | 6095:NSX[5].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentL1_A,lo:=6096,hi:=6097); | [6 empty] | 6097:NSX[5].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentL2_A,lo:=6098,hi:=6099); | [6 empty] | 6099:NSX[5].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentL3_A,lo:=6100,hi:=6101); | [6 empty] | 6101:NSX[5].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentMaxL1L2L3N_A,lo:=6102,hi:=6103); | [6 empty] | 6103:NSX[5].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_CurrentN_A,lo:=6104,hi:=6105); | [6 empty] | 6105:NSX[5].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_DistortionPowerL1_kVAr,lo:=6106,hi:=6107); | [6 empty] | 6107:NSX[5].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_DistortionPowerL2_kVAr,lo:=6108,hi:=6109); | [6 empty] | 6109:NSX[5].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_DistortionPowerL3_kVAr,lo:=6110,hi:=6111); | [6 empty] | 6111:NSX[5].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_DistortionPowerTotal_kVAr,lo:=6112,hi:=6113); | [6 empty] | 6113:NSX[5].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_Frequency_Hz,lo:=6114,hi:=6115); | [6 empty] | 6115:NSX[5].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL1_kVAr,lo:=6116,hi:=6117); | [6 empty] | 6117:NSX[5].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL2_kVAr,lo:=6118,hi:=6119); | [6 empty] | 6119:NSX[5].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL3_kVAr,lo:=6120,hi:=6121); | [6 empty] | 6121:NSX[5].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_FunReactivePowerTotal_kVAr,lo:=6122,hi:=6123); | [6 empty] | 6123:NSX[5].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_PowerFactorL1,lo:=6124,hi:=6125); | [6 empty] | 6125:NSX[5].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_PowerFactorL2,lo:=6126,hi:=6127); | [6 empty] | 6127:NSX[5].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_PowerFactorL3,lo:=6128,hi:=6129); | [6 empty] | 6129:NSX[5].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_PowerFactorTotal,lo:=6130,hi:=6131); | [6 empty] | 6131:NSX[5].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ReactivePowerL1_kVAr,lo:=6132,hi:=6133); | [6 empty] | 6133:NSX[5].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ReactivePowerL2_kVAr,lo:=6134,hi:=6135); | [6 empty] | 6135:NSX[5].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ReactivePowerL3_kVAr,lo:=6136,hi:=6137); | [6 empty] | 6137:NSX[5].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_ReactivePowerTotal_kVAr,lo:=6138,hi:=6139); | [6 empty] | 6139:NSX[5].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDI1_P,lo:=6140,hi:=6141); | [6 empty] | 6141:NSX[5].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDI2_P,lo:=6142,hi:=6143); | [6 empty] | 6143:NSX[5].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDI3_P,lo:=6144,hi:=6145); | [6 empty] | 6145:NSX[5].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV12_P,lo:=6146,hi:=6147); | [6 empty] | 6147:NSX[5].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV1N_P,lo:=6148,hi:=6149); | [6 empty] | 6149:NSX[5].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV23_P,lo:=6150,hi:=6151); | [6 empty] | 6151:NSX[5].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV2N_P,lo:=6152,hi:=6153); | [6 empty] | 6153:NSX[5].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV31_P,lo:=6154,hi:=6155); | [6 empty] | 6155:NSX[5].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_THDV3N_P,lo:=6156,hi:=6157); | [6 empty] | 6157:NSX[5].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageAvgPhToN_V,lo:=6158,hi:=6159); | [6 empty] | 6159:NSX[5].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageAvgPhToPh_V,lo:=6160,hi:=6161); | [6 empty] | 6161:NSX[5].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV12_P,lo:=6162,hi:=6163); | [6 empty] | 6163:NSX[5].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV1N_P,lo:=6164,hi:=6165); | [6 empty] | 6165:NSX[5].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV23_P,lo:=6166,hi:=6167); | [6 empty] | 6167:NSX[5].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV2N_P,lo:=6168,hi:=6169); | [6 empty] | 6169:NSX[5].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV31_P,lo:=6170,hi:=6171); | [6 empty] | 6171:NSX[5].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageUnbV3N_P,lo:=6172,hi:=6173); | [6 empty] | 6173:NSX[5].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV12_V,lo:=6174,hi:=6175); | [6 empty] | 6175:NSX[5].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV1N_V,lo:=6176,hi:=6177); | [6 empty] | 6177:NSX[5].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV23_V,lo:=6178,hi:=6179); | [6 empty] | 6179:NSX[5].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV2N_V,lo:=6180,hi:=6181); | [6 empty] | 6181:NSX[5].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV31_V,lo:=6182,hi:=6183); | [6 empty] | 6183:NSX[5].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].MIN_VoltageV3N_V,lo:=6184,hi:=6185); | [6 empty] | 6185:NSX[5].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].PowerFactorL1,lo:=6186,hi:=6187); | [6 empty] | 6187:NSX[5].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].PowerFactorL2,lo:=6188,hi:=6189); | [6 empty] | 6189:NSX[5].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].PowerFactorL3,lo:=6190,hi:=6191); | [6 empty] | 6191:NSX[5].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].PowerFactorTotal,lo:=6192,hi:=6193); | [6 empty] | 6193:NSX[5].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_D,lo:=6194,hi:=6195); | [6 empty] | 6195:NSX[5].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_D_SCADA,lo:=6196,hi:=6197); | [6 empty] | 6197:NSX[5].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_D_TEMP,lo:=6198,hi:=6199); | [6 empty] | 6199:NSX[5].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_M,lo:=6200,hi:=6201); | [6 empty] | 6201:NSX[5].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_M_SCADA,lo:=6202,hi:=6203); | [6 empty] | 6203:NSX[5].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_M_TEMP,lo:=6204,hi:=6205); | [6 empty] | 6205:NSX[5].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_T,lo:=6206,hi:=6207); | [6 empty] | 6207:NSX[5].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_T_SCADA,lo:=6208,hi:=6209); | [6 empty] | 6209:NSX[5].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].RazEner_T_TEMP,lo:=6210,hi:=6211); | [6 empty] | 6211:NSX[5].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactiveEnergy_kVArh,lo:=6212,hi:=6213); | [6 empty] | 6213:NSX[5].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactiveNegativeEnergy_kVArh,lo:=6214,hi:=6215); | [6 empty] | 6215:NSX[5].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePositiveEnergy_kVArh,lo:=6216,hi:=6217); | [6 empty] | 6217:NSX[5].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerDemand_kVAr,lo:=6218,hi:=6219); | [6 empty] | 6219:NSX[5].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerL1_kVAr,lo:=6220,hi:=6221); | [6 empty] | 6221:NSX[5].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerL2_kVAr,lo:=6222,hi:=6223); | [6 empty] | 6223:NSX[5].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerL3_kVAr,lo:=6224,hi:=6225); | [6 empty] | 6225:NSX[5].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerMaxDemand_kVAr,lo:=6226,hi:=6227); | [6 empty] | 6227:NSX[5].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].ReactivePowerTotal_kVAr,lo:=6228,hi:=6229); | [6 empty] | 6229:NSX[5].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDI1_P,lo:=6230,hi:=6231); | [6 empty] | 6231:NSX[5].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDI2_P,lo:=6232,hi:=6233); | [6 empty] | 6233:NSX[5].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDI3_P,lo:=6234,hi:=6235); | [6 empty] | 6235:NSX[5].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV12_P,lo:=6236,hi:=6237); | [6 empty] | 6237:NSX[5].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV1N_P,lo:=6238,hi:=6239); | [6 empty] | 6239:NSX[5].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV23_P,lo:=6240,hi:=6241); | [6 empty] | 6241:NSX[5].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV2N_P,lo:=6242,hi:=6243); | [6 empty] | 6243:NSX[5].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV31_P,lo:=6244,hi:=6245); | [6 empty] | 6245:NSX[5].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].THDV3N_P,lo:=6246,hi:=6247); | [6 empty] | 6247:NSX[5].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageAvgPhToN_V,lo:=6248,hi:=6249); | [6 empty] | 6249:NSX[5].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageAvgPhToPh_V,lo:=6250,hi:=6251); | [6 empty] | 6251:NSX[5].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV12_P,lo:=6252,hi:=6253); | [6 empty] | 6253:NSX[5].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV1N_P,lo:=6254,hi:=6255); | [6 empty] | 6255:NSX[5].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV23_P,lo:=6256,hi:=6257); | [6 empty] | 6257:NSX[5].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV2N_P,lo:=6258,hi:=6259); | [6 empty] | 6259:NSX[5].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV31_P,lo:=6260,hi:=6261); | [6 empty] | 6261:NSX[5].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageUnbV3N_P,lo:=6262,hi:=6263); | [6 empty] | 6263:NSX[5].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV12_V,lo:=6264,hi:=6265); | [6 empty] | 6265:NSX[5].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV1N_V,lo:=6266,hi:=6267); | [6 empty] | 6267:NSX[5].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV23_V,lo:=6268,hi:=6269); | [6 empty] | 6269:NSX[5].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV2N_V,lo:=6270,hi:=6271); | [6 empty] | 6271:NSX[5].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV31_V,lo:=6272,hi:=6273); | [6 empty] | 6273:NSX[5].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[5].VoltageV3N_V,lo:=6274,hi:=6275); | [6 empty] | 6275:NSX[5].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActiveEnergy_kWh,lo:=6276,hi:=6277); | [6 empty] | 6277:NSX[6].ActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActiveNegativeEnergy_kWh,lo:=6278,hi:=6279); | [6 empty] | 6279:NSX[6].ActiveNegativeEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePositiveEnergy_kWh,lo:=6280,hi:=6281); | [6 empty] | 6281:NSX[6].ActivePositiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerDemand_kW,lo:=6282,hi:=6283); | [6 empty] | 6283:NSX[6].ActivePowerDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerL1_kW,lo:=6284,hi:=6285); | [6 empty] | 6285:NSX[6].ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerL2_kW,lo:=6286,hi:=6287); | [6 empty] | 6287:NSX[6].ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerL3_kW,lo:=6288,hi:=6289); | [6 empty] | 6289:NSX[6].ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerMaxDemand_kW,lo:=6290,hi:=6291); | [6 empty] | 6291:NSX[6].ActivePowerMaxDemand_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ActivePowerTotal_kW,lo:=6292,hi:=6293); | [6 empty] | 6293:NSX[6].ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparentEnergy_kVAh,lo:=6294,hi:=6295); | [6 empty] | 6295:NSX[6].ApparentEnergy_kVAh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparentPowerDemand_kVA,lo:=6296,hi:=6297); | [6 empty] | 6297:NSX[6].ApparentPowerDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparentPowerMaxDemand_kVA,lo:=6298,hi:=6299); | [6 empty] | 6299:NSX[6].ApparentPowerMaxDemand_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparetnPowerL1_kVA,lo:=6300,hi:=6301); | [6 empty] | 6301:NSX[6].ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparetnPowerL2_kVA,lo:=6302,hi:=6303); | [6 empty] | 6303:NSX[6].ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparetnPowerL3_kVA,lo:=6304,hi:=6305); | [6 empty] | 6305:NSX[6].ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ApparetnPowerTotal_kVA,lo:=6306,hi:=6307); | [6 empty] | 6307:NSX[6].ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CosFL1,lo:=6308,hi:=6309); | [6 empty] | 6309:NSX[6].CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CosFL2,lo:=6310,hi:=6311); | [6 empty] | 6311:NSX[6].CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CosFL3,lo:=6312,hi:=6313); | [6 empty] | 6313:NSX[6].CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CosFTotal,lo:=6314,hi:=6315); | [6 empty] | 6315:NSX[6].CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CumulNegativeActiveEnergy_kWh,lo:=6316,hi:=6317); | [6 empty] | 6317:NSX[6].CumulNegativeActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CumulPositiveActiveEnergy_kWh,lo:=6318,hi:=6319); | [6 empty] | 6319:NSX[6].CumulPositiveActiveEnergy_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentAvgI1I2I3_A,lo:=6320,hi:=6321); | [6 empty] | 6321:NSX[6].CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandL1_A,lo:=6322,hi:=6323); | [6 empty] | 6323:NSX[6].CurrentDemandL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandL2_A,lo:=6324,hi:=6325); | [6 empty] | 6325:NSX[6].CurrentDemandL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandL3_A,lo:=6326,hi:=6327); | [6 empty] | 6327:NSX[6].CurrentDemandL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandMaxL1_A,lo:=6328,hi:=6329); | [6 empty] | 6329:NSX[6].CurrentDemandMaxL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandMaxL2_A,lo:=6330,hi:=6331); | [6 empty] | 6331:NSX[6].CurrentDemandMaxL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandMaxL3_A,lo:=6332,hi:=6333); | [6 empty] | 6333:NSX[6].CurrentDemandMaxL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandMaxN_A,lo:=6334,hi:=6335); | [6 empty] | 6335:NSX[6].CurrentDemandMaxN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentDemandN_A,lo:=6336,hi:=6337); | [6 empty] | 6337:NSX[6].CurrentDemandN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentL1_A,lo:=6338,hi:=6339); | [6 empty] | 6339:NSX[6].CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentL2_A,lo:=6340,hi:=6341); | [6 empty] | 6341:NSX[6].CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentL3_A,lo:=6342,hi:=6343); | [6 empty] | 6343:NSX[6].CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentN_A,lo:=6344,hi:=6345); | [6 empty] | 6345:NSX[6].CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentUnbI1_P,lo:=6346,hi:=6347); | [6 empty] | 6347:NSX[6].CurrentUnbI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentUnbI2_P,lo:=6348,hi:=6349); | [6 empty] | 6349:NSX[6].CurrentUnbI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentUnbI3_P,lo:=6350,hi:=6351); | [6 empty] | 6351:NSX[6].CurrentUnbI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].CurrentUnbN_P,lo:=6352,hi:=6353); | [6 empty] | 6353:NSX[6].CurrentUnbN_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].DelovnaEnergija_TEMP,lo:=6354,hi:=6355); | [6 empty] | 6355:NSX[6].DelovnaEnergija_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].DistortionPowerL1_kVAr,lo:=6356,hi:=6357); | [6 empty] | 6357:NSX[6].DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].DistortionPowerL2_kVAr,lo:=6358,hi:=6359); | [6 empty] | 6359:NSX[6].DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].DistortionPowerL3_kVAr,lo:=6360,hi:=6361); | [6 empty] | 6361:NSX[6].DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].DistortionPowerTotal_kVAr,lo:=6362,hi:=6363); | [6 empty] | 6363:NSX[6].DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].Frequency_Hz,lo:=6364,hi:=6365); | [6 empty] | 6365:NSX[6].Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].FunReactivePowerL1_kVAr,lo:=6366,hi:=6367); | [6 empty] | 6367:NSX[6].FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].FunReactivePowerL2_kVAr,lo:=6368,hi:=6369); | [6 empty] | 6369:NSX[6].FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].FunReactivePowerL3_kVAr,lo:=6370,hi:=6371); | [6 empty] | 6371:NSX[6].FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].FunReactivePowerTotal_kVAr,lo:=6372,hi:=6373); | [6 empty] | 6373:NSX[6].FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ActivePowerL1_kW,lo:=6374,hi:=6375); | [6 empty] | 6375:NSX[6].MAX_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ActivePowerL2_kW,lo:=6376,hi:=6377); | [6 empty] | 6377:NSX[6].MAX_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ActivePowerL3_kW,lo:=6378,hi:=6379); | [6 empty] | 6379:NSX[6].MAX_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ActivePowerTotal_kW,lo:=6380,hi:=6381); | [6 empty] | 6381:NSX[6].MAX_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL1_kVA,lo:=6382,hi:=6383); | [6 empty] | 6383:NSX[6].MAX_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL2_kVA,lo:=6384,hi:=6385); | [6 empty] | 6385:NSX[6].MAX_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL3_kVA,lo:=6386,hi:=6387); | [6 empty] | 6387:NSX[6].MAX_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ApparetnPowerTotal_kVA,lo:=6388,hi:=6389); | [6 empty] | 6389:NSX[6].MAX_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CosFL1,lo:=6390,hi:=6391); | [6 empty] | 6391:NSX[6].MAX_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CosFL2,lo:=6392,hi:=6393); | [6 empty] | 6393:NSX[6].MAX_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CosFL3,lo:=6394,hi:=6395); | [6 empty] | 6395:NSX[6].MAX_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CosFTotal,lo:=6396,hi:=6397); | [6 empty] | 6397:NSX[6].MAX_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentAvgI1I2I3_A,lo:=6398,hi:=6399); | [6 empty] | 6399:NSX[6].MAX_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentL1_A,lo:=6400,hi:=6401); | [6 empty] | 6401:NSX[6].MAX_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentL2_A,lo:=6402,hi:=6403); | [6 empty] | 6403:NSX[6].MAX_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentL3_A,lo:=6404,hi:=6405); | [6 empty] | 6405:NSX[6].MAX_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentMaxL1L2L3N_A,lo:=6406,hi:=6407); | [6 empty] | 6407:NSX[6].MAX_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_CurrentN_A,lo:=6408,hi:=6409); | [6 empty] | 6409:NSX[6].MAX_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_DistortionPowerL1_kVAr,lo:=6410,hi:=6411); | [6 empty] | 6411:NSX[6].MAX_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_DistortionPowerL2_kVAr,lo:=6412,hi:=6413); | [6 empty] | 6413:NSX[6].MAX_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_DistortionPowerL3_kVAr,lo:=6414,hi:=6415); | [6 empty] | 6415:NSX[6].MAX_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_DistortionPowerTotal_kVAr,lo:=6416,hi:=6417); | [6 empty] | 6417:NSX[6].MAX_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_Frequency_Hz,lo:=6418,hi:=6419); | [6 empty] | 6419:NSX[6].MAX_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL1_kVAr,lo:=6420,hi:=6421); | [6 empty] | 6421:NSX[6].MAX_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL2_kVAr,lo:=6422,hi:=6423); | [6 empty] | 6423:NSX[6].MAX_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL3_kVAr,lo:=6424,hi:=6425); | [6 empty] | 6425:NSX[6].MAX_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_FunReactivePowerTotal_kVAr,lo:=6426,hi:=6427); | [6 empty] | 6427:NSX[6].MAX_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_PowerFactorL1,lo:=6428,hi:=6429); | [6 empty] | 6429:NSX[6].MAX_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_PowerFactorL2,lo:=6430,hi:=6431); | [6 empty] | 6431:NSX[6].MAX_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_PowerFactorL3,lo:=6432,hi:=6433); | [6 empty] | 6433:NSX[6].MAX_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_PowerFactorTotal,lo:=6434,hi:=6435); | [6 empty] | 6435:NSX[6].MAX_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ReactivePowerL1_kVAr,lo:=6436,hi:=6437); | [6 empty] | 6437:NSX[6].MAX_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ReactivePowerL2_kVAr,lo:=6438,hi:=6439); | [6 empty] | 6439:NSX[6].MAX_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ReactivePowerL3_kVAr,lo:=6440,hi:=6441); | [6 empty] | 6441:NSX[6].MAX_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_ReactivePowerTotal_kVAr,lo:=6442,hi:=6443); | [6 empty] | 6443:NSX[6].MAX_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDI1_P,lo:=6444,hi:=6445); | [6 empty] | 6445:NSX[6].MAX_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDI2_P,lo:=6446,hi:=6447); | [6 empty] | 6447:NSX[6].MAX_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDI3_P,lo:=6448,hi:=6449); | [6 empty] | 6449:NSX[6].MAX_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV12_P,lo:=6450,hi:=6451); | [6 empty] | 6451:NSX[6].MAX_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV1N_P,lo:=6452,hi:=6453); | [6 empty] | 6453:NSX[6].MAX_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV23_P,lo:=6454,hi:=6455); | [6 empty] | 6455:NSX[6].MAX_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV2N_P,lo:=6456,hi:=6457); | [6 empty] | 6457:NSX[6].MAX_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV31_P,lo:=6458,hi:=6459); | [6 empty] | 6459:NSX[6].MAX_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_THDV3N_P,lo:=6460,hi:=6461); | [6 empty] | 6461:NSX[6].MAX_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageAvgPhToN_V,lo:=6462,hi:=6463); | [6 empty] | 6463:NSX[6].MAX_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageAvgPhToPh_V,lo:=6464,hi:=6465); | [6 empty] | 6465:NSX[6].MAX_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV12_P,lo:=6466,hi:=6467); | [6 empty] | 6467:NSX[6].MAX_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV1N_P,lo:=6468,hi:=6469); | [6 empty] | 6469:NSX[6].MAX_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV23_P,lo:=6470,hi:=6471); | [6 empty] | 6471:NSX[6].MAX_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV2N_P,lo:=6472,hi:=6473); | [6 empty] | 6473:NSX[6].MAX_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV31_P,lo:=6474,hi:=6475); | [6 empty] | 6475:NSX[6].MAX_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageUnbV3N_P,lo:=6476,hi:=6477); | [6 empty] | 6477:NSX[6].MAX_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV12_V,lo:=6478,hi:=6479); | [6 empty] | 6479:NSX[6].MAX_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV1N_V,lo:=6480,hi:=6481); | [6 empty] | 6481:NSX[6].MAX_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV23_V,lo:=6482,hi:=6483); | [6 empty] | 6483:NSX[6].MAX_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV2N_V,lo:=6484,hi:=6485); | [6 empty] | 6485:NSX[6].MAX_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV31_V,lo:=6486,hi:=6487); | [6 empty] | 6487:NSX[6].MAX_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MAX_VoltageV3N_V,lo:=6488,hi:=6489); | [6 empty] | 6489:NSX[6].MAX_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ActivePowerL1_kW,lo:=6490,hi:=6491); | [6 empty] | 6491:NSX[6].MIN_ActivePowerL1_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ActivePowerL2_kW,lo:=6492,hi:=6493); | [6 empty] | 6493:NSX[6].MIN_ActivePowerL2_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ActivePowerL3_kW,lo:=6494,hi:=6495); | [6 empty] | 6495:NSX[6].MIN_ActivePowerL3_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ActivePowerTotal_kW,lo:=6496,hi:=6497); | [6 empty] | 6497:NSX[6].MIN_ActivePowerTotal_kW:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL1_kVA,lo:=6498,hi:=6499); | [6 empty] | 6499:NSX[6].MIN_ApparetnPowerL1_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL2_kVA,lo:=6500,hi:=6501); | [6 empty] | 6501:NSX[6].MIN_ApparetnPowerL2_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL3_kVA,lo:=6502,hi:=6503); | [6 empty] | 6503:NSX[6].MIN_ApparetnPowerL3_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ApparetnPowerTotal_kVA,lo:=6504,hi:=6505); | [6 empty] | 6505:NSX[6].MIN_ApparetnPowerTotal_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CosFL1,lo:=6506,hi:=6507); | [6 empty] | 6507:NSX[6].MIN_CosFL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CosFL2,lo:=6508,hi:=6509); | [6 empty] | 6509:NSX[6].MIN_CosFL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CosFL3,lo:=6510,hi:=6511); | [6 empty] | 6511:NSX[6].MIN_CosFL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CosFTotal,lo:=6512,hi:=6513); | [6 empty] | 6513:NSX[6].MIN_CosFTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentAvgI1I2I3_A,lo:=6514,hi:=6515); | [6 empty] | 6515:NSX[6].MIN_CurrentAvgI1I2I3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentL1_A,lo:=6516,hi:=6517); | [6 empty] | 6517:NSX[6].MIN_CurrentL1_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentL2_A,lo:=6518,hi:=6519); | [6 empty] | 6519:NSX[6].MIN_CurrentL2_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentL3_A,lo:=6520,hi:=6521); | [6 empty] | 6521:NSX[6].MIN_CurrentL3_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentMaxL1L2L3N_A,lo:=6522,hi:=6523); | [6 empty] | 6523:NSX[6].MIN_CurrentMaxL1L2L3N_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_CurrentN_A,lo:=6524,hi:=6525); | [6 empty] | 6525:NSX[6].MIN_CurrentN_A:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_DistortionPowerL1_kVAr,lo:=6526,hi:=6527); | [6 empty] | 6527:NSX[6].MIN_DistortionPowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_DistortionPowerL2_kVAr,lo:=6528,hi:=6529); | [6 empty] | 6529:NSX[6].MIN_DistortionPowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_DistortionPowerL3_kVAr,lo:=6530,hi:=6531); | [6 empty] | 6531:NSX[6].MIN_DistortionPowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_DistortionPowerTotal_kVAr,lo:=6532,hi:=6533); | [6 empty] | 6533:NSX[6].MIN_DistortionPowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_Frequency_Hz,lo:=6534,hi:=6535); | [6 empty] | 6535:NSX[6].MIN_Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL1_kVAr,lo:=6536,hi:=6537); | [6 empty] | 6537:NSX[6].MIN_FunReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL2_kVAr,lo:=6538,hi:=6539); | [6 empty] | 6539:NSX[6].MIN_FunReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL3_kVAr,lo:=6540,hi:=6541); | [6 empty] | 6541:NSX[6].MIN_FunReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_FunReactivePowerTotal_kVAr,lo:=6542,hi:=6543); | [6 empty] | 6543:NSX[6].MIN_FunReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_PowerFactorL1,lo:=6544,hi:=6545); | [6 empty] | 6545:NSX[6].MIN_PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_PowerFactorL2,lo:=6546,hi:=6547); | [6 empty] | 6547:NSX[6].MIN_PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_PowerFactorL3,lo:=6548,hi:=6549); | [6 empty] | 6549:NSX[6].MIN_PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_PowerFactorTotal,lo:=6550,hi:=6551); | [6 empty] | 6551:NSX[6].MIN_PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ReactivePowerL1_kVAr,lo:=6552,hi:=6553); | [6 empty] | 6553:NSX[6].MIN_ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ReactivePowerL2_kVAr,lo:=6554,hi:=6555); | [6 empty] | 6555:NSX[6].MIN_ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ReactivePowerL3_kVAr,lo:=6556,hi:=6557); | [6 empty] | 6557:NSX[6].MIN_ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_ReactivePowerTotal_kVAr,lo:=6558,hi:=6559); | [6 empty] | 6559:NSX[6].MIN_ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDI1_P,lo:=6560,hi:=6561); | [6 empty] | 6561:NSX[6].MIN_THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDI2_P,lo:=6562,hi:=6563); | [6 empty] | 6563:NSX[6].MIN_THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDI3_P,lo:=6564,hi:=6565); | [6 empty] | 6565:NSX[6].MIN_THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV12_P,lo:=6566,hi:=6567); | [6 empty] | 6567:NSX[6].MIN_THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV1N_P,lo:=6568,hi:=6569); | [6 empty] | 6569:NSX[6].MIN_THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV23_P,lo:=6570,hi:=6571); | [6 empty] | 6571:NSX[6].MIN_THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV2N_P,lo:=6572,hi:=6573); | [6 empty] | 6573:NSX[6].MIN_THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV31_P,lo:=6574,hi:=6575); | [6 empty] | 6575:NSX[6].MIN_THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_THDV3N_P,lo:=6576,hi:=6577); | [6 empty] | 6577:NSX[6].MIN_THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageAvgPhToN_V,lo:=6578,hi:=6579); | [6 empty] | 6579:NSX[6].MIN_VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageAvgPhToPh_V,lo:=6580,hi:=6581); | [6 empty] | 6581:NSX[6].MIN_VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV12_P,lo:=6582,hi:=6583); | [6 empty] | 6583:NSX[6].MIN_VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV1N_P,lo:=6584,hi:=6585); | [6 empty] | 6585:NSX[6].MIN_VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV23_P,lo:=6586,hi:=6587); | [6 empty] | 6587:NSX[6].MIN_VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV2N_P,lo:=6588,hi:=6589); | [6 empty] | 6589:NSX[6].MIN_VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV31_P,lo:=6590,hi:=6591); | [6 empty] | 6591:NSX[6].MIN_VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageUnbV3N_P,lo:=6592,hi:=6593); | [6 empty] | 6593:NSX[6].MIN_VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV12_V,lo:=6594,hi:=6595); | [6 empty] | 6595:NSX[6].MIN_VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV1N_V,lo:=6596,hi:=6597); | [6 empty] | 6597:NSX[6].MIN_VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV23_V,lo:=6598,hi:=6599); | [6 empty] | 6599:NSX[6].MIN_VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV2N_V,lo:=6600,hi:=6601); | [6 empty] | 6601:NSX[6].MIN_VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV31_V,lo:=6602,hi:=6603); | [6 empty] | 6603:NSX[6].MIN_VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].MIN_VoltageV3N_V,lo:=6604,hi:=6605); | [6 empty] | 6605:NSX[6].MIN_VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].PowerFactorL1,lo:=6606,hi:=6607); | [6 empty] | 6607:NSX[6].PowerFactorL1:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].PowerFactorL2,lo:=6608,hi:=6609); | [6 empty] | 6609:NSX[6].PowerFactorL2:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].PowerFactorL3,lo:=6610,hi:=6611); | [6 empty] | 6611:NSX[6].PowerFactorL3:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].PowerFactorTotal,lo:=6612,hi:=6613); | [6 empty] | 6613:NSX[6].PowerFactorTotal:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_D,lo:=6614,hi:=6615); | [6 empty] | 6615:NSX[6].RazEner_D:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_D_SCADA,lo:=6616,hi:=6617); | [6 empty] | 6617:NSX[6].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_D_TEMP,lo:=6618,hi:=6619); | [6 empty] | 6619:NSX[6].RazEner_D_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_M,lo:=6620,hi:=6621); | [6 empty] | 6621:NSX[6].RazEner_M:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_M_SCADA,lo:=6622,hi:=6623); | [6 empty] | 6623:NSX[6].RazEner_M_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_M_TEMP,lo:=6624,hi:=6625); | [6 empty] | 6625:NSX[6].RazEner_M_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_T,lo:=6626,hi:=6627); | [6 empty] | 6627:NSX[6].RazEner_T:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_T_SCADA,lo:=6628,hi:=6629); | [6 empty] | 6629:NSX[6].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].RazEner_T_TEMP,lo:=6630,hi:=6631); | [6 empty] | 6631:NSX[6].RazEner_T_TEMP:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactiveEnergy_kVArh,lo:=6632,hi:=6633); | [6 empty] | 6633:NSX[6].ReactiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactiveNegativeEnergy_kVArh,lo:=6634,hi:=6635); | [6 empty] | 6635:NSX[6].ReactiveNegativeEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePositiveEnergy_kVArh,lo:=6636,hi:=6637); | [6 empty] | 6637:NSX[6].ReactivePositiveEnergy_kVArh:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerDemand_kVAr,lo:=6638,hi:=6639); | [6 empty] | 6639:NSX[6].ReactivePowerDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerL1_kVAr,lo:=6640,hi:=6641); | [6 empty] | 6641:NSX[6].ReactivePowerL1_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerL2_kVAr,lo:=6642,hi:=6643); | [6 empty] | 6643:NSX[6].ReactivePowerL2_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerL3_kVAr,lo:=6644,hi:=6645); | [6 empty] | 6645:NSX[6].ReactivePowerL3_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerMaxDemand_kVAr,lo:=6646,hi:=6647); | [6 empty] | 6647:NSX[6].ReactivePowerMaxDemand_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].ReactivePowerTotal_kVAr,lo:=6648,hi:=6649); | [6 empty] | 6649:NSX[6].ReactivePowerTotal_kVAr:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDI1_P,lo:=6650,hi:=6651); | [6 empty] | 6651:NSX[6].THDI1_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDI2_P,lo:=6652,hi:=6653); | [6 empty] | 6653:NSX[6].THDI2_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDI3_P,lo:=6654,hi:=6655); | [6 empty] | 6655:NSX[6].THDI3_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV12_P,lo:=6656,hi:=6657); | [6 empty] | 6657:NSX[6].THDV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV1N_P,lo:=6658,hi:=6659); | [6 empty] | 6659:NSX[6].THDV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV23_P,lo:=6660,hi:=6661); | [6 empty] | 6661:NSX[6].THDV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV2N_P,lo:=6662,hi:=6663); | [6 empty] | 6663:NSX[6].THDV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV31_P,lo:=6664,hi:=6665); | [6 empty] | 6665:NSX[6].THDV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].THDV3N_P,lo:=6666,hi:=6667); | [6 empty] | 6667:NSX[6].THDV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageAvgPhToN_V,lo:=6668,hi:=6669); | [6 empty] | 6669:NSX[6].VoltageAvgPhToN_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageAvgPhToPh_V,lo:=6670,hi:=6671); | [6 empty] | 6671:NSX[6].VoltageAvgPhToPh_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV12_P,lo:=6672,hi:=6673); | [6 empty] | 6673:NSX[6].VoltageUnbV12_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV1N_P,lo:=6674,hi:=6675); | [6 empty] | 6675:NSX[6].VoltageUnbV1N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV23_P,lo:=6676,hi:=6677); | [6 empty] | 6677:NSX[6].VoltageUnbV23_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV2N_P,lo:=6678,hi:=6679); | [6 empty] | 6679:NSX[6].VoltageUnbV2N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV31_P,lo:=6680,hi:=6681); | [6 empty] | 6681:NSX[6].VoltageUnbV31_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageUnbV3N_P,lo:=6682,hi:=6683); | [6 empty] | 6683:NSX[6].VoltageUnbV3N_P:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV12_V,lo:=6684,hi:=6685); | [6 empty] | 6685:NSX[6].VoltageV12_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV1N_V,lo:=6686,hi:=6687); | [6 empty] | 6687:NSX[6].VoltageV1N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV23_V,lo:=6688,hi:=6689); | [6 empty] | 6689:NSX[6].VoltageV23_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV2N_V,lo:=6690,hi:=6691); | [6 empty] | 6691:NSX[6].VoltageV2N_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV31_V,lo:=6692,hi:=6693); | [6 empty] | 6693:NSX[6].VoltageV31_V:=Real_0;
|  |  |  | Read_Real(rVar:=NSX[6].VoltageV3N_V,lo:=6694,hi:=6695); | [6 empty] | 6695:NSX[6].VoltageV3N_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[10],lo:=6696,hi:=6697); | [6 empty] | 6697:PMM.VirA.Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[11],lo:=6698,hi:=6699); | [6 empty] | 6699:PMM.VirA.Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[12],lo:=6700,hi:=6701); | [6 empty] | 6701:PMM.VirA.Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[13],lo:=6702,hi:=6703); | [6 empty] | 6703:PMM.VirA.Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[14],lo:=6704,hi:=6705); | [6 empty] | 6705:PMM.VirA.Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[15],lo:=6706,hi:=6707); | [6 empty] | 6707:PMM.VirA.Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[16],lo:=6708,hi:=6709); | [6 empty] | 6709:PMM.VirA.Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[17],lo:=6710,hi:=6711); | [6 empty] | 6711:PMM.VirA.Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[18],lo:=6712,hi:=6713); | [6 empty] | 6713:PMM.VirA.Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[19],lo:=6714,hi:=6715); | [6 empty] | 6715:PMM.VirA.Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[1],lo:=6716,hi:=6717); | [6 empty] | 6717:PMM.VirA.Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[20],lo:=6718,hi:=6719); | [6 empty] | 6719:PMM.VirA.Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[21],lo:=6720,hi:=6721); | [6 empty] | 6721:PMM.VirA.Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[22],lo:=6722,hi:=6723); | [6 empty] | 6723:PMM.VirA.Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[23],lo:=6724,hi:=6725); | [6 empty] | 6725:PMM.VirA.Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[24],lo:=6726,hi:=6727); | [6 empty] | 6727:PMM.VirA.Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[25],lo:=6728,hi:=6729); | [6 empty] | 6729:PMM.VirA.Current[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[26],lo:=6730,hi:=6731); | [6 empty] | 6731:PMM.VirA.Current[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[27],lo:=6732,hi:=6733); | [6 empty] | 6733:PMM.VirA.Current[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[28],lo:=6734,hi:=6735); | [6 empty] | 6735:PMM.VirA.Current[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[29],lo:=6736,hi:=6737); | [6 empty] | 6737:PMM.VirA.Current[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[2],lo:=6738,hi:=6739); | [6 empty] | 6739:PMM.VirA.Current[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[30],lo:=6740,hi:=6741); | [6 empty] | 6741:PMM.VirA.Current[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[31],lo:=6742,hi:=6743); | [6 empty] | 6743:PMM.VirA.Current[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[32],lo:=6744,hi:=6745); | [6 empty] | 6745:PMM.VirA.Current[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[33],lo:=6746,hi:=6747); | [6 empty] | 6747:PMM.VirA.Current[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[34],lo:=6748,hi:=6749); | [6 empty] | 6749:PMM.VirA.Current[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[35],lo:=6750,hi:=6751); | [6 empty] | 6751:PMM.VirA.Current[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[36],lo:=6752,hi:=6753); | [6 empty] | 6753:PMM.VirA.Current[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[37],lo:=6754,hi:=6755); | [6 empty] | 6755:PMM.VirA.Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[38],lo:=6756,hi:=6757); | [6 empty] | 6757:PMM.VirA.Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[39],lo:=6758,hi:=6759); | [6 empty] | 6759:PMM.VirA.Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[3],lo:=6760,hi:=6761); | [6 empty] | 6761:PMM.VirA.Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[40],lo:=6762,hi:=6763); | [6 empty] | 6763:PMM.VirA.Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[41],lo:=6764,hi:=6765); | [6 empty] | 6765:PMM.VirA.Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[42],lo:=6766,hi:=6767); | [6 empty] | 6767:PMM.VirA.Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[43],lo:=6768,hi:=6769); | [6 empty] | 6769:PMM.VirA.Current[43]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[44],lo:=6770,hi:=6771); | [6 empty] | 6771:PMM.VirA.Current[44]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[4],lo:=6772,hi:=6773); | [6 empty] | 6773:PMM.VirA.Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[5],lo:=6774,hi:=6775); | [6 empty] | 6775:PMM.VirA.Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[6],lo:=6776,hi:=6777); | [6 empty] | 6777:PMM.VirA.Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[7],lo:=6778,hi:=6779); | [6 empty] | 6779:PMM.VirA.Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[8],lo:=6780,hi:=6781); | [6 empty] | 6781:PMM.VirA.Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA.Current[9],lo:=6782,hi:=6783); | [6 empty] | 6783:PMM.VirA.Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_fsys,lo:=6784,hi:=6785); | [6 empty] | 6785:PMM.VirA_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_Isys,lo:=6786,hi:=6787); | [6 empty] | 6787:PMM.VirA_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_PFsys,lo:=6788,hi:=6789); | [6 empty] | 6789:PMM.VirA_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_Psys,lo:=6790,hi:=6791); | [6 empty] | 6791:PMM.VirA_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_Qsys,lo:=6792,hi:=6793); | [6 empty] | 6793:PMM.VirA_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_Ssys,lo:=6794,hi:=6795); | [6 empty] | 6795:PMM.VirA_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirA_Usys,lo:=6796,hi:=6797); | [6 empty] | 6797:PMM.VirA_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAActiveEnergyConsumed_kWh,lo:=6798,hi:=6799); | [6 empty] | 6799:PMM.VirAActiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAActivePowerPhaseA_kW,lo:=6800,hi:=6801); | [6 empty] | 6801:PMM.VirAActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAActivePowerPhaseB_kW,lo:=6802,hi:=6803); | [6 empty] | 6803:PMM.VirAActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAActivePowerPhaseC_kW,lo:=6804,hi:=6805); | [6 empty] | 6805:PMM.VirAActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAAparentPowerPhaseA,lo:=6806,hi:=6807); | [6 empty] | 6807:PMM.VirAAparentPowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAAparentPowerPhaseB,lo:=6808,hi:=6809); | [6 empty] | 6809:PMM.VirAAparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAAparentPowerPhaseC,lo:=6810,hi:=6811); | [6 empty] | 6811:PMM.VirAAparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirACurrentInPhaseA_A,lo:=6812,hi:=6813); | [6 empty] | 6813:PMM.VirACurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirACurrentInPhaseB_A,lo:=6814,hi:=6815); | [6 empty] | 6815:PMM.VirACurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirACurrentInPhaseC_A,lo:=6816,hi:=6817); | [6 empty] | 6817:PMM.VirACurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAReactiveEnergyConsumed_kVARh,lo:=6818,hi:=6819); | [6 empty] | 6819:PMM.VirAReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAReactivePowerPhaseA,lo:=6820,hi:=6821); | [6 empty] | 6821:PMM.VirAReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAReactivePowerPhaseB,lo:=6822,hi:=6823); | [6 empty] | 6823:PMM.VirAReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAReactivePowerPhaseC,lo:=6824,hi:=6825); | [6 empty] | 6825:PMM.VirAReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseAB_V,lo:=6826,hi:=6827); | [6 empty] | 6827:PMM.VirAVoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseAN_V,lo:=6828,hi:=6829); | [6 empty] | 6829:PMM.VirAVoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseBC_V,lo:=6830,hi:=6831); | [6 empty] | 6831:PMM.VirAVoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseBN_V,lo:=6832,hi:=6833); | [6 empty] | 6833:PMM.VirAVoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseCA_V,lo:=6834,hi:=6835); | [6 empty] | 6835:PMM.VirAVoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseCN_V,lo:=6836,hi:=6837); | [6 empty] | 6837:PMM.VirAVoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[10],lo:=6838,hi:=6839); | [6 empty] | 6839:PMM.VirB.Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[11],lo:=6840,hi:=6841); | [6 empty] | 6841:PMM.VirB.Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[12],lo:=6842,hi:=6843); | [6 empty] | 6843:PMM.VirB.Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[13],lo:=6844,hi:=6845); | [6 empty] | 6845:PMM.VirB.Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[14],lo:=6846,hi:=6847); | [6 empty] | 6847:PMM.VirB.Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[15],lo:=6848,hi:=6849); | [6 empty] | 6849:PMM.VirB.Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[16],lo:=6850,hi:=6851); | [6 empty] | 6851:PMM.VirB.Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[17],lo:=6852,hi:=6853); | [6 empty] | 6853:PMM.VirB.Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[18],lo:=6854,hi:=6855); | [6 empty] | 6855:PMM.VirB.Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[19],lo:=6856,hi:=6857); | [6 empty] | 6857:PMM.VirB.Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[1],lo:=6858,hi:=6859); | [6 empty] | 6859:PMM.VirB.Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[20],lo:=6860,hi:=6861); | [6 empty] | 6861:PMM.VirB.Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[21],lo:=6862,hi:=6863); | [6 empty] | 6863:PMM.VirB.Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[22],lo:=6864,hi:=6865); | [6 empty] | 6865:PMM.VirB.Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[23],lo:=6866,hi:=6867); | [6 empty] | 6867:PMM.VirB.Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[24],lo:=6868,hi:=6869); | [6 empty] | 6869:PMM.VirB.Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[25],lo:=6870,hi:=6871); | [6 empty] | 6871:PMM.VirB.Current[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[26],lo:=6872,hi:=6873); | [6 empty] | 6873:PMM.VirB.Current[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[27],lo:=6874,hi:=6875); | [6 empty] | 6875:PMM.VirB.Current[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[28],lo:=6876,hi:=6877); | [6 empty] | 6877:PMM.VirB.Current[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[29],lo:=6878,hi:=6879); | [6 empty] | 6879:PMM.VirB.Current[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[2],lo:=6880,hi:=6881); | [6 empty] | 6881:PMM.VirB.Current[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[30],lo:=6882,hi:=6883); | [6 empty] | 6883:PMM.VirB.Current[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[31],lo:=6884,hi:=6885); | [6 empty] | 6885:PMM.VirB.Current[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[32],lo:=6886,hi:=6887); | [6 empty] | 6887:PMM.VirB.Current[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[33],lo:=6888,hi:=6889); | [6 empty] | 6889:PMM.VirB.Current[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[34],lo:=6890,hi:=6891); | [6 empty] | 6891:PMM.VirB.Current[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[35],lo:=6892,hi:=6893); | [6 empty] | 6893:PMM.VirB.Current[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[36],lo:=6894,hi:=6895); | [6 empty] | 6895:PMM.VirB.Current[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[37],lo:=6896,hi:=6897); | [6 empty] | 6897:PMM.VirB.Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[38],lo:=6898,hi:=6899); | [6 empty] | 6899:PMM.VirB.Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[39],lo:=6900,hi:=6901); | [6 empty] | 6901:PMM.VirB.Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[3],lo:=6902,hi:=6903); | [6 empty] | 6903:PMM.VirB.Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[40],lo:=6904,hi:=6905); | [6 empty] | 6905:PMM.VirB.Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[41],lo:=6906,hi:=6907); | [6 empty] | 6907:PMM.VirB.Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[42],lo:=6908,hi:=6909); | [6 empty] | 6909:PMM.VirB.Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[43],lo:=6910,hi:=6911); | [6 empty] | 6911:PMM.VirB.Current[43]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[44],lo:=6912,hi:=6913); | [6 empty] | 6913:PMM.VirB.Current[44]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[4],lo:=6914,hi:=6915); | [6 empty] | 6915:PMM.VirB.Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[5],lo:=6916,hi:=6917); | [6 empty] | 6917:PMM.VirB.Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[6],lo:=6918,hi:=6919); | [6 empty] | 6919:PMM.VirB.Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[7],lo:=6920,hi:=6921); | [6 empty] | 6921:PMM.VirB.Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[8],lo:=6922,hi:=6923); | [6 empty] | 6923:PMM.VirB.Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB.Current[9],lo:=6924,hi:=6925); | [6 empty] | 6925:PMM.VirB.Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_fsys,lo:=6926,hi:=6927); | [6 empty] | 6927:PMM.VirB_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_Isys,lo:=6928,hi:=6929); | [6 empty] | 6929:PMM.VirB_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_PFsys,lo:=6930,hi:=6931); | [6 empty] | 6931:PMM.VirB_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_Psys,lo:=6932,hi:=6933); | [6 empty] | 6933:PMM.VirB_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_Qsys,lo:=6934,hi:=6935); | [6 empty] | 6935:PMM.VirB_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_Ssys,lo:=6936,hi:=6937); | [6 empty] | 6937:PMM.VirB_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirB_Usys,lo:=6938,hi:=6939); | [6 empty] | 6939:PMM.VirB_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=6940,hi:=6941); | [6 empty] | 6941:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=6942,hi:=6943); | [6 empty] | 6943:PMM.VirBActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=6944,hi:=6945); | [6 empty] | 6945:PMM.VirBActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=6946,hi:=6947); | [6 empty] | 6947:PMM.VirBActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=6948,hi:=6949); | [6 empty] | 6949:PMM.VirBAparentPowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=6950,hi:=6951); | [6 empty] | 6951:PMM.VirBAparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=6952,hi:=6953); | [6 empty] | 6953:PMM.VirBAparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=6954,hi:=6955); | [6 empty] | 6955:PMM.VirBCurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=6956,hi:=6957); | [6 empty] | 6957:PMM.VirBCurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=6958,hi:=6959); | [6 empty] | 6959:PMM.VirBCurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kVARh,lo:=6960,hi:=6961); | [6 empty] | 6961:PMM.VirBReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=6962,hi:=6963); | [6 empty] | 6963:PMM.VirBReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=6964,hi:=6965); | [6 empty] | 6965:PMM.VirBReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=6966,hi:=6967); | [6 empty] | 6967:PMM.VirBReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=6968,hi:=6969); | [6 empty] | 6969:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=6970,hi:=6971); | [6 empty] | 6971:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=6972,hi:=6973); | [6 empty] | 6973:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=6974,hi:=6975); | [6 empty] | 6975:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=6976,hi:=6977); | [6 empty] | 6977:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=6978,hi:=6979); | [6 empty] | 6979:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[1]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[2]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[3]:=Circ_Vpis_Mesecna_energija_scada2;
mind_bool[4]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[5]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[6]:=ComError;
mind_bool[7]:=ComSCADA;
mind_bool[8]:=ComSCADA1;
mind_bool[9]:=ComSCADA2;
mind_bool[10]:=ComSCADA3;
mind_bool[11]:=DI2_I10_Rezerva3;
mind_bool[12]:=DI2_I11_Rezerva4;
mind_bool[13]:=DI2_I12_Rezerva5;
mind_bool[14]:=DI2_I13_Rezerva6;
mind_bool[15]:=DI2_I8_Rezerva1;
mind_bool[16]:=DI2_I9_Rezerva2;
mind_bool[17]:=DI_SB_IROGSM21_Q0_Izkljucen;
mind_bool[18]:=DI_SB_IROGSM21_Q0_Vkljucen;
mind_bool[19]:=DI_SB_IROGSM21_Q11_Izkljucen;
mind_bool[20]:=DI_SB_IROGSM21_Q11_Vkljucen;
mind_bool[21]:=DI_SB_IROGSM21_Q12_Izkljucen;
mind_bool[22]:=DI_SB_IROGSM21_Q12_Vkljucen;
mind_bool[23]:=DI_SB_IROGSM21_Q13_Izpad;
mind_bool[24]:=DI_SB_IROGSM21_Q13_Vkljucen;
mind_bool[25]:=DI_SB_IROGSM21_Q14_Izpad;
mind_bool[26]:=DI_SB_IROGSM21_Q14_Vkljucen;
mind_bool[27]:=DI_SB_IROGSM21_Q15_Izpad;
mind_bool[28]:=DI_SB_IROGSM21_Q15_Vkljucen;
mind_bool[29]:=DI_SB_IROGSM21_SkupnaNapaka;
mind_bool[30]:=DI_SB_IROGSM22_Q0_Izkljucen;
mind_bool[31]:=DI_SB_IROGSM22_Q0_Vkljucen;
mind_bool[32]:=DI_SB_IROGSM22_Q11_Izkljucen;
mind_bool[33]:=DI_SB_IROGSM22_Q11_Vkljucen;
mind_bool[34]:=DI_SB_IROGSM22_Q12_Izkljucen;
mind_bool[35]:=DI_SB_IROGSM22_Q12_Vkljucen;
mind_bool[36]:=DI_SB_IROGSM22_Q13_Izpad;
mind_bool[37]:=DI_SB_IROGSM22_Q13_Vkljucen;
mind_bool[38]:=DI_SB_IROGSM22_Q14_Izpad;
mind_bool[39]:=DI_SB_IROGSM22_Q14_Vkljucen;
mind_bool[40]:=DI_SB_IROGSM22_Q15_Izpad;
mind_bool[41]:=DI_SB_IROGSM22_Q15_Vkljucen;
mind_bool[42]:=DI_SB_IROGSM22_SkupnaNapaka;
mind_bool[43]:=DI_SBi_RAZS_AA_Izolacija_NOT_OK;
mind_bool[44]:=DI_SBi_RAZS_AB_Izolacija_NOT_OK;
mind_bool[45]:=ErrComNSX[1];
mind_bool[46]:=ErrComNSX[2];
mind_bool[47]:=ErrComNSX[3];
mind_bool[48]:=ErrComNSX[4];
mind_bool[49]:=ErrComNSX[5];
mind_bool[50]:=ErrComNSX[6];
mind_bool[51]:=ErrComPMM[1];
mind_bool[52]:=ErrComPort2;
mind_bool[53]:=ErrorComPMM[1].Error;
mind_bool[54]:=napaka_kom_panel;
mind_bool[55]:=napaka_kom_scada;
mind_bool[56]:=napaka_kom_scada2;
mind_bool[57]:=NapakaSenzorSkupno;
mind_bool[58]:=NapakaSenzorVlagaHIA1;
mind_bool[59]:=NapakaSenzorVlagaHIA2;
mind_bool[60]:=NapakaSenzorVlagaHIA3;
mind_bool[61]:=NapakaSenzorVlagaHIA4;
mind_bool[62]:=NapakaSenzorVlagaHIA5;
mind_bool[63]:=NapakaSenzorVlagaHIA6;
mind_bool[64]:=NapakaSenzorVlagaHIA7;
mind_bool[65]:=NapakaSenzorVlagaHIA8;
mind_bool[66]:=NapakaTSTempTIA1;
mind_bool[67]:=NapakaTSTempTIA2;
mind_bool[68]:=NapakaTSTempTIA3;
mind_bool[69]:=NapakaTSTempTIA4;
mind_bool[70]:=NapakaTSTempTIA5;
mind_bool[71]:=NapakaTSTempTIA6;
mind_bool[72]:=NapakaTSTempTIA7;
mind_bool[73]:=NapakaTSTempTIA8;
mind_bool[74]:=NSX[1].ResetMAX;
mind_bool[75]:=NSX[1].ResetMIN;
mind_bool[76]:=NSX[2].ResetMAX;
mind_bool[77]:=NSX[2].ResetMIN;
mind_bool[78]:=NSX[3].ResetMAX;
mind_bool[79]:=NSX[3].ResetMIN;
mind_bool[80]:=NSX[4].ResetMAX;
mind_bool[81]:=NSX[4].ResetMIN;
mind_bool[82]:=NSX[5].ResetMAX;
mind_bool[83]:=NSX[5].ResetMIN;
mind_bool[84]:=NSX[6].ResetMAX;
mind_bool[85]:=NSX[6].ResetMIN;
mind_bool[86]:=PLC_SB_IROGSM21_F2_2_NOT_OK;
mind_bool[87]:=PLC_SB_IROGSM22_F2_2_NOT_OK;
mind_bool[88]:=PMM.QA1_GlStik_IZKLOP_IZPAD;
mind_bool[89]:=PMM.QB1_GlStik_IZKLOP_IZPAD;
mind_bool[90]:=PMM.SkNapaka_med60in80;
mind_bool[91]:=PMM.SkNapaka_nad80;
mind_bool[92]:=PMM.SkNapakaVirA_med60in80;
mind_bool[93]:=PMM.SkNapakaVirA_nad80;
mind_bool[94]:=PMM.SkNapakaVirB_med60in80;
mind_bool[95]:=PMM.SkNapakaVirB_nad80;
mind_bool[96]:=PMM.VirA_NapakaOzemljitve;
mind_bool[97]:=PMM.VirB_NapakaOzemljitve;
mind_bool[98]:=PrevisokaTemp;
mind_bool[99]:=razlitjeLAH1;
mind_bool[100]:=SetDateTime;
mind_bool[101]:=SetDateTimeDemand;
mind_bool[102]:=SetDateTimeError;
mind_bool[103]:=SetDateTimeFinished;
mind_bool[104]:=SlabaBaterijaPLC;
mind_bool[105]:=TIA1_previs_temp;
mind_bool[106]:=TIA2_previs_temp;
mind_bool[107]:=TIA3_previs_temp;
mind_bool[108]:=TIA4_previs_temp;
mind_bool[109]:=TIA5_previs_temp;
mind_bool[110]:=TIA6_previs_temp;
mind_bool[111]:=TIA7_previs_temp;
mind_bool[112]:=TIA8_previs_temp;
mind_bool[113]:=ups_alarm;
mind_bool[114]:=ups_baterijski_nac;
mind_bool[115]:=ups_polnjenje;
mind_bool[116]:=UserLoggedIn;
mind_bool[117]:=XVH_AlarmOn;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.PLC_Dan;
mind[6]:=DateTime.PLC_DanVTednu;
mind[7]:=DateTime.PLC_Leto;
mind[8]:=DateTime.PLC_Mesec;
mind[9]:=DateTime.PLC_Minuta;
mind[10]:=DateTime.PLC_Sekunda;
mind[11]:=DateTime.PLC_Ura;
mind[12]:=DateTime.Sekunda;
mind[13]:=DateTime.Ura;
mind[14]:=ErrorComPMM[1].Status;
mind[15]:=HIA1_vlaga_s;
mind[16]:=HIA2_vlaga_s;
mind[17]:=HIA3_vlaga_s;
mind[18]:=HIA4_vlaga_s;
mind[19]:=HIA5_vlaga_s;
mind[20]:=HIA6_vlaga_s;
mind[21]:=HIA7_vlaga_s;
mind[22]:=HIA8_vlaga_s;
mind[23]:=TIA1_alarm;
mind[24]:=TIA1_temp_s;
mind[25]:=TIA2_alarm;
mind[26]:=TIA2_temp_s;
mind[27]:=TIA3_alarm;
mind[28]:=TIA3_temp_s;
mind[29]:=TIA4_alarm;
mind[30]:=TIA4_temp_s;
mind[31]:=TIA5_alarm;
mind[32]:=TIA5_temp_s;
mind[33]:=TIA6_alarm;
mind[34]:=TIA6_temp_s;
mind[35]:=TIA7_alarm;
mind[36]:=TIA7_temp_s;
mind[37]:=TIA8_alarm;
mind[38]:=TIA8_temp_s;
mind[39]:=UserCurrentLevel;
(*Branje UINT*)
(**)
mind[8000]:=NSX[1].StatusSwitch;
mind[8001]:=NSX[2].StatusSwitch;
mind[8002]:=NSX[3].StatusSwitch;
mind[8003]:=NSX[4].StatusSwitch;
mind[8004]:=NSX[5].StatusSwitch;
mind[8005]:=NSX[6].StatusSwitch;
mind[8006]:=PMM.VirAAlarmPhase.C01_16_60to80;
mind[8007]:=PMM.VirAAlarmPhase.C01_16_over80;
mind[8008]:=PMM.VirAAlarmPhase.C17_32_60to80;
mind[8009]:=PMM.VirAAlarmPhase.C17_32_over80;
mind[8010]:=PMM.VirAAlarmPhase.C33_44_60to80;
mind[8011]:=PMM.VirAAlarmPhase.C33_44_over80;
mind[8012]:=PMM.VirBAlarmPhase.C01_16_60to80;
mind[8013]:=PMM.VirBAlarmPhase.C01_16_over80;
mind[8014]:=PMM.VirBAlarmPhase.C17_32_60to80;
mind[8015]:=PMM.VirBAlarmPhase.C17_32_over80;
mind[8016]:=PMM.VirBAlarmPhase.C33_44_60to80;
mind[8017]:=PMM.VirBAlarmPhase.C33_44_over80;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=iPMM_VirA_Tok1,lo:=4000,hi:=4001);
Read_Real(rVar:=iPMM_VirA_Tok10,lo:=4002,hi:=4003);
Read_Real(rVar:=iPMM_VirA_Tok11,lo:=4004,hi:=4005);
Read_Real(rVar:=iPMM_VirA_Tok12,lo:=4006,hi:=4007);
Read_Real(rVar:=iPMM_VirA_Tok13,lo:=4008,hi:=4009);
Read_Real(rVar:=iPMM_VirA_Tok14,lo:=4010,hi:=4011);
Read_Real(rVar:=iPMM_VirA_Tok15,lo:=4012,hi:=4013);
Read_Real(rVar:=iPMM_VirA_Tok16,lo:=4014,hi:=4015);
Read_Real(rVar:=iPMM_VirA_Tok17,lo:=4016,hi:=4017);
Read_Real(rVar:=iPMM_VirA_Tok18,lo:=4018,hi:=4019);
Read_Real(rVar:=iPMM_VirA_Tok19,lo:=4020,hi:=4021);
Read_Real(rVar:=iPMM_VirA_Tok2,lo:=4022,hi:=4023);
Read_Real(rVar:=iPMM_VirA_Tok20,lo:=4024,hi:=4025);
Read_Real(rVar:=iPMM_VirA_Tok21,lo:=4026,hi:=4027);
Read_Real(rVar:=iPMM_VirA_Tok22,lo:=4028,hi:=4029);
Read_Real(rVar:=iPMM_VirA_Tok23,lo:=4030,hi:=4031);
Read_Real(rVar:=iPMM_VirA_Tok24,lo:=4032,hi:=4033);
Read_Real(rVar:=iPMM_VirA_Tok25,lo:=4034,hi:=4035);
Read_Real(rVar:=iPMM_VirA_Tok26,lo:=4036,hi:=4037);
Read_Real(rVar:=iPMM_VirA_Tok27,lo:=4038,hi:=4039);
Read_Real(rVar:=iPMM_VirA_Tok28,lo:=4040,hi:=4041);
Read_Real(rVar:=iPMM_VirA_Tok29,lo:=4042,hi:=4043);
Read_Real(rVar:=iPMM_VirA_Tok3,lo:=4044,hi:=4045);
Read_Real(rVar:=iPMM_VirA_Tok30,lo:=4046,hi:=4047);
Read_Real(rVar:=iPMM_VirA_Tok31,lo:=4048,hi:=4049);
Read_Real(rVar:=iPMM_VirA_Tok32,lo:=4050,hi:=4051);
Read_Real(rVar:=iPMM_VirA_Tok33,lo:=4052,hi:=4053);
Read_Real(rVar:=iPMM_VirA_Tok34,lo:=4054,hi:=4055);
Read_Real(rVar:=iPMM_VirA_Tok35,lo:=4056,hi:=4057);
Read_Real(rVar:=iPMM_VirA_Tok36,lo:=4058,hi:=4059);
Read_Real(rVar:=iPMM_VirA_Tok37,lo:=4060,hi:=4061);
Read_Real(rVar:=iPMM_VirA_Tok38,lo:=4062,hi:=4063);
Read_Real(rVar:=iPMM_VirA_Tok39,lo:=4064,hi:=4065);
Read_Real(rVar:=iPMM_VirA_Tok4,lo:=4066,hi:=4067);
Read_Real(rVar:=iPMM_VirA_Tok40,lo:=4068,hi:=4069);
Read_Real(rVar:=iPMM_VirA_Tok41,lo:=4070,hi:=4071);
Read_Real(rVar:=iPMM_VirA_Tok42,lo:=4072,hi:=4073);
Read_Real(rVar:=iPMM_VirA_Tok43,lo:=4074,hi:=4075);
Read_Real(rVar:=iPMM_VirA_Tok44,lo:=4076,hi:=4077);
Read_Real(rVar:=iPMM_VirA_Tok5,lo:=4078,hi:=4079);
Read_Real(rVar:=iPMM_VirA_Tok6,lo:=4080,hi:=4081);
Read_Real(rVar:=iPMM_VirA_Tok7,lo:=4082,hi:=4083);
Read_Real(rVar:=iPMM_VirA_Tok8,lo:=4084,hi:=4085);
Read_Real(rVar:=iPMM_VirA_Tok9,lo:=4086,hi:=4087);
Read_Real(rVar:=iPMM_VirB_Tok1,lo:=4088,hi:=4089);
Read_Real(rVar:=iPMM_VirB_Tok10,lo:=4090,hi:=4091);
Read_Real(rVar:=iPMM_VirB_Tok11,lo:=4092,hi:=4093);
Read_Real(rVar:=iPMM_VirB_Tok12,lo:=4094,hi:=4095);
Read_Real(rVar:=iPMM_VirB_Tok13,lo:=4096,hi:=4097);
Read_Real(rVar:=iPMM_VirB_Tok14,lo:=4098,hi:=4099);
Read_Real(rVar:=iPMM_VirB_Tok15,lo:=4100,hi:=4101);
Read_Real(rVar:=iPMM_VirB_Tok16,lo:=4102,hi:=4103);
Read_Real(rVar:=iPMM_VirB_Tok17,lo:=4104,hi:=4105);
Read_Real(rVar:=iPMM_VirB_Tok18,lo:=4106,hi:=4107);
Read_Real(rVar:=iPMM_VirB_Tok19,lo:=4108,hi:=4109);
Read_Real(rVar:=iPMM_VirB_Tok2,lo:=4110,hi:=4111);
Read_Real(rVar:=iPMM_VirB_Tok20,lo:=4112,hi:=4113);
Read_Real(rVar:=iPMM_VirB_Tok21,lo:=4114,hi:=4115);
Read_Real(rVar:=iPMM_VirB_Tok22,lo:=4116,hi:=4117);
Read_Real(rVar:=iPMM_VirB_Tok23,lo:=4118,hi:=4119);
Read_Real(rVar:=iPMM_VirB_Tok24,lo:=4120,hi:=4121);
Read_Real(rVar:=iPMM_VirB_Tok25,lo:=4122,hi:=4123);
Read_Real(rVar:=iPMM_VirB_Tok26,lo:=4124,hi:=4125);
Read_Real(rVar:=iPMM_VirB_Tok27,lo:=4126,hi:=4127);
Read_Real(rVar:=iPMM_VirB_Tok28,lo:=4128,hi:=4129);
Read_Real(rVar:=iPMM_VirB_Tok29,lo:=4130,hi:=4131);
Read_Real(rVar:=iPMM_VirB_Tok3,lo:=4132,hi:=4133);
Read_Real(rVar:=iPMM_VirB_Tok30,lo:=4134,hi:=4135);
Read_Real(rVar:=iPMM_VirB_Tok31,lo:=4136,hi:=4137);
Read_Real(rVar:=iPMM_VirB_Tok32,lo:=4138,hi:=4139);
Read_Real(rVar:=iPMM_VirB_Tok33,lo:=4140,hi:=4141);
Read_Real(rVar:=iPMM_VirB_Tok34,lo:=4142,hi:=4143);
Read_Real(rVar:=iPMM_VirB_Tok35,lo:=4144,hi:=4145);
Read_Real(rVar:=iPMM_VirB_Tok36,lo:=4146,hi:=4147);
Read_Real(rVar:=iPMM_VirB_Tok37,lo:=4148,hi:=4149);
Read_Real(rVar:=iPMM_VirB_Tok38,lo:=4150,hi:=4151);
Read_Real(rVar:=iPMM_VirB_Tok39,lo:=4152,hi:=4153);
Read_Real(rVar:=iPMM_VirB_Tok4,lo:=4154,hi:=4155);
Read_Real(rVar:=iPMM_VirB_Tok40,lo:=4156,hi:=4157);
Read_Real(rVar:=iPMM_VirB_Tok41,lo:=4158,hi:=4159);
Read_Real(rVar:=iPMM_VirB_Tok42,lo:=4160,hi:=4161);
Read_Real(rVar:=iPMM_VirB_Tok43,lo:=4162,hi:=4163);
Read_Real(rVar:=iPMM_VirB_Tok44,lo:=4164,hi:=4165);
Read_Real(rVar:=iPMM_VirB_Tok5,lo:=4166,hi:=4167);
Read_Real(rVar:=iPMM_VirB_Tok6,lo:=4168,hi:=4169);
Read_Real(rVar:=iPMM_VirB_Tok7,lo:=4170,hi:=4171);
Read_Real(rVar:=iPMM_VirB_Tok8,lo:=4172,hi:=4173);
Read_Real(rVar:=iPMM_VirB_Tok9,lo:=4174,hi:=4175);
Read_Real(rVar:=NSX[1].ActiveEnergy_kWh,lo:=4176,hi:=4177);
Read_Real(rVar:=NSX[1].ActiveNegativeEnergy_kWh,lo:=4178,hi:=4179);
Read_Real(rVar:=NSX[1].ActivePositiveEnergy_kWh,lo:=4180,hi:=4181);
Read_Real(rVar:=NSX[1].ActivePowerDemand_kW,lo:=4182,hi:=4183);
Read_Real(rVar:=NSX[1].ActivePowerL1_kW,lo:=4184,hi:=4185);
Read_Real(rVar:=NSX[1].ActivePowerL2_kW,lo:=4186,hi:=4187);
Read_Real(rVar:=NSX[1].ActivePowerL3_kW,lo:=4188,hi:=4189);
Read_Real(rVar:=NSX[1].ActivePowerMaxDemand_kW,lo:=4190,hi:=4191);
Read_Real(rVar:=NSX[1].ActivePowerTotal_kW,lo:=4192,hi:=4193);
Read_Real(rVar:=NSX[1].ApparentEnergy_kVAh,lo:=4194,hi:=4195);
Read_Real(rVar:=NSX[1].ApparentPowerDemand_kVA,lo:=4196,hi:=4197);
Read_Real(rVar:=NSX[1].ApparentPowerMaxDemand_kVA,lo:=4198,hi:=4199);
Read_Real(rVar:=NSX[1].ApparetnPowerL1_kVA,lo:=4200,hi:=4201);
Read_Real(rVar:=NSX[1].ApparetnPowerL2_kVA,lo:=4202,hi:=4203);
Read_Real(rVar:=NSX[1].ApparetnPowerL3_kVA,lo:=4204,hi:=4205);
Read_Real(rVar:=NSX[1].ApparetnPowerTotal_kVA,lo:=4206,hi:=4207);
Read_Real(rVar:=NSX[1].CosFL1,lo:=4208,hi:=4209);
Read_Real(rVar:=NSX[1].CosFL2,lo:=4210,hi:=4211);
Read_Real(rVar:=NSX[1].CosFL3,lo:=4212,hi:=4213);
Read_Real(rVar:=NSX[1].CosFTotal,lo:=4214,hi:=4215);
Read_Real(rVar:=NSX[1].CumulNegativeActiveEnergy_kWh,lo:=4216,hi:=4217);
Read_Real(rVar:=NSX[1].CumulPositiveActiveEnergy_kWh,lo:=4218,hi:=4219);
Read_Real(rVar:=NSX[1].CurrentAvgI1I2I3_A,lo:=4220,hi:=4221);
Read_Real(rVar:=NSX[1].CurrentDemandL1_A,lo:=4222,hi:=4223);
Read_Real(rVar:=NSX[1].CurrentDemandL2_A,lo:=4224,hi:=4225);
Read_Real(rVar:=NSX[1].CurrentDemandL3_A,lo:=4226,hi:=4227);
Read_Real(rVar:=NSX[1].CurrentDemandMaxL1_A,lo:=4228,hi:=4229);
Read_Real(rVar:=NSX[1].CurrentDemandMaxL2_A,lo:=4230,hi:=4231);
Read_Real(rVar:=NSX[1].CurrentDemandMaxL3_A,lo:=4232,hi:=4233);
Read_Real(rVar:=NSX[1].CurrentDemandMaxN_A,lo:=4234,hi:=4235);
Read_Real(rVar:=NSX[1].CurrentDemandN_A,lo:=4236,hi:=4237);
Read_Real(rVar:=NSX[1].CurrentL1_A,lo:=4238,hi:=4239);
Read_Real(rVar:=NSX[1].CurrentL2_A,lo:=4240,hi:=4241);
Read_Real(rVar:=NSX[1].CurrentL3_A,lo:=4242,hi:=4243);
Read_Real(rVar:=NSX[1].CurrentN_A,lo:=4244,hi:=4245);
Read_Real(rVar:=NSX[1].CurrentUnbI1_P,lo:=4246,hi:=4247);
Read_Real(rVar:=NSX[1].CurrentUnbI2_P,lo:=4248,hi:=4249);
Read_Real(rVar:=NSX[1].CurrentUnbI3_P,lo:=4250,hi:=4251);
Read_Real(rVar:=NSX[1].CurrentUnbN_P,lo:=4252,hi:=4253);
Read_Real(rVar:=NSX[1].DelovnaEnergija_TEMP,lo:=4254,hi:=4255);
Read_Real(rVar:=NSX[1].DistortionPowerL1_kVAr,lo:=4256,hi:=4257);
Read_Real(rVar:=NSX[1].DistortionPowerL2_kVAr,lo:=4258,hi:=4259);
Read_Real(rVar:=NSX[1].DistortionPowerL3_kVAr,lo:=4260,hi:=4261);
Read_Real(rVar:=NSX[1].DistortionPowerTotal_kVAr,lo:=4262,hi:=4263);
Read_Real(rVar:=NSX[1].Frequency_Hz,lo:=4264,hi:=4265);
Read_Real(rVar:=NSX[1].FunReactivePowerL1_kVAr,lo:=4266,hi:=4267);
Read_Real(rVar:=NSX[1].FunReactivePowerL2_kVAr,lo:=4268,hi:=4269);
Read_Real(rVar:=NSX[1].FunReactivePowerL3_kVAr,lo:=4270,hi:=4271);
Read_Real(rVar:=NSX[1].FunReactivePowerTotal_kVAr,lo:=4272,hi:=4273);
Read_Real(rVar:=NSX[1].MAX_ActivePowerL1_kW,lo:=4274,hi:=4275);
Read_Real(rVar:=NSX[1].MAX_ActivePowerL2_kW,lo:=4276,hi:=4277);
Read_Real(rVar:=NSX[1].MAX_ActivePowerL3_kW,lo:=4278,hi:=4279);
Read_Real(rVar:=NSX[1].MAX_ActivePowerTotal_kW,lo:=4280,hi:=4281);
Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL1_kVA,lo:=4282,hi:=4283);
Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL2_kVA,lo:=4284,hi:=4285);
Read_Real(rVar:=NSX[1].MAX_ApparetnPowerL3_kVA,lo:=4286,hi:=4287);
Read_Real(rVar:=NSX[1].MAX_ApparetnPowerTotal_kVA,lo:=4288,hi:=4289);
Read_Real(rVar:=NSX[1].MAX_CosFL1,lo:=4290,hi:=4291);
Read_Real(rVar:=NSX[1].MAX_CosFL2,lo:=4292,hi:=4293);
Read_Real(rVar:=NSX[1].MAX_CosFL3,lo:=4294,hi:=4295);
Read_Real(rVar:=NSX[1].MAX_CosFTotal,lo:=4296,hi:=4297);
Read_Real(rVar:=NSX[1].MAX_CurrentAvgI1I2I3_A,lo:=4298,hi:=4299);
Read_Real(rVar:=NSX[1].MAX_CurrentL1_A,lo:=4300,hi:=4301);
Read_Real(rVar:=NSX[1].MAX_CurrentL2_A,lo:=4302,hi:=4303);
Read_Real(rVar:=NSX[1].MAX_CurrentL3_A,lo:=4304,hi:=4305);
Read_Real(rVar:=NSX[1].MAX_CurrentMaxL1L2L3N_A,lo:=4306,hi:=4307);
Read_Real(rVar:=NSX[1].MAX_CurrentN_A,lo:=4308,hi:=4309);
Read_Real(rVar:=NSX[1].MAX_DistortionPowerL1_kVAr,lo:=4310,hi:=4311);
Read_Real(rVar:=NSX[1].MAX_DistortionPowerL2_kVAr,lo:=4312,hi:=4313);
Read_Real(rVar:=NSX[1].MAX_DistortionPowerL3_kVAr,lo:=4314,hi:=4315);
Read_Real(rVar:=NSX[1].MAX_DistortionPowerTotal_kVAr,lo:=4316,hi:=4317);
Read_Real(rVar:=NSX[1].MAX_Frequency_Hz,lo:=4318,hi:=4319);
Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL1_kVAr,lo:=4320,hi:=4321);
Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL2_kVAr,lo:=4322,hi:=4323);
Read_Real(rVar:=NSX[1].MAX_FunReactivePowerL3_kVAr,lo:=4324,hi:=4325);
Read_Real(rVar:=NSX[1].MAX_FunReactivePowerTotal_kVAr,lo:=4326,hi:=4327);
Read_Real(rVar:=NSX[1].MAX_PowerFactorL1,lo:=4328,hi:=4329);
Read_Real(rVar:=NSX[1].MAX_PowerFactorL2,lo:=4330,hi:=4331);
Read_Real(rVar:=NSX[1].MAX_PowerFactorL3,lo:=4332,hi:=4333);
Read_Real(rVar:=NSX[1].MAX_PowerFactorTotal,lo:=4334,hi:=4335);
Read_Real(rVar:=NSX[1].MAX_ReactivePowerL1_kVAr,lo:=4336,hi:=4337);
Read_Real(rVar:=NSX[1].MAX_ReactivePowerL2_kVAr,lo:=4338,hi:=4339);
Read_Real(rVar:=NSX[1].MAX_ReactivePowerL3_kVAr,lo:=4340,hi:=4341);
Read_Real(rVar:=NSX[1].MAX_ReactivePowerTotal_kVAr,lo:=4342,hi:=4343);
Read_Real(rVar:=NSX[1].MAX_THDI1_P,lo:=4344,hi:=4345);
Read_Real(rVar:=NSX[1].MAX_THDI2_P,lo:=4346,hi:=4347);
Read_Real(rVar:=NSX[1].MAX_THDI3_P,lo:=4348,hi:=4349);
Read_Real(rVar:=NSX[1].MAX_THDV12_P,lo:=4350,hi:=4351);
Read_Real(rVar:=NSX[1].MAX_THDV1N_P,lo:=4352,hi:=4353);
Read_Real(rVar:=NSX[1].MAX_THDV23_P,lo:=4354,hi:=4355);
Read_Real(rVar:=NSX[1].MAX_THDV2N_P,lo:=4356,hi:=4357);
Read_Real(rVar:=NSX[1].MAX_THDV31_P,lo:=4358,hi:=4359);
Read_Real(rVar:=NSX[1].MAX_THDV3N_P,lo:=4360,hi:=4361);
Read_Real(rVar:=NSX[1].MAX_VoltageAvgPhToN_V,lo:=4362,hi:=4363);
Read_Real(rVar:=NSX[1].MAX_VoltageAvgPhToPh_V,lo:=4364,hi:=4365);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV12_P,lo:=4366,hi:=4367);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV1N_P,lo:=4368,hi:=4369);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV23_P,lo:=4370,hi:=4371);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV2N_P,lo:=4372,hi:=4373);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV31_P,lo:=4374,hi:=4375);
Read_Real(rVar:=NSX[1].MAX_VoltageUnbV3N_P,lo:=4376,hi:=4377);
Read_Real(rVar:=NSX[1].MAX_VoltageV12_V,lo:=4378,hi:=4379);
Read_Real(rVar:=NSX[1].MAX_VoltageV1N_V,lo:=4380,hi:=4381);
Read_Real(rVar:=NSX[1].MAX_VoltageV23_V,lo:=4382,hi:=4383);
Read_Real(rVar:=NSX[1].MAX_VoltageV2N_V,lo:=4384,hi:=4385);
Read_Real(rVar:=NSX[1].MAX_VoltageV31_V,lo:=4386,hi:=4387);
Read_Real(rVar:=NSX[1].MAX_VoltageV3N_V,lo:=4388,hi:=4389);
Read_Real(rVar:=NSX[1].MIN_ActivePowerL1_kW,lo:=4390,hi:=4391);
Read_Real(rVar:=NSX[1].MIN_ActivePowerL2_kW,lo:=4392,hi:=4393);
Read_Real(rVar:=NSX[1].MIN_ActivePowerL3_kW,lo:=4394,hi:=4395);
Read_Real(rVar:=NSX[1].MIN_ActivePowerTotal_kW,lo:=4396,hi:=4397);
Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL1_kVA,lo:=4398,hi:=4399);
Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL2_kVA,lo:=4400,hi:=4401);
Read_Real(rVar:=NSX[1].MIN_ApparetnPowerL3_kVA,lo:=4402,hi:=4403);
Read_Real(rVar:=NSX[1].MIN_ApparetnPowerTotal_kVA,lo:=4404,hi:=4405);
Read_Real(rVar:=NSX[1].MIN_CosFL1,lo:=4406,hi:=4407);
Read_Real(rVar:=NSX[1].MIN_CosFL2,lo:=4408,hi:=4409);
Read_Real(rVar:=NSX[1].MIN_CosFL3,lo:=4410,hi:=4411);
Read_Real(rVar:=NSX[1].MIN_CosFTotal,lo:=4412,hi:=4413);
Read_Real(rVar:=NSX[1].MIN_CurrentAvgI1I2I3_A,lo:=4414,hi:=4415);
Read_Real(rVar:=NSX[1].MIN_CurrentL1_A,lo:=4416,hi:=4417);
Read_Real(rVar:=NSX[1].MIN_CurrentL2_A,lo:=4418,hi:=4419);
Read_Real(rVar:=NSX[1].MIN_CurrentL3_A,lo:=4420,hi:=4421);
Read_Real(rVar:=NSX[1].MIN_CurrentMaxL1L2L3N_A,lo:=4422,hi:=4423);
Read_Real(rVar:=NSX[1].MIN_CurrentN_A,lo:=4424,hi:=4425);
Read_Real(rVar:=NSX[1].MIN_DistortionPowerL1_kVAr,lo:=4426,hi:=4427);
Read_Real(rVar:=NSX[1].MIN_DistortionPowerL2_kVAr,lo:=4428,hi:=4429);
Read_Real(rVar:=NSX[1].MIN_DistortionPowerL3_kVAr,lo:=4430,hi:=4431);
Read_Real(rVar:=NSX[1].MIN_DistortionPowerTotal_kVAr,lo:=4432,hi:=4433);
Read_Real(rVar:=NSX[1].MIN_Frequency_Hz,lo:=4434,hi:=4435);
Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL1_kVAr,lo:=4436,hi:=4437);
Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL2_kVAr,lo:=4438,hi:=4439);
Read_Real(rVar:=NSX[1].MIN_FunReactivePowerL3_kVAr,lo:=4440,hi:=4441);
Read_Real(rVar:=NSX[1].MIN_FunReactivePowerTotal_kVAr,lo:=4442,hi:=4443);
Read_Real(rVar:=NSX[1].MIN_PowerFactorL1,lo:=4444,hi:=4445);
Read_Real(rVar:=NSX[1].MIN_PowerFactorL2,lo:=4446,hi:=4447);
Read_Real(rVar:=NSX[1].MIN_PowerFactorL3,lo:=4448,hi:=4449);
Read_Real(rVar:=NSX[1].MIN_PowerFactorTotal,lo:=4450,hi:=4451);
Read_Real(rVar:=NSX[1].MIN_ReactivePowerL1_kVAr,lo:=4452,hi:=4453);
Read_Real(rVar:=NSX[1].MIN_ReactivePowerL2_kVAr,lo:=4454,hi:=4455);
Read_Real(rVar:=NSX[1].MIN_ReactivePowerL3_kVAr,lo:=4456,hi:=4457);
Read_Real(rVar:=NSX[1].MIN_ReactivePowerTotal_kVAr,lo:=4458,hi:=4459);
Read_Real(rVar:=NSX[1].MIN_THDI1_P,lo:=4460,hi:=4461);
Read_Real(rVar:=NSX[1].MIN_THDI2_P,lo:=4462,hi:=4463);
Read_Real(rVar:=NSX[1].MIN_THDI3_P,lo:=4464,hi:=4465);
Read_Real(rVar:=NSX[1].MIN_THDV12_P,lo:=4466,hi:=4467);
Read_Real(rVar:=NSX[1].MIN_THDV1N_P,lo:=4468,hi:=4469);
Read_Real(rVar:=NSX[1].MIN_THDV23_P,lo:=4470,hi:=4471);
Read_Real(rVar:=NSX[1].MIN_THDV2N_P,lo:=4472,hi:=4473);
Read_Real(rVar:=NSX[1].MIN_THDV31_P,lo:=4474,hi:=4475);
Read_Real(rVar:=NSX[1].MIN_THDV3N_P,lo:=4476,hi:=4477);
Read_Real(rVar:=NSX[1].MIN_VoltageAvgPhToN_V,lo:=4478,hi:=4479);
Read_Real(rVar:=NSX[1].MIN_VoltageAvgPhToPh_V,lo:=4480,hi:=4481);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV12_P,lo:=4482,hi:=4483);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV1N_P,lo:=4484,hi:=4485);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV23_P,lo:=4486,hi:=4487);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV2N_P,lo:=4488,hi:=4489);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV31_P,lo:=4490,hi:=4491);
Read_Real(rVar:=NSX[1].MIN_VoltageUnbV3N_P,lo:=4492,hi:=4493);
Read_Real(rVar:=NSX[1].MIN_VoltageV12_V,lo:=4494,hi:=4495);
Read_Real(rVar:=NSX[1].MIN_VoltageV1N_V,lo:=4496,hi:=4497);
Read_Real(rVar:=NSX[1].MIN_VoltageV23_V,lo:=4498,hi:=4499);
Read_Real(rVar:=NSX[1].MIN_VoltageV2N_V,lo:=4500,hi:=4501);
Read_Real(rVar:=NSX[1].MIN_VoltageV31_V,lo:=4502,hi:=4503);
Read_Real(rVar:=NSX[1].MIN_VoltageV3N_V,lo:=4504,hi:=4505);
Read_Real(rVar:=NSX[1].PowerFactorL1,lo:=4506,hi:=4507);
Read_Real(rVar:=NSX[1].PowerFactorL2,lo:=4508,hi:=4509);
Read_Real(rVar:=NSX[1].PowerFactorL3,lo:=4510,hi:=4511);
Read_Real(rVar:=NSX[1].PowerFactorTotal,lo:=4512,hi:=4513);
Read_Real(rVar:=NSX[1].RazEner_D,lo:=4514,hi:=4515);
Read_Real(rVar:=NSX[1].RazEner_D_SCADA,lo:=4516,hi:=4517);
Read_Real(rVar:=NSX[1].RazEner_D_TEMP,lo:=4518,hi:=4519);
Read_Real(rVar:=NSX[1].RazEner_M,lo:=4520,hi:=4521);
Read_Real(rVar:=NSX[1].RazEner_M_SCADA,lo:=4522,hi:=4523);
Read_Real(rVar:=NSX[1].RazEner_M_TEMP,lo:=4524,hi:=4525);
Read_Real(rVar:=NSX[1].RazEner_T,lo:=4526,hi:=4527);
Read_Real(rVar:=NSX[1].RazEner_T_SCADA,lo:=4528,hi:=4529);
Read_Real(rVar:=NSX[1].RazEner_T_TEMP,lo:=4530,hi:=4531);
Read_Real(rVar:=NSX[1].ReactiveEnergy_kVArh,lo:=4532,hi:=4533);
Read_Real(rVar:=NSX[1].ReactiveNegativeEnergy_kVArh,lo:=4534,hi:=4535);
Read_Real(rVar:=NSX[1].ReactivePositiveEnergy_kVArh,lo:=4536,hi:=4537);
Read_Real(rVar:=NSX[1].ReactivePowerDemand_kVAr,lo:=4538,hi:=4539);
Read_Real(rVar:=NSX[1].ReactivePowerL1_kVAr,lo:=4540,hi:=4541);
Read_Real(rVar:=NSX[1].ReactivePowerL2_kVAr,lo:=4542,hi:=4543);
Read_Real(rVar:=NSX[1].ReactivePowerL3_kVAr,lo:=4544,hi:=4545);
Read_Real(rVar:=NSX[1].ReactivePowerMaxDemand_kVAr,lo:=4546,hi:=4547);
Read_Real(rVar:=NSX[1].ReactivePowerTotal_kVAr,lo:=4548,hi:=4549);
Read_Real(rVar:=NSX[1].THDI1_P,lo:=4550,hi:=4551);
Read_Real(rVar:=NSX[1].THDI2_P,lo:=4552,hi:=4553);
Read_Real(rVar:=NSX[1].THDI3_P,lo:=4554,hi:=4555);
Read_Real(rVar:=NSX[1].THDV12_P,lo:=4556,hi:=4557);
Read_Real(rVar:=NSX[1].THDV1N_P,lo:=4558,hi:=4559);
Read_Real(rVar:=NSX[1].THDV23_P,lo:=4560,hi:=4561);
Read_Real(rVar:=NSX[1].THDV2N_P,lo:=4562,hi:=4563);
Read_Real(rVar:=NSX[1].THDV31_P,lo:=4564,hi:=4565);
Read_Real(rVar:=NSX[1].THDV3N_P,lo:=4566,hi:=4567);
Read_Real(rVar:=NSX[1].VoltageAvgPhToN_V,lo:=4568,hi:=4569);
Read_Real(rVar:=NSX[1].VoltageAvgPhToPh_V,lo:=4570,hi:=4571);
Read_Real(rVar:=NSX[1].VoltageUnbV12_P,lo:=4572,hi:=4573);
Read_Real(rVar:=NSX[1].VoltageUnbV1N_P,lo:=4574,hi:=4575);
Read_Real(rVar:=NSX[1].VoltageUnbV23_P,lo:=4576,hi:=4577);
Read_Real(rVar:=NSX[1].VoltageUnbV2N_P,lo:=4578,hi:=4579);
Read_Real(rVar:=NSX[1].VoltageUnbV31_P,lo:=4580,hi:=4581);
Read_Real(rVar:=NSX[1].VoltageUnbV3N_P,lo:=4582,hi:=4583);
Read_Real(rVar:=NSX[1].VoltageV12_V,lo:=4584,hi:=4585);
Read_Real(rVar:=NSX[1].VoltageV1N_V,lo:=4586,hi:=4587);
Read_Real(rVar:=NSX[1].VoltageV23_V,lo:=4588,hi:=4589);
Read_Real(rVar:=NSX[1].VoltageV2N_V,lo:=4590,hi:=4591);
Read_Real(rVar:=NSX[1].VoltageV31_V,lo:=4592,hi:=4593);
Read_Real(rVar:=NSX[1].VoltageV3N_V,lo:=4594,hi:=4595);
Read_Real(rVar:=NSX[2].ActiveEnergy_kWh,lo:=4596,hi:=4597);
Read_Real(rVar:=NSX[2].ActiveNegativeEnergy_kWh,lo:=4598,hi:=4599);
Read_Real(rVar:=NSX[2].ActivePositiveEnergy_kWh,lo:=4600,hi:=4601);
Read_Real(rVar:=NSX[2].ActivePowerDemand_kW,lo:=4602,hi:=4603);
Read_Real(rVar:=NSX[2].ActivePowerL1_kW,lo:=4604,hi:=4605);
Read_Real(rVar:=NSX[2].ActivePowerL2_kW,lo:=4606,hi:=4607);
Read_Real(rVar:=NSX[2].ActivePowerL3_kW,lo:=4608,hi:=4609);
Read_Real(rVar:=NSX[2].ActivePowerMaxDemand_kW,lo:=4610,hi:=4611);
Read_Real(rVar:=NSX[2].ActivePowerTotal_kW,lo:=4612,hi:=4613);
Read_Real(rVar:=NSX[2].ApparentEnergy_kVAh,lo:=4614,hi:=4615);
Read_Real(rVar:=NSX[2].ApparentPowerDemand_kVA,lo:=4616,hi:=4617);
Read_Real(rVar:=NSX[2].ApparentPowerMaxDemand_kVA,lo:=4618,hi:=4619);
Read_Real(rVar:=NSX[2].ApparetnPowerL1_kVA,lo:=4620,hi:=4621);
Read_Real(rVar:=NSX[2].ApparetnPowerL2_kVA,lo:=4622,hi:=4623);
Read_Real(rVar:=NSX[2].ApparetnPowerL3_kVA,lo:=4624,hi:=4625);
Read_Real(rVar:=NSX[2].ApparetnPowerTotal_kVA,lo:=4626,hi:=4627);
Read_Real(rVar:=NSX[2].CosFL1,lo:=4628,hi:=4629);
Read_Real(rVar:=NSX[2].CosFL2,lo:=4630,hi:=4631);
Read_Real(rVar:=NSX[2].CosFL3,lo:=4632,hi:=4633);
Read_Real(rVar:=NSX[2].CosFTotal,lo:=4634,hi:=4635);
Read_Real(rVar:=NSX[2].CumulNegativeActiveEnergy_kWh,lo:=4636,hi:=4637);
Read_Real(rVar:=NSX[2].CumulPositiveActiveEnergy_kWh,lo:=4638,hi:=4639);
Read_Real(rVar:=NSX[2].CurrentAvgI1I2I3_A,lo:=4640,hi:=4641);
Read_Real(rVar:=NSX[2].CurrentDemandL1_A,lo:=4642,hi:=4643);
Read_Real(rVar:=NSX[2].CurrentDemandL2_A,lo:=4644,hi:=4645);
Read_Real(rVar:=NSX[2].CurrentDemandL3_A,lo:=4646,hi:=4647);
Read_Real(rVar:=NSX[2].CurrentDemandMaxL1_A,lo:=4648,hi:=4649);
Read_Real(rVar:=NSX[2].CurrentDemandMaxL2_A,lo:=4650,hi:=4651);
Read_Real(rVar:=NSX[2].CurrentDemandMaxL3_A,lo:=4652,hi:=4653);
Read_Real(rVar:=NSX[2].CurrentDemandMaxN_A,lo:=4654,hi:=4655);
Read_Real(rVar:=NSX[2].CurrentDemandN_A,lo:=4656,hi:=4657);
Read_Real(rVar:=NSX[2].CurrentL1_A,lo:=4658,hi:=4659);
Read_Real(rVar:=NSX[2].CurrentL2_A,lo:=4660,hi:=4661);
Read_Real(rVar:=NSX[2].CurrentL3_A,lo:=4662,hi:=4663);
Read_Real(rVar:=NSX[2].CurrentN_A,lo:=4664,hi:=4665);
Read_Real(rVar:=NSX[2].CurrentUnbI1_P,lo:=4666,hi:=4667);
Read_Real(rVar:=NSX[2].CurrentUnbI2_P,lo:=4668,hi:=4669);
Read_Real(rVar:=NSX[2].CurrentUnbI3_P,lo:=4670,hi:=4671);
Read_Real(rVar:=NSX[2].CurrentUnbN_P,lo:=4672,hi:=4673);
Read_Real(rVar:=NSX[2].DelovnaEnergija_TEMP,lo:=4674,hi:=4675);
Read_Real(rVar:=NSX[2].DistortionPowerL1_kVAr,lo:=4676,hi:=4677);
Read_Real(rVar:=NSX[2].DistortionPowerL2_kVAr,lo:=4678,hi:=4679);
Read_Real(rVar:=NSX[2].DistortionPowerL3_kVAr,lo:=4680,hi:=4681);
Read_Real(rVar:=NSX[2].DistortionPowerTotal_kVAr,lo:=4682,hi:=4683);
Read_Real(rVar:=NSX[2].Frequency_Hz,lo:=4684,hi:=4685);
Read_Real(rVar:=NSX[2].FunReactivePowerL1_kVAr,lo:=4686,hi:=4687);
Read_Real(rVar:=NSX[2].FunReactivePowerL2_kVAr,lo:=4688,hi:=4689);
Read_Real(rVar:=NSX[2].FunReactivePowerL3_kVAr,lo:=4690,hi:=4691);
Read_Real(rVar:=NSX[2].FunReactivePowerTotal_kVAr,lo:=4692,hi:=4693);
Read_Real(rVar:=NSX[2].MAX_ActivePowerL1_kW,lo:=4694,hi:=4695);
Read_Real(rVar:=NSX[2].MAX_ActivePowerL2_kW,lo:=4696,hi:=4697);
Read_Real(rVar:=NSX[2].MAX_ActivePowerL3_kW,lo:=4698,hi:=4699);
Read_Real(rVar:=NSX[2].MAX_ActivePowerTotal_kW,lo:=4700,hi:=4701);
Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL1_kVA,lo:=4702,hi:=4703);
Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL2_kVA,lo:=4704,hi:=4705);
Read_Real(rVar:=NSX[2].MAX_ApparetnPowerL3_kVA,lo:=4706,hi:=4707);
Read_Real(rVar:=NSX[2].MAX_ApparetnPowerTotal_kVA,lo:=4708,hi:=4709);
Read_Real(rVar:=NSX[2].MAX_CosFL1,lo:=4710,hi:=4711);
Read_Real(rVar:=NSX[2].MAX_CosFL2,lo:=4712,hi:=4713);
Read_Real(rVar:=NSX[2].MAX_CosFL3,lo:=4714,hi:=4715);
Read_Real(rVar:=NSX[2].MAX_CosFTotal,lo:=4716,hi:=4717);
Read_Real(rVar:=NSX[2].MAX_CurrentAvgI1I2I3_A,lo:=4718,hi:=4719);
Read_Real(rVar:=NSX[2].MAX_CurrentL1_A,lo:=4720,hi:=4721);
Read_Real(rVar:=NSX[2].MAX_CurrentL2_A,lo:=4722,hi:=4723);
Read_Real(rVar:=NSX[2].MAX_CurrentL3_A,lo:=4724,hi:=4725);
Read_Real(rVar:=NSX[2].MAX_CurrentMaxL1L2L3N_A,lo:=4726,hi:=4727);
Read_Real(rVar:=NSX[2].MAX_CurrentN_A,lo:=4728,hi:=4729);
Read_Real(rVar:=NSX[2].MAX_DistortionPowerL1_kVAr,lo:=4730,hi:=4731);
Read_Real(rVar:=NSX[2].MAX_DistortionPowerL2_kVAr,lo:=4732,hi:=4733);
Read_Real(rVar:=NSX[2].MAX_DistortionPowerL3_kVAr,lo:=4734,hi:=4735);
Read_Real(rVar:=NSX[2].MAX_DistortionPowerTotal_kVAr,lo:=4736,hi:=4737);
Read_Real(rVar:=NSX[2].MAX_Frequency_Hz,lo:=4738,hi:=4739);
Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL1_kVAr,lo:=4740,hi:=4741);
Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL2_kVAr,lo:=4742,hi:=4743);
Read_Real(rVar:=NSX[2].MAX_FunReactivePowerL3_kVAr,lo:=4744,hi:=4745);
Read_Real(rVar:=NSX[2].MAX_FunReactivePowerTotal_kVAr,lo:=4746,hi:=4747);
Read_Real(rVar:=NSX[2].MAX_PowerFactorL1,lo:=4748,hi:=4749);
Read_Real(rVar:=NSX[2].MAX_PowerFactorL2,lo:=4750,hi:=4751);
Read_Real(rVar:=NSX[2].MAX_PowerFactorL3,lo:=4752,hi:=4753);
Read_Real(rVar:=NSX[2].MAX_PowerFactorTotal,lo:=4754,hi:=4755);
Read_Real(rVar:=NSX[2].MAX_ReactivePowerL1_kVAr,lo:=4756,hi:=4757);
Read_Real(rVar:=NSX[2].MAX_ReactivePowerL2_kVAr,lo:=4758,hi:=4759);
Read_Real(rVar:=NSX[2].MAX_ReactivePowerL3_kVAr,lo:=4760,hi:=4761);
Read_Real(rVar:=NSX[2].MAX_ReactivePowerTotal_kVAr,lo:=4762,hi:=4763);
Read_Real(rVar:=NSX[2].MAX_THDI1_P,lo:=4764,hi:=4765);
Read_Real(rVar:=NSX[2].MAX_THDI2_P,lo:=4766,hi:=4767);
Read_Real(rVar:=NSX[2].MAX_THDI3_P,lo:=4768,hi:=4769);
Read_Real(rVar:=NSX[2].MAX_THDV12_P,lo:=4770,hi:=4771);
Read_Real(rVar:=NSX[2].MAX_THDV1N_P,lo:=4772,hi:=4773);
Read_Real(rVar:=NSX[2].MAX_THDV23_P,lo:=4774,hi:=4775);
Read_Real(rVar:=NSX[2].MAX_THDV2N_P,lo:=4776,hi:=4777);
Read_Real(rVar:=NSX[2].MAX_THDV31_P,lo:=4778,hi:=4779);
Read_Real(rVar:=NSX[2].MAX_THDV3N_P,lo:=4780,hi:=4781);
Read_Real(rVar:=NSX[2].MAX_VoltageAvgPhToN_V,lo:=4782,hi:=4783);
Read_Real(rVar:=NSX[2].MAX_VoltageAvgPhToPh_V,lo:=4784,hi:=4785);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV12_P,lo:=4786,hi:=4787);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV1N_P,lo:=4788,hi:=4789);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV23_P,lo:=4790,hi:=4791);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV2N_P,lo:=4792,hi:=4793);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV31_P,lo:=4794,hi:=4795);
Read_Real(rVar:=NSX[2].MAX_VoltageUnbV3N_P,lo:=4796,hi:=4797);
Read_Real(rVar:=NSX[2].MAX_VoltageV12_V,lo:=4798,hi:=4799);
Read_Real(rVar:=NSX[2].MAX_VoltageV1N_V,lo:=4800,hi:=4801);
Read_Real(rVar:=NSX[2].MAX_VoltageV23_V,lo:=4802,hi:=4803);
Read_Real(rVar:=NSX[2].MAX_VoltageV2N_V,lo:=4804,hi:=4805);
Read_Real(rVar:=NSX[2].MAX_VoltageV31_V,lo:=4806,hi:=4807);
Read_Real(rVar:=NSX[2].MAX_VoltageV3N_V,lo:=4808,hi:=4809);
Read_Real(rVar:=NSX[2].MIN_ActivePowerL1_kW,lo:=4810,hi:=4811);
Read_Real(rVar:=NSX[2].MIN_ActivePowerL2_kW,lo:=4812,hi:=4813);
Read_Real(rVar:=NSX[2].MIN_ActivePowerL3_kW,lo:=4814,hi:=4815);
Read_Real(rVar:=NSX[2].MIN_ActivePowerTotal_kW,lo:=4816,hi:=4817);
Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL1_kVA,lo:=4818,hi:=4819);
Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL2_kVA,lo:=4820,hi:=4821);
Read_Real(rVar:=NSX[2].MIN_ApparetnPowerL3_kVA,lo:=4822,hi:=4823);
Read_Real(rVar:=NSX[2].MIN_ApparetnPowerTotal_kVA,lo:=4824,hi:=4825);
Read_Real(rVar:=NSX[2].MIN_CosFL1,lo:=4826,hi:=4827);
Read_Real(rVar:=NSX[2].MIN_CosFL2,lo:=4828,hi:=4829);
Read_Real(rVar:=NSX[2].MIN_CosFL3,lo:=4830,hi:=4831);
Read_Real(rVar:=NSX[2].MIN_CosFTotal,lo:=4832,hi:=4833);
Read_Real(rVar:=NSX[2].MIN_CurrentAvgI1I2I3_A,lo:=4834,hi:=4835);
Read_Real(rVar:=NSX[2].MIN_CurrentL1_A,lo:=4836,hi:=4837);
Read_Real(rVar:=NSX[2].MIN_CurrentL2_A,lo:=4838,hi:=4839);
Read_Real(rVar:=NSX[2].MIN_CurrentL3_A,lo:=4840,hi:=4841);
Read_Real(rVar:=NSX[2].MIN_CurrentMaxL1L2L3N_A,lo:=4842,hi:=4843);
Read_Real(rVar:=NSX[2].MIN_CurrentN_A,lo:=4844,hi:=4845);
Read_Real(rVar:=NSX[2].MIN_DistortionPowerL1_kVAr,lo:=4846,hi:=4847);
Read_Real(rVar:=NSX[2].MIN_DistortionPowerL2_kVAr,lo:=4848,hi:=4849);
Read_Real(rVar:=NSX[2].MIN_DistortionPowerL3_kVAr,lo:=4850,hi:=4851);
Read_Real(rVar:=NSX[2].MIN_DistortionPowerTotal_kVAr,lo:=4852,hi:=4853);
Read_Real(rVar:=NSX[2].MIN_Frequency_Hz,lo:=4854,hi:=4855);
Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL1_kVAr,lo:=4856,hi:=4857);
Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL2_kVAr,lo:=4858,hi:=4859);
Read_Real(rVar:=NSX[2].MIN_FunReactivePowerL3_kVAr,lo:=4860,hi:=4861);
Read_Real(rVar:=NSX[2].MIN_FunReactivePowerTotal_kVAr,lo:=4862,hi:=4863);
Read_Real(rVar:=NSX[2].MIN_PowerFactorL1,lo:=4864,hi:=4865);
Read_Real(rVar:=NSX[2].MIN_PowerFactorL2,lo:=4866,hi:=4867);
Read_Real(rVar:=NSX[2].MIN_PowerFactorL3,lo:=4868,hi:=4869);
Read_Real(rVar:=NSX[2].MIN_PowerFactorTotal,lo:=4870,hi:=4871);
Read_Real(rVar:=NSX[2].MIN_ReactivePowerL1_kVAr,lo:=4872,hi:=4873);
Read_Real(rVar:=NSX[2].MIN_ReactivePowerL2_kVAr,lo:=4874,hi:=4875);
Read_Real(rVar:=NSX[2].MIN_ReactivePowerL3_kVAr,lo:=4876,hi:=4877);
Read_Real(rVar:=NSX[2].MIN_ReactivePowerTotal_kVAr,lo:=4878,hi:=4879);
Read_Real(rVar:=NSX[2].MIN_THDI1_P,lo:=4880,hi:=4881);
Read_Real(rVar:=NSX[2].MIN_THDI2_P,lo:=4882,hi:=4883);
Read_Real(rVar:=NSX[2].MIN_THDI3_P,lo:=4884,hi:=4885);
Read_Real(rVar:=NSX[2].MIN_THDV12_P,lo:=4886,hi:=4887);
Read_Real(rVar:=NSX[2].MIN_THDV1N_P,lo:=4888,hi:=4889);
Read_Real(rVar:=NSX[2].MIN_THDV23_P,lo:=4890,hi:=4891);
Read_Real(rVar:=NSX[2].MIN_THDV2N_P,lo:=4892,hi:=4893);
Read_Real(rVar:=NSX[2].MIN_THDV31_P,lo:=4894,hi:=4895);
Read_Real(rVar:=NSX[2].MIN_THDV3N_P,lo:=4896,hi:=4897);
Read_Real(rVar:=NSX[2].MIN_VoltageAvgPhToN_V,lo:=4898,hi:=4899);
Read_Real(rVar:=NSX[2].MIN_VoltageAvgPhToPh_V,lo:=4900,hi:=4901);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV12_P,lo:=4902,hi:=4903);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV1N_P,lo:=4904,hi:=4905);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV23_P,lo:=4906,hi:=4907);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV2N_P,lo:=4908,hi:=4909);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV31_P,lo:=4910,hi:=4911);
Read_Real(rVar:=NSX[2].MIN_VoltageUnbV3N_P,lo:=4912,hi:=4913);
Read_Real(rVar:=NSX[2].MIN_VoltageV12_V,lo:=4914,hi:=4915);
Read_Real(rVar:=NSX[2].MIN_VoltageV1N_V,lo:=4916,hi:=4917);
Read_Real(rVar:=NSX[2].MIN_VoltageV23_V,lo:=4918,hi:=4919);
Read_Real(rVar:=NSX[2].MIN_VoltageV2N_V,lo:=4920,hi:=4921);
Read_Real(rVar:=NSX[2].MIN_VoltageV31_V,lo:=4922,hi:=4923);
Read_Real(rVar:=NSX[2].MIN_VoltageV3N_V,lo:=4924,hi:=4925);
Read_Real(rVar:=NSX[2].PowerFactorL1,lo:=4926,hi:=4927);
Read_Real(rVar:=NSX[2].PowerFactorL2,lo:=4928,hi:=4929);
Read_Real(rVar:=NSX[2].PowerFactorL3,lo:=4930,hi:=4931);
Read_Real(rVar:=NSX[2].PowerFactorTotal,lo:=4932,hi:=4933);
Read_Real(rVar:=NSX[2].RazEner_D,lo:=4934,hi:=4935);
Read_Real(rVar:=NSX[2].RazEner_D_SCADA,lo:=4936,hi:=4937);
Read_Real(rVar:=NSX[2].RazEner_D_TEMP,lo:=4938,hi:=4939);
Read_Real(rVar:=NSX[2].RazEner_M,lo:=4940,hi:=4941);
Read_Real(rVar:=NSX[2].RazEner_M_SCADA,lo:=4942,hi:=4943);
Read_Real(rVar:=NSX[2].RazEner_M_TEMP,lo:=4944,hi:=4945);
Read_Real(rVar:=NSX[2].RazEner_T,lo:=4946,hi:=4947);
Read_Real(rVar:=NSX[2].RazEner_T_SCADA,lo:=4948,hi:=4949);
Read_Real(rVar:=NSX[2].RazEner_T_TEMP,lo:=4950,hi:=4951);
Read_Real(rVar:=NSX[2].ReactiveEnergy_kVArh,lo:=4952,hi:=4953);
Read_Real(rVar:=NSX[2].ReactiveNegativeEnergy_kVArh,lo:=4954,hi:=4955);
Read_Real(rVar:=NSX[2].ReactivePositiveEnergy_kVArh,lo:=4956,hi:=4957);
Read_Real(rVar:=NSX[2].ReactivePowerDemand_kVAr,lo:=4958,hi:=4959);
Read_Real(rVar:=NSX[2].ReactivePowerL1_kVAr,lo:=4960,hi:=4961);
Read_Real(rVar:=NSX[2].ReactivePowerL2_kVAr,lo:=4962,hi:=4963);
Read_Real(rVar:=NSX[2].ReactivePowerL3_kVAr,lo:=4964,hi:=4965);
Read_Real(rVar:=NSX[2].ReactivePowerMaxDemand_kVAr,lo:=4966,hi:=4967);
Read_Real(rVar:=NSX[2].ReactivePowerTotal_kVAr,lo:=4968,hi:=4969);
Read_Real(rVar:=NSX[2].THDI1_P,lo:=4970,hi:=4971);
Read_Real(rVar:=NSX[2].THDI2_P,lo:=4972,hi:=4973);
Read_Real(rVar:=NSX[2].THDI3_P,lo:=4974,hi:=4975);
Read_Real(rVar:=NSX[2].THDV12_P,lo:=4976,hi:=4977);
Read_Real(rVar:=NSX[2].THDV1N_P,lo:=4978,hi:=4979);
Read_Real(rVar:=NSX[2].THDV23_P,lo:=4980,hi:=4981);
Read_Real(rVar:=NSX[2].THDV2N_P,lo:=4982,hi:=4983);
Read_Real(rVar:=NSX[2].THDV31_P,lo:=4984,hi:=4985);
Read_Real(rVar:=NSX[2].THDV3N_P,lo:=4986,hi:=4987);
Read_Real(rVar:=NSX[2].VoltageAvgPhToN_V,lo:=4988,hi:=4989);
Read_Real(rVar:=NSX[2].VoltageAvgPhToPh_V,lo:=4990,hi:=4991);
Read_Real(rVar:=NSX[2].VoltageUnbV12_P,lo:=4992,hi:=4993);
Read_Real(rVar:=NSX[2].VoltageUnbV1N_P,lo:=4994,hi:=4995);
Read_Real(rVar:=NSX[2].VoltageUnbV23_P,lo:=4996,hi:=4997);
Read_Real(rVar:=NSX[2].VoltageUnbV2N_P,lo:=4998,hi:=4999);
Read_Real(rVar:=NSX[2].VoltageUnbV31_P,lo:=5000,hi:=5001);
Read_Real(rVar:=NSX[2].VoltageUnbV3N_P,lo:=5002,hi:=5003);
Read_Real(rVar:=NSX[2].VoltageV12_V,lo:=5004,hi:=5005);
Read_Real(rVar:=NSX[2].VoltageV1N_V,lo:=5006,hi:=5007);
Read_Real(rVar:=NSX[2].VoltageV23_V,lo:=5008,hi:=5009);
Read_Real(rVar:=NSX[2].VoltageV2N_V,lo:=5010,hi:=5011);
Read_Real(rVar:=NSX[2].VoltageV31_V,lo:=5012,hi:=5013);
Read_Real(rVar:=NSX[2].VoltageV3N_V,lo:=5014,hi:=5015);
Read_Real(rVar:=NSX[3].ActiveEnergy_kWh,lo:=5016,hi:=5017);
Read_Real(rVar:=NSX[3].ActiveNegativeEnergy_kWh,lo:=5018,hi:=5019);
Read_Real(rVar:=NSX[3].ActivePositiveEnergy_kWh,lo:=5020,hi:=5021);
Read_Real(rVar:=NSX[3].ActivePowerDemand_kW,lo:=5022,hi:=5023);
Read_Real(rVar:=NSX[3].ActivePowerL1_kW,lo:=5024,hi:=5025);
Read_Real(rVar:=NSX[3].ActivePowerL2_kW,lo:=5026,hi:=5027);
Read_Real(rVar:=NSX[3].ActivePowerL3_kW,lo:=5028,hi:=5029);
Read_Real(rVar:=NSX[3].ActivePowerMaxDemand_kW,lo:=5030,hi:=5031);
Read_Real(rVar:=NSX[3].ActivePowerTotal_kW,lo:=5032,hi:=5033);
Read_Real(rVar:=NSX[3].ApparentEnergy_kVAh,lo:=5034,hi:=5035);
Read_Real(rVar:=NSX[3].ApparentPowerDemand_kVA,lo:=5036,hi:=5037);
Read_Real(rVar:=NSX[3].ApparentPowerMaxDemand_kVA,lo:=5038,hi:=5039);
Read_Real(rVar:=NSX[3].ApparetnPowerL1_kVA,lo:=5040,hi:=5041);
Read_Real(rVar:=NSX[3].ApparetnPowerL2_kVA,lo:=5042,hi:=5043);
Read_Real(rVar:=NSX[3].ApparetnPowerL3_kVA,lo:=5044,hi:=5045);
Read_Real(rVar:=NSX[3].ApparetnPowerTotal_kVA,lo:=5046,hi:=5047);
Read_Real(rVar:=NSX[3].CosFL1,lo:=5048,hi:=5049);
Read_Real(rVar:=NSX[3].CosFL2,lo:=5050,hi:=5051);
Read_Real(rVar:=NSX[3].CosFL3,lo:=5052,hi:=5053);
Read_Real(rVar:=NSX[3].CosFTotal,lo:=5054,hi:=5055);
Read_Real(rVar:=NSX[3].CumulNegativeActiveEnergy_kWh,lo:=5056,hi:=5057);
Read_Real(rVar:=NSX[3].CumulPositiveActiveEnergy_kWh,lo:=5058,hi:=5059);
Read_Real(rVar:=NSX[3].CurrentAvgI1I2I3_A,lo:=5060,hi:=5061);
Read_Real(rVar:=NSX[3].CurrentDemandL1_A,lo:=5062,hi:=5063);
Read_Real(rVar:=NSX[3].CurrentDemandL2_A,lo:=5064,hi:=5065);
Read_Real(rVar:=NSX[3].CurrentDemandL3_A,lo:=5066,hi:=5067);
Read_Real(rVar:=NSX[3].CurrentDemandMaxL1_A,lo:=5068,hi:=5069);
Read_Real(rVar:=NSX[3].CurrentDemandMaxL2_A,lo:=5070,hi:=5071);
Read_Real(rVar:=NSX[3].CurrentDemandMaxL3_A,lo:=5072,hi:=5073);
Read_Real(rVar:=NSX[3].CurrentDemandMaxN_A,lo:=5074,hi:=5075);
Read_Real(rVar:=NSX[3].CurrentDemandN_A,lo:=5076,hi:=5077);
Read_Real(rVar:=NSX[3].CurrentL1_A,lo:=5078,hi:=5079);
Read_Real(rVar:=NSX[3].CurrentL2_A,lo:=5080,hi:=5081);
Read_Real(rVar:=NSX[3].CurrentL3_A,lo:=5082,hi:=5083);
Read_Real(rVar:=NSX[3].CurrentN_A,lo:=5084,hi:=5085);
Read_Real(rVar:=NSX[3].CurrentUnbI1_P,lo:=5086,hi:=5087);
Read_Real(rVar:=NSX[3].CurrentUnbI2_P,lo:=5088,hi:=5089);
Read_Real(rVar:=NSX[3].CurrentUnbI3_P,lo:=5090,hi:=5091);
Read_Real(rVar:=NSX[3].CurrentUnbN_P,lo:=5092,hi:=5093);
Read_Real(rVar:=NSX[3].DelovnaEnergija_TEMP,lo:=5094,hi:=5095);
Read_Real(rVar:=NSX[3].DistortionPowerL1_kVAr,lo:=5096,hi:=5097);
Read_Real(rVar:=NSX[3].DistortionPowerL2_kVAr,lo:=5098,hi:=5099);
Read_Real(rVar:=NSX[3].DistortionPowerL3_kVAr,lo:=5100,hi:=5101);
Read_Real(rVar:=NSX[3].DistortionPowerTotal_kVAr,lo:=5102,hi:=5103);
Read_Real(rVar:=NSX[3].Frequency_Hz,lo:=5104,hi:=5105);
Read_Real(rVar:=NSX[3].FunReactivePowerL1_kVAr,lo:=5106,hi:=5107);
Read_Real(rVar:=NSX[3].FunReactivePowerL2_kVAr,lo:=5108,hi:=5109);
Read_Real(rVar:=NSX[3].FunReactivePowerL3_kVAr,lo:=5110,hi:=5111);
Read_Real(rVar:=NSX[3].FunReactivePowerTotal_kVAr,lo:=5112,hi:=5113);
Read_Real(rVar:=NSX[3].MAX_ActivePowerL1_kW,lo:=5114,hi:=5115);
Read_Real(rVar:=NSX[3].MAX_ActivePowerL2_kW,lo:=5116,hi:=5117);
Read_Real(rVar:=NSX[3].MAX_ActivePowerL3_kW,lo:=5118,hi:=5119);
Read_Real(rVar:=NSX[3].MAX_ActivePowerTotal_kW,lo:=5120,hi:=5121);
Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL1_kVA,lo:=5122,hi:=5123);
Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL2_kVA,lo:=5124,hi:=5125);
Read_Real(rVar:=NSX[3].MAX_ApparetnPowerL3_kVA,lo:=5126,hi:=5127);
Read_Real(rVar:=NSX[3].MAX_ApparetnPowerTotal_kVA,lo:=5128,hi:=5129);
Read_Real(rVar:=NSX[3].MAX_CosFL1,lo:=5130,hi:=5131);
Read_Real(rVar:=NSX[3].MAX_CosFL2,lo:=5132,hi:=5133);
Read_Real(rVar:=NSX[3].MAX_CosFL3,lo:=5134,hi:=5135);
Read_Real(rVar:=NSX[3].MAX_CosFTotal,lo:=5136,hi:=5137);
Read_Real(rVar:=NSX[3].MAX_CurrentAvgI1I2I3_A,lo:=5138,hi:=5139);
Read_Real(rVar:=NSX[3].MAX_CurrentL1_A,lo:=5140,hi:=5141);
Read_Real(rVar:=NSX[3].MAX_CurrentL2_A,lo:=5142,hi:=5143);
Read_Real(rVar:=NSX[3].MAX_CurrentL3_A,lo:=5144,hi:=5145);
Read_Real(rVar:=NSX[3].MAX_CurrentMaxL1L2L3N_A,lo:=5146,hi:=5147);
Read_Real(rVar:=NSX[3].MAX_CurrentN_A,lo:=5148,hi:=5149);
Read_Real(rVar:=NSX[3].MAX_DistortionPowerL1_kVAr,lo:=5150,hi:=5151);
Read_Real(rVar:=NSX[3].MAX_DistortionPowerL2_kVAr,lo:=5152,hi:=5153);
Read_Real(rVar:=NSX[3].MAX_DistortionPowerL3_kVAr,lo:=5154,hi:=5155);
Read_Real(rVar:=NSX[3].MAX_DistortionPowerTotal_kVAr,lo:=5156,hi:=5157);
Read_Real(rVar:=NSX[3].MAX_Frequency_Hz,lo:=5158,hi:=5159);
Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL1_kVAr,lo:=5160,hi:=5161);
Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL2_kVAr,lo:=5162,hi:=5163);
Read_Real(rVar:=NSX[3].MAX_FunReactivePowerL3_kVAr,lo:=5164,hi:=5165);
Read_Real(rVar:=NSX[3].MAX_FunReactivePowerTotal_kVAr,lo:=5166,hi:=5167);
Read_Real(rVar:=NSX[3].MAX_PowerFactorL1,lo:=5168,hi:=5169);
Read_Real(rVar:=NSX[3].MAX_PowerFactorL2,lo:=5170,hi:=5171);
Read_Real(rVar:=NSX[3].MAX_PowerFactorL3,lo:=5172,hi:=5173);
Read_Real(rVar:=NSX[3].MAX_PowerFactorTotal,lo:=5174,hi:=5175);
Read_Real(rVar:=NSX[3].MAX_ReactivePowerL1_kVAr,lo:=5176,hi:=5177);
Read_Real(rVar:=NSX[3].MAX_ReactivePowerL2_kVAr,lo:=5178,hi:=5179);
Read_Real(rVar:=NSX[3].MAX_ReactivePowerL3_kVAr,lo:=5180,hi:=5181);
Read_Real(rVar:=NSX[3].MAX_ReactivePowerTotal_kVAr,lo:=5182,hi:=5183);
Read_Real(rVar:=NSX[3].MAX_THDI1_P,lo:=5184,hi:=5185);
Read_Real(rVar:=NSX[3].MAX_THDI2_P,lo:=5186,hi:=5187);
Read_Real(rVar:=NSX[3].MAX_THDI3_P,lo:=5188,hi:=5189);
Read_Real(rVar:=NSX[3].MAX_THDV12_P,lo:=5190,hi:=5191);
Read_Real(rVar:=NSX[3].MAX_THDV1N_P,lo:=5192,hi:=5193);
Read_Real(rVar:=NSX[3].MAX_THDV23_P,lo:=5194,hi:=5195);
Read_Real(rVar:=NSX[3].MAX_THDV2N_P,lo:=5196,hi:=5197);
Read_Real(rVar:=NSX[3].MAX_THDV31_P,lo:=5198,hi:=5199);
Read_Real(rVar:=NSX[3].MAX_THDV3N_P,lo:=5200,hi:=5201);
Read_Real(rVar:=NSX[3].MAX_VoltageAvgPhToN_V,lo:=5202,hi:=5203);
Read_Real(rVar:=NSX[3].MAX_VoltageAvgPhToPh_V,lo:=5204,hi:=5205);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV12_P,lo:=5206,hi:=5207);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV1N_P,lo:=5208,hi:=5209);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV23_P,lo:=5210,hi:=5211);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV2N_P,lo:=5212,hi:=5213);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV31_P,lo:=5214,hi:=5215);
Read_Real(rVar:=NSX[3].MAX_VoltageUnbV3N_P,lo:=5216,hi:=5217);
Read_Real(rVar:=NSX[3].MAX_VoltageV12_V,lo:=5218,hi:=5219);
Read_Real(rVar:=NSX[3].MAX_VoltageV1N_V,lo:=5220,hi:=5221);
Read_Real(rVar:=NSX[3].MAX_VoltageV23_V,lo:=5222,hi:=5223);
Read_Real(rVar:=NSX[3].MAX_VoltageV2N_V,lo:=5224,hi:=5225);
Read_Real(rVar:=NSX[3].MAX_VoltageV31_V,lo:=5226,hi:=5227);
Read_Real(rVar:=NSX[3].MAX_VoltageV3N_V,lo:=5228,hi:=5229);
Read_Real(rVar:=NSX[3].MIN_ActivePowerL1_kW,lo:=5230,hi:=5231);
Read_Real(rVar:=NSX[3].MIN_ActivePowerL2_kW,lo:=5232,hi:=5233);
Read_Real(rVar:=NSX[3].MIN_ActivePowerL3_kW,lo:=5234,hi:=5235);
Read_Real(rVar:=NSX[3].MIN_ActivePowerTotal_kW,lo:=5236,hi:=5237);
Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL1_kVA,lo:=5238,hi:=5239);
Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL2_kVA,lo:=5240,hi:=5241);
Read_Real(rVar:=NSX[3].MIN_ApparetnPowerL3_kVA,lo:=5242,hi:=5243);
Read_Real(rVar:=NSX[3].MIN_ApparetnPowerTotal_kVA,lo:=5244,hi:=5245);
Read_Real(rVar:=NSX[3].MIN_CosFL1,lo:=5246,hi:=5247);
Read_Real(rVar:=NSX[3].MIN_CosFL2,lo:=5248,hi:=5249);
Read_Real(rVar:=NSX[3].MIN_CosFL3,lo:=5250,hi:=5251);
Read_Real(rVar:=NSX[3].MIN_CosFTotal,lo:=5252,hi:=5253);
Read_Real(rVar:=NSX[3].MIN_CurrentAvgI1I2I3_A,lo:=5254,hi:=5255);
Read_Real(rVar:=NSX[3].MIN_CurrentL1_A,lo:=5256,hi:=5257);
Read_Real(rVar:=NSX[3].MIN_CurrentL2_A,lo:=5258,hi:=5259);
Read_Real(rVar:=NSX[3].MIN_CurrentL3_A,lo:=5260,hi:=5261);
Read_Real(rVar:=NSX[3].MIN_CurrentMaxL1L2L3N_A,lo:=5262,hi:=5263);
Read_Real(rVar:=NSX[3].MIN_CurrentN_A,lo:=5264,hi:=5265);
Read_Real(rVar:=NSX[3].MIN_DistortionPowerL1_kVAr,lo:=5266,hi:=5267);
Read_Real(rVar:=NSX[3].MIN_DistortionPowerL2_kVAr,lo:=5268,hi:=5269);
Read_Real(rVar:=NSX[3].MIN_DistortionPowerL3_kVAr,lo:=5270,hi:=5271);
Read_Real(rVar:=NSX[3].MIN_DistortionPowerTotal_kVAr,lo:=5272,hi:=5273);
Read_Real(rVar:=NSX[3].MIN_Frequency_Hz,lo:=5274,hi:=5275);
Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL1_kVAr,lo:=5276,hi:=5277);
Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL2_kVAr,lo:=5278,hi:=5279);
Read_Real(rVar:=NSX[3].MIN_FunReactivePowerL3_kVAr,lo:=5280,hi:=5281);
Read_Real(rVar:=NSX[3].MIN_FunReactivePowerTotal_kVAr,lo:=5282,hi:=5283);
Read_Real(rVar:=NSX[3].MIN_PowerFactorL1,lo:=5284,hi:=5285);
Read_Real(rVar:=NSX[3].MIN_PowerFactorL2,lo:=5286,hi:=5287);
Read_Real(rVar:=NSX[3].MIN_PowerFactorL3,lo:=5288,hi:=5289);
Read_Real(rVar:=NSX[3].MIN_PowerFactorTotal,lo:=5290,hi:=5291);
Read_Real(rVar:=NSX[3].MIN_ReactivePowerL1_kVAr,lo:=5292,hi:=5293);
Read_Real(rVar:=NSX[3].MIN_ReactivePowerL2_kVAr,lo:=5294,hi:=5295);
Read_Real(rVar:=NSX[3].MIN_ReactivePowerL3_kVAr,lo:=5296,hi:=5297);
Read_Real(rVar:=NSX[3].MIN_ReactivePowerTotal_kVAr,lo:=5298,hi:=5299);
Read_Real(rVar:=NSX[3].MIN_THDI1_P,lo:=5300,hi:=5301);
Read_Real(rVar:=NSX[3].MIN_THDI2_P,lo:=5302,hi:=5303);
Read_Real(rVar:=NSX[3].MIN_THDI3_P,lo:=5304,hi:=5305);
Read_Real(rVar:=NSX[3].MIN_THDV12_P,lo:=5306,hi:=5307);
Read_Real(rVar:=NSX[3].MIN_THDV1N_P,lo:=5308,hi:=5309);
Read_Real(rVar:=NSX[3].MIN_THDV23_P,lo:=5310,hi:=5311);
Read_Real(rVar:=NSX[3].MIN_THDV2N_P,lo:=5312,hi:=5313);
Read_Real(rVar:=NSX[3].MIN_THDV31_P,lo:=5314,hi:=5315);
Read_Real(rVar:=NSX[3].MIN_THDV3N_P,lo:=5316,hi:=5317);
Read_Real(rVar:=NSX[3].MIN_VoltageAvgPhToN_V,lo:=5318,hi:=5319);
Read_Real(rVar:=NSX[3].MIN_VoltageAvgPhToPh_V,lo:=5320,hi:=5321);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV12_P,lo:=5322,hi:=5323);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV1N_P,lo:=5324,hi:=5325);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV23_P,lo:=5326,hi:=5327);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV2N_P,lo:=5328,hi:=5329);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV31_P,lo:=5330,hi:=5331);
Read_Real(rVar:=NSX[3].MIN_VoltageUnbV3N_P,lo:=5332,hi:=5333);
Read_Real(rVar:=NSX[3].MIN_VoltageV12_V,lo:=5334,hi:=5335);
Read_Real(rVar:=NSX[3].MIN_VoltageV1N_V,lo:=5336,hi:=5337);
Read_Real(rVar:=NSX[3].MIN_VoltageV23_V,lo:=5338,hi:=5339);
Read_Real(rVar:=NSX[3].MIN_VoltageV2N_V,lo:=5340,hi:=5341);
Read_Real(rVar:=NSX[3].MIN_VoltageV31_V,lo:=5342,hi:=5343);
Read_Real(rVar:=NSX[3].MIN_VoltageV3N_V,lo:=5344,hi:=5345);
Read_Real(rVar:=NSX[3].PowerFactorL1,lo:=5346,hi:=5347);
Read_Real(rVar:=NSX[3].PowerFactorL2,lo:=5348,hi:=5349);
Read_Real(rVar:=NSX[3].PowerFactorL3,lo:=5350,hi:=5351);
Read_Real(rVar:=NSX[3].PowerFactorTotal,lo:=5352,hi:=5353);
Read_Real(rVar:=NSX[3].RazEner_D,lo:=5354,hi:=5355);
Read_Real(rVar:=NSX[3].RazEner_D_SCADA,lo:=5356,hi:=5357);
Read_Real(rVar:=NSX[3].RazEner_D_TEMP,lo:=5358,hi:=5359);
Read_Real(rVar:=NSX[3].RazEner_M,lo:=5360,hi:=5361);
Read_Real(rVar:=NSX[3].RazEner_M_SCADA,lo:=5362,hi:=5363);
Read_Real(rVar:=NSX[3].RazEner_M_TEMP,lo:=5364,hi:=5365);
Read_Real(rVar:=NSX[3].RazEner_T,lo:=5366,hi:=5367);
Read_Real(rVar:=NSX[3].RazEner_T_SCADA,lo:=5368,hi:=5369);
Read_Real(rVar:=NSX[3].RazEner_T_TEMP,lo:=5370,hi:=5371);
Read_Real(rVar:=NSX[3].ReactiveEnergy_kVArh,lo:=5372,hi:=5373);
Read_Real(rVar:=NSX[3].ReactiveNegativeEnergy_kVArh,lo:=5374,hi:=5375);
Read_Real(rVar:=NSX[3].ReactivePositiveEnergy_kVArh,lo:=5376,hi:=5377);
Read_Real(rVar:=NSX[3].ReactivePowerDemand_kVAr,lo:=5378,hi:=5379);
Read_Real(rVar:=NSX[3].ReactivePowerL1_kVAr,lo:=5380,hi:=5381);
Read_Real(rVar:=NSX[3].ReactivePowerL2_kVAr,lo:=5382,hi:=5383);
Read_Real(rVar:=NSX[3].ReactivePowerL3_kVAr,lo:=5384,hi:=5385);
Read_Real(rVar:=NSX[3].ReactivePowerMaxDemand_kVAr,lo:=5386,hi:=5387);
Read_Real(rVar:=NSX[3].ReactivePowerTotal_kVAr,lo:=5388,hi:=5389);
Read_Real(rVar:=NSX[3].THDI1_P,lo:=5390,hi:=5391);
Read_Real(rVar:=NSX[3].THDI2_P,lo:=5392,hi:=5393);
Read_Real(rVar:=NSX[3].THDI3_P,lo:=5394,hi:=5395);
Read_Real(rVar:=NSX[3].THDV12_P,lo:=5396,hi:=5397);
Read_Real(rVar:=NSX[3].THDV1N_P,lo:=5398,hi:=5399);
Read_Real(rVar:=NSX[3].THDV23_P,lo:=5400,hi:=5401);
Read_Real(rVar:=NSX[3].THDV2N_P,lo:=5402,hi:=5403);
Read_Real(rVar:=NSX[3].THDV31_P,lo:=5404,hi:=5405);
Read_Real(rVar:=NSX[3].THDV3N_P,lo:=5406,hi:=5407);
Read_Real(rVar:=NSX[3].VoltageAvgPhToN_V,lo:=5408,hi:=5409);
Read_Real(rVar:=NSX[3].VoltageAvgPhToPh_V,lo:=5410,hi:=5411);
Read_Real(rVar:=NSX[3].VoltageUnbV12_P,lo:=5412,hi:=5413);
Read_Real(rVar:=NSX[3].VoltageUnbV1N_P,lo:=5414,hi:=5415);
Read_Real(rVar:=NSX[3].VoltageUnbV23_P,lo:=5416,hi:=5417);
Read_Real(rVar:=NSX[3].VoltageUnbV2N_P,lo:=5418,hi:=5419);
Read_Real(rVar:=NSX[3].VoltageUnbV31_P,lo:=5420,hi:=5421);
Read_Real(rVar:=NSX[3].VoltageUnbV3N_P,lo:=5422,hi:=5423);
Read_Real(rVar:=NSX[3].VoltageV12_V,lo:=5424,hi:=5425);
Read_Real(rVar:=NSX[3].VoltageV1N_V,lo:=5426,hi:=5427);
Read_Real(rVar:=NSX[3].VoltageV23_V,lo:=5428,hi:=5429);
Read_Real(rVar:=NSX[3].VoltageV2N_V,lo:=5430,hi:=5431);
Read_Real(rVar:=NSX[3].VoltageV31_V,lo:=5432,hi:=5433);
Read_Real(rVar:=NSX[3].VoltageV3N_V,lo:=5434,hi:=5435);
Read_Real(rVar:=NSX[4].ActiveEnergy_kWh,lo:=5436,hi:=5437);
Read_Real(rVar:=NSX[4].ActiveNegativeEnergy_kWh,lo:=5438,hi:=5439);
Read_Real(rVar:=NSX[4].ActivePositiveEnergy_kWh,lo:=5440,hi:=5441);
Read_Real(rVar:=NSX[4].ActivePowerDemand_kW,lo:=5442,hi:=5443);
Read_Real(rVar:=NSX[4].ActivePowerL1_kW,lo:=5444,hi:=5445);
Read_Real(rVar:=NSX[4].ActivePowerL2_kW,lo:=5446,hi:=5447);
Read_Real(rVar:=NSX[4].ActivePowerL3_kW,lo:=5448,hi:=5449);
Read_Real(rVar:=NSX[4].ActivePowerMaxDemand_kW,lo:=5450,hi:=5451);
Read_Real(rVar:=NSX[4].ActivePowerTotal_kW,lo:=5452,hi:=5453);
Read_Real(rVar:=NSX[4].ApparentEnergy_kVAh,lo:=5454,hi:=5455);
Read_Real(rVar:=NSX[4].ApparentPowerDemand_kVA,lo:=5456,hi:=5457);
Read_Real(rVar:=NSX[4].ApparentPowerMaxDemand_kVA,lo:=5458,hi:=5459);
Read_Real(rVar:=NSX[4].ApparetnPowerL1_kVA,lo:=5460,hi:=5461);
Read_Real(rVar:=NSX[4].ApparetnPowerL2_kVA,lo:=5462,hi:=5463);
Read_Real(rVar:=NSX[4].ApparetnPowerL3_kVA,lo:=5464,hi:=5465);
Read_Real(rVar:=NSX[4].ApparetnPowerTotal_kVA,lo:=5466,hi:=5467);
Read_Real(rVar:=NSX[4].CosFL1,lo:=5468,hi:=5469);
Read_Real(rVar:=NSX[4].CosFL2,lo:=5470,hi:=5471);
Read_Real(rVar:=NSX[4].CosFL3,lo:=5472,hi:=5473);
Read_Real(rVar:=NSX[4].CosFTotal,lo:=5474,hi:=5475);
Read_Real(rVar:=NSX[4].CumulNegativeActiveEnergy_kWh,lo:=5476,hi:=5477);
Read_Real(rVar:=NSX[4].CumulPositiveActiveEnergy_kWh,lo:=5478,hi:=5479);
Read_Real(rVar:=NSX[4].CurrentAvgI1I2I3_A,lo:=5480,hi:=5481);
Read_Real(rVar:=NSX[4].CurrentDemandL1_A,lo:=5482,hi:=5483);
Read_Real(rVar:=NSX[4].CurrentDemandL2_A,lo:=5484,hi:=5485);
Read_Real(rVar:=NSX[4].CurrentDemandL3_A,lo:=5486,hi:=5487);
Read_Real(rVar:=NSX[4].CurrentDemandMaxL1_A,lo:=5488,hi:=5489);
Read_Real(rVar:=NSX[4].CurrentDemandMaxL2_A,lo:=5490,hi:=5491);
Read_Real(rVar:=NSX[4].CurrentDemandMaxL3_A,lo:=5492,hi:=5493);
Read_Real(rVar:=NSX[4].CurrentDemandMaxN_A,lo:=5494,hi:=5495);
Read_Real(rVar:=NSX[4].CurrentDemandN_A,lo:=5496,hi:=5497);
Read_Real(rVar:=NSX[4].CurrentL1_A,lo:=5498,hi:=5499);
Read_Real(rVar:=NSX[4].CurrentL2_A,lo:=5500,hi:=5501);
Read_Real(rVar:=NSX[4].CurrentL3_A,lo:=5502,hi:=5503);
Read_Real(rVar:=NSX[4].CurrentN_A,lo:=5504,hi:=5505);
Read_Real(rVar:=NSX[4].CurrentUnbI1_P,lo:=5506,hi:=5507);
Read_Real(rVar:=NSX[4].CurrentUnbI2_P,lo:=5508,hi:=5509);
Read_Real(rVar:=NSX[4].CurrentUnbI3_P,lo:=5510,hi:=5511);
Read_Real(rVar:=NSX[4].CurrentUnbN_P,lo:=5512,hi:=5513);
Read_Real(rVar:=NSX[4].DelovnaEnergija_TEMP,lo:=5514,hi:=5515);
Read_Real(rVar:=NSX[4].DistortionPowerL1_kVAr,lo:=5516,hi:=5517);
Read_Real(rVar:=NSX[4].DistortionPowerL2_kVAr,lo:=5518,hi:=5519);
Read_Real(rVar:=NSX[4].DistortionPowerL3_kVAr,lo:=5520,hi:=5521);
Read_Real(rVar:=NSX[4].DistortionPowerTotal_kVAr,lo:=5522,hi:=5523);
Read_Real(rVar:=NSX[4].Frequency_Hz,lo:=5524,hi:=5525);
Read_Real(rVar:=NSX[4].FunReactivePowerL1_kVAr,lo:=5526,hi:=5527);
Read_Real(rVar:=NSX[4].FunReactivePowerL2_kVAr,lo:=5528,hi:=5529);
Read_Real(rVar:=NSX[4].FunReactivePowerL3_kVAr,lo:=5530,hi:=5531);
Read_Real(rVar:=NSX[4].FunReactivePowerTotal_kVAr,lo:=5532,hi:=5533);
Read_Real(rVar:=NSX[4].MAX_ActivePowerL1_kW,lo:=5534,hi:=5535);
Read_Real(rVar:=NSX[4].MAX_ActivePowerL2_kW,lo:=5536,hi:=5537);
Read_Real(rVar:=NSX[4].MAX_ActivePowerL3_kW,lo:=5538,hi:=5539);
Read_Real(rVar:=NSX[4].MAX_ActivePowerTotal_kW,lo:=5540,hi:=5541);
Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL1_kVA,lo:=5542,hi:=5543);
Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL2_kVA,lo:=5544,hi:=5545);
Read_Real(rVar:=NSX[4].MAX_ApparetnPowerL3_kVA,lo:=5546,hi:=5547);
Read_Real(rVar:=NSX[4].MAX_ApparetnPowerTotal_kVA,lo:=5548,hi:=5549);
Read_Real(rVar:=NSX[4].MAX_CosFL1,lo:=5550,hi:=5551);
Read_Real(rVar:=NSX[4].MAX_CosFL2,lo:=5552,hi:=5553);
Read_Real(rVar:=NSX[4].MAX_CosFL3,lo:=5554,hi:=5555);
Read_Real(rVar:=NSX[4].MAX_CosFTotal,lo:=5556,hi:=5557);
Read_Real(rVar:=NSX[4].MAX_CurrentAvgI1I2I3_A,lo:=5558,hi:=5559);
Read_Real(rVar:=NSX[4].MAX_CurrentL1_A,lo:=5560,hi:=5561);
Read_Real(rVar:=NSX[4].MAX_CurrentL2_A,lo:=5562,hi:=5563);
Read_Real(rVar:=NSX[4].MAX_CurrentL3_A,lo:=5564,hi:=5565);
Read_Real(rVar:=NSX[4].MAX_CurrentMaxL1L2L3N_A,lo:=5566,hi:=5567);
Read_Real(rVar:=NSX[4].MAX_CurrentN_A,lo:=5568,hi:=5569);
Read_Real(rVar:=NSX[4].MAX_DistortionPowerL1_kVAr,lo:=5570,hi:=5571);
Read_Real(rVar:=NSX[4].MAX_DistortionPowerL2_kVAr,lo:=5572,hi:=5573);
Read_Real(rVar:=NSX[4].MAX_DistortionPowerL3_kVAr,lo:=5574,hi:=5575);
Read_Real(rVar:=NSX[4].MAX_DistortionPowerTotal_kVAr,lo:=5576,hi:=5577);
Read_Real(rVar:=NSX[4].MAX_Frequency_Hz,lo:=5578,hi:=5579);
Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL1_kVAr,lo:=5580,hi:=5581);
Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL2_kVAr,lo:=5582,hi:=5583);
Read_Real(rVar:=NSX[4].MAX_FunReactivePowerL3_kVAr,lo:=5584,hi:=5585);
Read_Real(rVar:=NSX[4].MAX_FunReactivePowerTotal_kVAr,lo:=5586,hi:=5587);
Read_Real(rVar:=NSX[4].MAX_PowerFactorL1,lo:=5588,hi:=5589);
Read_Real(rVar:=NSX[4].MAX_PowerFactorL2,lo:=5590,hi:=5591);
Read_Real(rVar:=NSX[4].MAX_PowerFactorL3,lo:=5592,hi:=5593);
Read_Real(rVar:=NSX[4].MAX_PowerFactorTotal,lo:=5594,hi:=5595);
Read_Real(rVar:=NSX[4].MAX_ReactivePowerL1_kVAr,lo:=5596,hi:=5597);
Read_Real(rVar:=NSX[4].MAX_ReactivePowerL2_kVAr,lo:=5598,hi:=5599);
Read_Real(rVar:=NSX[4].MAX_ReactivePowerL3_kVAr,lo:=5600,hi:=5601);
Read_Real(rVar:=NSX[4].MAX_ReactivePowerTotal_kVAr,lo:=5602,hi:=5603);
Read_Real(rVar:=NSX[4].MAX_THDI1_P,lo:=5604,hi:=5605);
Read_Real(rVar:=NSX[4].MAX_THDI2_P,lo:=5606,hi:=5607);
Read_Real(rVar:=NSX[4].MAX_THDI3_P,lo:=5608,hi:=5609);
Read_Real(rVar:=NSX[4].MAX_THDV12_P,lo:=5610,hi:=5611);
Read_Real(rVar:=NSX[4].MAX_THDV1N_P,lo:=5612,hi:=5613);
Read_Real(rVar:=NSX[4].MAX_THDV23_P,lo:=5614,hi:=5615);
Read_Real(rVar:=NSX[4].MAX_THDV2N_P,lo:=5616,hi:=5617);
Read_Real(rVar:=NSX[4].MAX_THDV31_P,lo:=5618,hi:=5619);
Read_Real(rVar:=NSX[4].MAX_THDV3N_P,lo:=5620,hi:=5621);
Read_Real(rVar:=NSX[4].MAX_VoltageAvgPhToN_V,lo:=5622,hi:=5623);
Read_Real(rVar:=NSX[4].MAX_VoltageAvgPhToPh_V,lo:=5624,hi:=5625);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV12_P,lo:=5626,hi:=5627);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV1N_P,lo:=5628,hi:=5629);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV23_P,lo:=5630,hi:=5631);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV2N_P,lo:=5632,hi:=5633);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV31_P,lo:=5634,hi:=5635);
Read_Real(rVar:=NSX[4].MAX_VoltageUnbV3N_P,lo:=5636,hi:=5637);
Read_Real(rVar:=NSX[4].MAX_VoltageV12_V,lo:=5638,hi:=5639);
Read_Real(rVar:=NSX[4].MAX_VoltageV1N_V,lo:=5640,hi:=5641);
Read_Real(rVar:=NSX[4].MAX_VoltageV23_V,lo:=5642,hi:=5643);
Read_Real(rVar:=NSX[4].MAX_VoltageV2N_V,lo:=5644,hi:=5645);
Read_Real(rVar:=NSX[4].MAX_VoltageV31_V,lo:=5646,hi:=5647);
Read_Real(rVar:=NSX[4].MAX_VoltageV3N_V,lo:=5648,hi:=5649);
Read_Real(rVar:=NSX[4].MIN_ActivePowerL1_kW,lo:=5650,hi:=5651);
Read_Real(rVar:=NSX[4].MIN_ActivePowerL2_kW,lo:=5652,hi:=5653);
Read_Real(rVar:=NSX[4].MIN_ActivePowerL3_kW,lo:=5654,hi:=5655);
Read_Real(rVar:=NSX[4].MIN_ActivePowerTotal_kW,lo:=5656,hi:=5657);
Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL1_kVA,lo:=5658,hi:=5659);
Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL2_kVA,lo:=5660,hi:=5661);
Read_Real(rVar:=NSX[4].MIN_ApparetnPowerL3_kVA,lo:=5662,hi:=5663);
Read_Real(rVar:=NSX[4].MIN_ApparetnPowerTotal_kVA,lo:=5664,hi:=5665);
Read_Real(rVar:=NSX[4].MIN_CosFL1,lo:=5666,hi:=5667);
Read_Real(rVar:=NSX[4].MIN_CosFL2,lo:=5668,hi:=5669);
Read_Real(rVar:=NSX[4].MIN_CosFL3,lo:=5670,hi:=5671);
Read_Real(rVar:=NSX[4].MIN_CosFTotal,lo:=5672,hi:=5673);
Read_Real(rVar:=NSX[4].MIN_CurrentAvgI1I2I3_A,lo:=5674,hi:=5675);
Read_Real(rVar:=NSX[4].MIN_CurrentL1_A,lo:=5676,hi:=5677);
Read_Real(rVar:=NSX[4].MIN_CurrentL2_A,lo:=5678,hi:=5679);
Read_Real(rVar:=NSX[4].MIN_CurrentL3_A,lo:=5680,hi:=5681);
Read_Real(rVar:=NSX[4].MIN_CurrentMaxL1L2L3N_A,lo:=5682,hi:=5683);
Read_Real(rVar:=NSX[4].MIN_CurrentN_A,lo:=5684,hi:=5685);
Read_Real(rVar:=NSX[4].MIN_DistortionPowerL1_kVAr,lo:=5686,hi:=5687);
Read_Real(rVar:=NSX[4].MIN_DistortionPowerL2_kVAr,lo:=5688,hi:=5689);
Read_Real(rVar:=NSX[4].MIN_DistortionPowerL3_kVAr,lo:=5690,hi:=5691);
Read_Real(rVar:=NSX[4].MIN_DistortionPowerTotal_kVAr,lo:=5692,hi:=5693);
Read_Real(rVar:=NSX[4].MIN_Frequency_Hz,lo:=5694,hi:=5695);
Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL1_kVAr,lo:=5696,hi:=5697);
Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL2_kVAr,lo:=5698,hi:=5699);
Read_Real(rVar:=NSX[4].MIN_FunReactivePowerL3_kVAr,lo:=5700,hi:=5701);
Read_Real(rVar:=NSX[4].MIN_FunReactivePowerTotal_kVAr,lo:=5702,hi:=5703);
Read_Real(rVar:=NSX[4].MIN_PowerFactorL1,lo:=5704,hi:=5705);
Read_Real(rVar:=NSX[4].MIN_PowerFactorL2,lo:=5706,hi:=5707);
Read_Real(rVar:=NSX[4].MIN_PowerFactorL3,lo:=5708,hi:=5709);
Read_Real(rVar:=NSX[4].MIN_PowerFactorTotal,lo:=5710,hi:=5711);
Read_Real(rVar:=NSX[4].MIN_ReactivePowerL1_kVAr,lo:=5712,hi:=5713);
Read_Real(rVar:=NSX[4].MIN_ReactivePowerL2_kVAr,lo:=5714,hi:=5715);
Read_Real(rVar:=NSX[4].MIN_ReactivePowerL3_kVAr,lo:=5716,hi:=5717);
Read_Real(rVar:=NSX[4].MIN_ReactivePowerTotal_kVAr,lo:=5718,hi:=5719);
Read_Real(rVar:=NSX[4].MIN_THDI1_P,lo:=5720,hi:=5721);
Read_Real(rVar:=NSX[4].MIN_THDI2_P,lo:=5722,hi:=5723);
Read_Real(rVar:=NSX[4].MIN_THDI3_P,lo:=5724,hi:=5725);
Read_Real(rVar:=NSX[4].MIN_THDV12_P,lo:=5726,hi:=5727);
Read_Real(rVar:=NSX[4].MIN_THDV1N_P,lo:=5728,hi:=5729);
Read_Real(rVar:=NSX[4].MIN_THDV23_P,lo:=5730,hi:=5731);
Read_Real(rVar:=NSX[4].MIN_THDV2N_P,lo:=5732,hi:=5733);
Read_Real(rVar:=NSX[4].MIN_THDV31_P,lo:=5734,hi:=5735);
Read_Real(rVar:=NSX[4].MIN_THDV3N_P,lo:=5736,hi:=5737);
Read_Real(rVar:=NSX[4].MIN_VoltageAvgPhToN_V,lo:=5738,hi:=5739);
Read_Real(rVar:=NSX[4].MIN_VoltageAvgPhToPh_V,lo:=5740,hi:=5741);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV12_P,lo:=5742,hi:=5743);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV1N_P,lo:=5744,hi:=5745);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV23_P,lo:=5746,hi:=5747);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV2N_P,lo:=5748,hi:=5749);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV31_P,lo:=5750,hi:=5751);
Read_Real(rVar:=NSX[4].MIN_VoltageUnbV3N_P,lo:=5752,hi:=5753);
Read_Real(rVar:=NSX[4].MIN_VoltageV12_V,lo:=5754,hi:=5755);
Read_Real(rVar:=NSX[4].MIN_VoltageV1N_V,lo:=5756,hi:=5757);
Read_Real(rVar:=NSX[4].MIN_VoltageV23_V,lo:=5758,hi:=5759);
Read_Real(rVar:=NSX[4].MIN_VoltageV2N_V,lo:=5760,hi:=5761);
Read_Real(rVar:=NSX[4].MIN_VoltageV31_V,lo:=5762,hi:=5763);
Read_Real(rVar:=NSX[4].MIN_VoltageV3N_V,lo:=5764,hi:=5765);
Read_Real(rVar:=NSX[4].PowerFactorL1,lo:=5766,hi:=5767);
Read_Real(rVar:=NSX[4].PowerFactorL2,lo:=5768,hi:=5769);
Read_Real(rVar:=NSX[4].PowerFactorL3,lo:=5770,hi:=5771);
Read_Real(rVar:=NSX[4].PowerFactorTotal,lo:=5772,hi:=5773);
Read_Real(rVar:=NSX[4].RazEner_D,lo:=5774,hi:=5775);
Read_Real(rVar:=NSX[4].RazEner_D_SCADA,lo:=5776,hi:=5777);
Read_Real(rVar:=NSX[4].RazEner_D_TEMP,lo:=5778,hi:=5779);
Read_Real(rVar:=NSX[4].RazEner_M,lo:=5780,hi:=5781);
Read_Real(rVar:=NSX[4].RazEner_M_SCADA,lo:=5782,hi:=5783);
Read_Real(rVar:=NSX[4].RazEner_M_TEMP,lo:=5784,hi:=5785);
Read_Real(rVar:=NSX[4].RazEner_T,lo:=5786,hi:=5787);
Read_Real(rVar:=NSX[4].RazEner_T_SCADA,lo:=5788,hi:=5789);
Read_Real(rVar:=NSX[4].RazEner_T_TEMP,lo:=5790,hi:=5791);
Read_Real(rVar:=NSX[4].ReactiveEnergy_kVArh,lo:=5792,hi:=5793);
Read_Real(rVar:=NSX[4].ReactiveNegativeEnergy_kVArh,lo:=5794,hi:=5795);
Read_Real(rVar:=NSX[4].ReactivePositiveEnergy_kVArh,lo:=5796,hi:=5797);
Read_Real(rVar:=NSX[4].ReactivePowerDemand_kVAr,lo:=5798,hi:=5799);
Read_Real(rVar:=NSX[4].ReactivePowerL1_kVAr,lo:=5800,hi:=5801);
Read_Real(rVar:=NSX[4].ReactivePowerL2_kVAr,lo:=5802,hi:=5803);
Read_Real(rVar:=NSX[4].ReactivePowerL3_kVAr,lo:=5804,hi:=5805);
Read_Real(rVar:=NSX[4].ReactivePowerMaxDemand_kVAr,lo:=5806,hi:=5807);
Read_Real(rVar:=NSX[4].ReactivePowerTotal_kVAr,lo:=5808,hi:=5809);
Read_Real(rVar:=NSX[4].THDI1_P,lo:=5810,hi:=5811);
Read_Real(rVar:=NSX[4].THDI2_P,lo:=5812,hi:=5813);
Read_Real(rVar:=NSX[4].THDI3_P,lo:=5814,hi:=5815);
Read_Real(rVar:=NSX[4].THDV12_P,lo:=5816,hi:=5817);
Read_Real(rVar:=NSX[4].THDV1N_P,lo:=5818,hi:=5819);
Read_Real(rVar:=NSX[4].THDV23_P,lo:=5820,hi:=5821);
Read_Real(rVar:=NSX[4].THDV2N_P,lo:=5822,hi:=5823);
Read_Real(rVar:=NSX[4].THDV31_P,lo:=5824,hi:=5825);
Read_Real(rVar:=NSX[4].THDV3N_P,lo:=5826,hi:=5827);
Read_Real(rVar:=NSX[4].VoltageAvgPhToN_V,lo:=5828,hi:=5829);
Read_Real(rVar:=NSX[4].VoltageAvgPhToPh_V,lo:=5830,hi:=5831);
Read_Real(rVar:=NSX[4].VoltageUnbV12_P,lo:=5832,hi:=5833);
Read_Real(rVar:=NSX[4].VoltageUnbV1N_P,lo:=5834,hi:=5835);
Read_Real(rVar:=NSX[4].VoltageUnbV23_P,lo:=5836,hi:=5837);
Read_Real(rVar:=NSX[4].VoltageUnbV2N_P,lo:=5838,hi:=5839);
Read_Real(rVar:=NSX[4].VoltageUnbV31_P,lo:=5840,hi:=5841);
Read_Real(rVar:=NSX[4].VoltageUnbV3N_P,lo:=5842,hi:=5843);
Read_Real(rVar:=NSX[4].VoltageV12_V,lo:=5844,hi:=5845);
Read_Real(rVar:=NSX[4].VoltageV1N_V,lo:=5846,hi:=5847);
Read_Real(rVar:=NSX[4].VoltageV23_V,lo:=5848,hi:=5849);
Read_Real(rVar:=NSX[4].VoltageV2N_V,lo:=5850,hi:=5851);
Read_Real(rVar:=NSX[4].VoltageV31_V,lo:=5852,hi:=5853);
Read_Real(rVar:=NSX[4].VoltageV3N_V,lo:=5854,hi:=5855);
Read_Real(rVar:=NSX[5].ActiveEnergy_kWh,lo:=5856,hi:=5857);
Read_Real(rVar:=NSX[5].ActiveNegativeEnergy_kWh,lo:=5858,hi:=5859);
Read_Real(rVar:=NSX[5].ActivePositiveEnergy_kWh,lo:=5860,hi:=5861);
Read_Real(rVar:=NSX[5].ActivePowerDemand_kW,lo:=5862,hi:=5863);
Read_Real(rVar:=NSX[5].ActivePowerL1_kW,lo:=5864,hi:=5865);
Read_Real(rVar:=NSX[5].ActivePowerL2_kW,lo:=5866,hi:=5867);
Read_Real(rVar:=NSX[5].ActivePowerL3_kW,lo:=5868,hi:=5869);
Read_Real(rVar:=NSX[5].ActivePowerMaxDemand_kW,lo:=5870,hi:=5871);
Read_Real(rVar:=NSX[5].ActivePowerTotal_kW,lo:=5872,hi:=5873);
Read_Real(rVar:=NSX[5].ApparentEnergy_kVAh,lo:=5874,hi:=5875);
Read_Real(rVar:=NSX[5].ApparentPowerDemand_kVA,lo:=5876,hi:=5877);
Read_Real(rVar:=NSX[5].ApparentPowerMaxDemand_kVA,lo:=5878,hi:=5879);
Read_Real(rVar:=NSX[5].ApparetnPowerL1_kVA,lo:=5880,hi:=5881);
Read_Real(rVar:=NSX[5].ApparetnPowerL2_kVA,lo:=5882,hi:=5883);
Read_Real(rVar:=NSX[5].ApparetnPowerL3_kVA,lo:=5884,hi:=5885);
Read_Real(rVar:=NSX[5].ApparetnPowerTotal_kVA,lo:=5886,hi:=5887);
Read_Real(rVar:=NSX[5].CosFL1,lo:=5888,hi:=5889);
Read_Real(rVar:=NSX[5].CosFL2,lo:=5890,hi:=5891);
Read_Real(rVar:=NSX[5].CosFL3,lo:=5892,hi:=5893);
Read_Real(rVar:=NSX[5].CosFTotal,lo:=5894,hi:=5895);
Read_Real(rVar:=NSX[5].CumulNegativeActiveEnergy_kWh,lo:=5896,hi:=5897);
Read_Real(rVar:=NSX[5].CumulPositiveActiveEnergy_kWh,lo:=5898,hi:=5899);
Read_Real(rVar:=NSX[5].CurrentAvgI1I2I3_A,lo:=5900,hi:=5901);
Read_Real(rVar:=NSX[5].CurrentDemandL1_A,lo:=5902,hi:=5903);
Read_Real(rVar:=NSX[5].CurrentDemandL2_A,lo:=5904,hi:=5905);
Read_Real(rVar:=NSX[5].CurrentDemandL3_A,lo:=5906,hi:=5907);
Read_Real(rVar:=NSX[5].CurrentDemandMaxL1_A,lo:=5908,hi:=5909);
Read_Real(rVar:=NSX[5].CurrentDemandMaxL2_A,lo:=5910,hi:=5911);
Read_Real(rVar:=NSX[5].CurrentDemandMaxL3_A,lo:=5912,hi:=5913);
Read_Real(rVar:=NSX[5].CurrentDemandMaxN_A,lo:=5914,hi:=5915);
Read_Real(rVar:=NSX[5].CurrentDemandN_A,lo:=5916,hi:=5917);
Read_Real(rVar:=NSX[5].CurrentL1_A,lo:=5918,hi:=5919);
Read_Real(rVar:=NSX[5].CurrentL2_A,lo:=5920,hi:=5921);
Read_Real(rVar:=NSX[5].CurrentL3_A,lo:=5922,hi:=5923);
Read_Real(rVar:=NSX[5].CurrentN_A,lo:=5924,hi:=5925);
Read_Real(rVar:=NSX[5].CurrentUnbI1_P,lo:=5926,hi:=5927);
Read_Real(rVar:=NSX[5].CurrentUnbI2_P,lo:=5928,hi:=5929);
Read_Real(rVar:=NSX[5].CurrentUnbI3_P,lo:=5930,hi:=5931);
Read_Real(rVar:=NSX[5].CurrentUnbN_P,lo:=5932,hi:=5933);
Read_Real(rVar:=NSX[5].DelovnaEnergija_TEMP,lo:=5934,hi:=5935);
Read_Real(rVar:=NSX[5].DistortionPowerL1_kVAr,lo:=5936,hi:=5937);
Read_Real(rVar:=NSX[5].DistortionPowerL2_kVAr,lo:=5938,hi:=5939);
Read_Real(rVar:=NSX[5].DistortionPowerL3_kVAr,lo:=5940,hi:=5941);
Read_Real(rVar:=NSX[5].DistortionPowerTotal_kVAr,lo:=5942,hi:=5943);
Read_Real(rVar:=NSX[5].Frequency_Hz,lo:=5944,hi:=5945);
Read_Real(rVar:=NSX[5].FunReactivePowerL1_kVAr,lo:=5946,hi:=5947);
Read_Real(rVar:=NSX[5].FunReactivePowerL2_kVAr,lo:=5948,hi:=5949);
Read_Real(rVar:=NSX[5].FunReactivePowerL3_kVAr,lo:=5950,hi:=5951);
Read_Real(rVar:=NSX[5].FunReactivePowerTotal_kVAr,lo:=5952,hi:=5953);
Read_Real(rVar:=NSX[5].MAX_ActivePowerL1_kW,lo:=5954,hi:=5955);
Read_Real(rVar:=NSX[5].MAX_ActivePowerL2_kW,lo:=5956,hi:=5957);
Read_Real(rVar:=NSX[5].MAX_ActivePowerL3_kW,lo:=5958,hi:=5959);
Read_Real(rVar:=NSX[5].MAX_ActivePowerTotal_kW,lo:=5960,hi:=5961);
Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL1_kVA,lo:=5962,hi:=5963);
Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL2_kVA,lo:=5964,hi:=5965);
Read_Real(rVar:=NSX[5].MAX_ApparetnPowerL3_kVA,lo:=5966,hi:=5967);
Read_Real(rVar:=NSX[5].MAX_ApparetnPowerTotal_kVA,lo:=5968,hi:=5969);
Read_Real(rVar:=NSX[5].MAX_CosFL1,lo:=5970,hi:=5971);
Read_Real(rVar:=NSX[5].MAX_CosFL2,lo:=5972,hi:=5973);
Read_Real(rVar:=NSX[5].MAX_CosFL3,lo:=5974,hi:=5975);
Read_Real(rVar:=NSX[5].MAX_CosFTotal,lo:=5976,hi:=5977);
Read_Real(rVar:=NSX[5].MAX_CurrentAvgI1I2I3_A,lo:=5978,hi:=5979);
Read_Real(rVar:=NSX[5].MAX_CurrentL1_A,lo:=5980,hi:=5981);
Read_Real(rVar:=NSX[5].MAX_CurrentL2_A,lo:=5982,hi:=5983);
Read_Real(rVar:=NSX[5].MAX_CurrentL3_A,lo:=5984,hi:=5985);
Read_Real(rVar:=NSX[5].MAX_CurrentMaxL1L2L3N_A,lo:=5986,hi:=5987);
Read_Real(rVar:=NSX[5].MAX_CurrentN_A,lo:=5988,hi:=5989);
Read_Real(rVar:=NSX[5].MAX_DistortionPowerL1_kVAr,lo:=5990,hi:=5991);
Read_Real(rVar:=NSX[5].MAX_DistortionPowerL2_kVAr,lo:=5992,hi:=5993);
Read_Real(rVar:=NSX[5].MAX_DistortionPowerL3_kVAr,lo:=5994,hi:=5995);
Read_Real(rVar:=NSX[5].MAX_DistortionPowerTotal_kVAr,lo:=5996,hi:=5997);
Read_Real(rVar:=NSX[5].MAX_Frequency_Hz,lo:=5998,hi:=5999);
Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL1_kVAr,lo:=6000,hi:=6001);
Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL2_kVAr,lo:=6002,hi:=6003);
Read_Real(rVar:=NSX[5].MAX_FunReactivePowerL3_kVAr,lo:=6004,hi:=6005);
Read_Real(rVar:=NSX[5].MAX_FunReactivePowerTotal_kVAr,lo:=6006,hi:=6007);
Read_Real(rVar:=NSX[5].MAX_PowerFactorL1,lo:=6008,hi:=6009);
Read_Real(rVar:=NSX[5].MAX_PowerFactorL2,lo:=6010,hi:=6011);
Read_Real(rVar:=NSX[5].MAX_PowerFactorL3,lo:=6012,hi:=6013);
Read_Real(rVar:=NSX[5].MAX_PowerFactorTotal,lo:=6014,hi:=6015);
Read_Real(rVar:=NSX[5].MAX_ReactivePowerL1_kVAr,lo:=6016,hi:=6017);
Read_Real(rVar:=NSX[5].MAX_ReactivePowerL2_kVAr,lo:=6018,hi:=6019);
Read_Real(rVar:=NSX[5].MAX_ReactivePowerL3_kVAr,lo:=6020,hi:=6021);
Read_Real(rVar:=NSX[5].MAX_ReactivePowerTotal_kVAr,lo:=6022,hi:=6023);
Read_Real(rVar:=NSX[5].MAX_THDI1_P,lo:=6024,hi:=6025);
Read_Real(rVar:=NSX[5].MAX_THDI2_P,lo:=6026,hi:=6027);
Read_Real(rVar:=NSX[5].MAX_THDI3_P,lo:=6028,hi:=6029);
Read_Real(rVar:=NSX[5].MAX_THDV12_P,lo:=6030,hi:=6031);
Read_Real(rVar:=NSX[5].MAX_THDV1N_P,lo:=6032,hi:=6033);
Read_Real(rVar:=NSX[5].MAX_THDV23_P,lo:=6034,hi:=6035);
Read_Real(rVar:=NSX[5].MAX_THDV2N_P,lo:=6036,hi:=6037);
Read_Real(rVar:=NSX[5].MAX_THDV31_P,lo:=6038,hi:=6039);
Read_Real(rVar:=NSX[5].MAX_THDV3N_P,lo:=6040,hi:=6041);
Read_Real(rVar:=NSX[5].MAX_VoltageAvgPhToN_V,lo:=6042,hi:=6043);
Read_Real(rVar:=NSX[5].MAX_VoltageAvgPhToPh_V,lo:=6044,hi:=6045);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV12_P,lo:=6046,hi:=6047);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV1N_P,lo:=6048,hi:=6049);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV23_P,lo:=6050,hi:=6051);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV2N_P,lo:=6052,hi:=6053);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV31_P,lo:=6054,hi:=6055);
Read_Real(rVar:=NSX[5].MAX_VoltageUnbV3N_P,lo:=6056,hi:=6057);
Read_Real(rVar:=NSX[5].MAX_VoltageV12_V,lo:=6058,hi:=6059);
Read_Real(rVar:=NSX[5].MAX_VoltageV1N_V,lo:=6060,hi:=6061);
Read_Real(rVar:=NSX[5].MAX_VoltageV23_V,lo:=6062,hi:=6063);
Read_Real(rVar:=NSX[5].MAX_VoltageV2N_V,lo:=6064,hi:=6065);
Read_Real(rVar:=NSX[5].MAX_VoltageV31_V,lo:=6066,hi:=6067);
Read_Real(rVar:=NSX[5].MAX_VoltageV3N_V,lo:=6068,hi:=6069);
Read_Real(rVar:=NSX[5].MIN_ActivePowerL1_kW,lo:=6070,hi:=6071);
Read_Real(rVar:=NSX[5].MIN_ActivePowerL2_kW,lo:=6072,hi:=6073);
Read_Real(rVar:=NSX[5].MIN_ActivePowerL3_kW,lo:=6074,hi:=6075);
Read_Real(rVar:=NSX[5].MIN_ActivePowerTotal_kW,lo:=6076,hi:=6077);
Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL1_kVA,lo:=6078,hi:=6079);
Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL2_kVA,lo:=6080,hi:=6081);
Read_Real(rVar:=NSX[5].MIN_ApparetnPowerL3_kVA,lo:=6082,hi:=6083);
Read_Real(rVar:=NSX[5].MIN_ApparetnPowerTotal_kVA,lo:=6084,hi:=6085);
Read_Real(rVar:=NSX[5].MIN_CosFL1,lo:=6086,hi:=6087);
Read_Real(rVar:=NSX[5].MIN_CosFL2,lo:=6088,hi:=6089);
Read_Real(rVar:=NSX[5].MIN_CosFL3,lo:=6090,hi:=6091);
Read_Real(rVar:=NSX[5].MIN_CosFTotal,lo:=6092,hi:=6093);
Read_Real(rVar:=NSX[5].MIN_CurrentAvgI1I2I3_A,lo:=6094,hi:=6095);
Read_Real(rVar:=NSX[5].MIN_CurrentL1_A,lo:=6096,hi:=6097);
Read_Real(rVar:=NSX[5].MIN_CurrentL2_A,lo:=6098,hi:=6099);
Read_Real(rVar:=NSX[5].MIN_CurrentL3_A,lo:=6100,hi:=6101);
Read_Real(rVar:=NSX[5].MIN_CurrentMaxL1L2L3N_A,lo:=6102,hi:=6103);
Read_Real(rVar:=NSX[5].MIN_CurrentN_A,lo:=6104,hi:=6105);
Read_Real(rVar:=NSX[5].MIN_DistortionPowerL1_kVAr,lo:=6106,hi:=6107);
Read_Real(rVar:=NSX[5].MIN_DistortionPowerL2_kVAr,lo:=6108,hi:=6109);
Read_Real(rVar:=NSX[5].MIN_DistortionPowerL3_kVAr,lo:=6110,hi:=6111);
Read_Real(rVar:=NSX[5].MIN_DistortionPowerTotal_kVAr,lo:=6112,hi:=6113);
Read_Real(rVar:=NSX[5].MIN_Frequency_Hz,lo:=6114,hi:=6115);
Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL1_kVAr,lo:=6116,hi:=6117);
Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL2_kVAr,lo:=6118,hi:=6119);
Read_Real(rVar:=NSX[5].MIN_FunReactivePowerL3_kVAr,lo:=6120,hi:=6121);
Read_Real(rVar:=NSX[5].MIN_FunReactivePowerTotal_kVAr,lo:=6122,hi:=6123);
Read_Real(rVar:=NSX[5].MIN_PowerFactorL1,lo:=6124,hi:=6125);
Read_Real(rVar:=NSX[5].MIN_PowerFactorL2,lo:=6126,hi:=6127);
Read_Real(rVar:=NSX[5].MIN_PowerFactorL3,lo:=6128,hi:=6129);
Read_Real(rVar:=NSX[5].MIN_PowerFactorTotal,lo:=6130,hi:=6131);
Read_Real(rVar:=NSX[5].MIN_ReactivePowerL1_kVAr,lo:=6132,hi:=6133);
Read_Real(rVar:=NSX[5].MIN_ReactivePowerL2_kVAr,lo:=6134,hi:=6135);
Read_Real(rVar:=NSX[5].MIN_ReactivePowerL3_kVAr,lo:=6136,hi:=6137);
Read_Real(rVar:=NSX[5].MIN_ReactivePowerTotal_kVAr,lo:=6138,hi:=6139);
Read_Real(rVar:=NSX[5].MIN_THDI1_P,lo:=6140,hi:=6141);
Read_Real(rVar:=NSX[5].MIN_THDI2_P,lo:=6142,hi:=6143);
Read_Real(rVar:=NSX[5].MIN_THDI3_P,lo:=6144,hi:=6145);
Read_Real(rVar:=NSX[5].MIN_THDV12_P,lo:=6146,hi:=6147);
Read_Real(rVar:=NSX[5].MIN_THDV1N_P,lo:=6148,hi:=6149);
Read_Real(rVar:=NSX[5].MIN_THDV23_P,lo:=6150,hi:=6151);
Read_Real(rVar:=NSX[5].MIN_THDV2N_P,lo:=6152,hi:=6153);
Read_Real(rVar:=NSX[5].MIN_THDV31_P,lo:=6154,hi:=6155);
Read_Real(rVar:=NSX[5].MIN_THDV3N_P,lo:=6156,hi:=6157);
Read_Real(rVar:=NSX[5].MIN_VoltageAvgPhToN_V,lo:=6158,hi:=6159);
Read_Real(rVar:=NSX[5].MIN_VoltageAvgPhToPh_V,lo:=6160,hi:=6161);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV12_P,lo:=6162,hi:=6163);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV1N_P,lo:=6164,hi:=6165);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV23_P,lo:=6166,hi:=6167);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV2N_P,lo:=6168,hi:=6169);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV31_P,lo:=6170,hi:=6171);
Read_Real(rVar:=NSX[5].MIN_VoltageUnbV3N_P,lo:=6172,hi:=6173);
Read_Real(rVar:=NSX[5].MIN_VoltageV12_V,lo:=6174,hi:=6175);
Read_Real(rVar:=NSX[5].MIN_VoltageV1N_V,lo:=6176,hi:=6177);
Read_Real(rVar:=NSX[5].MIN_VoltageV23_V,lo:=6178,hi:=6179);
Read_Real(rVar:=NSX[5].MIN_VoltageV2N_V,lo:=6180,hi:=6181);
Read_Real(rVar:=NSX[5].MIN_VoltageV31_V,lo:=6182,hi:=6183);
Read_Real(rVar:=NSX[5].MIN_VoltageV3N_V,lo:=6184,hi:=6185);
Read_Real(rVar:=NSX[5].PowerFactorL1,lo:=6186,hi:=6187);
Read_Real(rVar:=NSX[5].PowerFactorL2,lo:=6188,hi:=6189);
Read_Real(rVar:=NSX[5].PowerFactorL3,lo:=6190,hi:=6191);
Read_Real(rVar:=NSX[5].PowerFactorTotal,lo:=6192,hi:=6193);
Read_Real(rVar:=NSX[5].RazEner_D,lo:=6194,hi:=6195);
Read_Real(rVar:=NSX[5].RazEner_D_SCADA,lo:=6196,hi:=6197);
Read_Real(rVar:=NSX[5].RazEner_D_TEMP,lo:=6198,hi:=6199);
Read_Real(rVar:=NSX[5].RazEner_M,lo:=6200,hi:=6201);
Read_Real(rVar:=NSX[5].RazEner_M_SCADA,lo:=6202,hi:=6203);
Read_Real(rVar:=NSX[5].RazEner_M_TEMP,lo:=6204,hi:=6205);
Read_Real(rVar:=NSX[5].RazEner_T,lo:=6206,hi:=6207);
Read_Real(rVar:=NSX[5].RazEner_T_SCADA,lo:=6208,hi:=6209);
Read_Real(rVar:=NSX[5].RazEner_T_TEMP,lo:=6210,hi:=6211);
Read_Real(rVar:=NSX[5].ReactiveEnergy_kVArh,lo:=6212,hi:=6213);
Read_Real(rVar:=NSX[5].ReactiveNegativeEnergy_kVArh,lo:=6214,hi:=6215);
Read_Real(rVar:=NSX[5].ReactivePositiveEnergy_kVArh,lo:=6216,hi:=6217);
Read_Real(rVar:=NSX[5].ReactivePowerDemand_kVAr,lo:=6218,hi:=6219);
Read_Real(rVar:=NSX[5].ReactivePowerL1_kVAr,lo:=6220,hi:=6221);
Read_Real(rVar:=NSX[5].ReactivePowerL2_kVAr,lo:=6222,hi:=6223);
Read_Real(rVar:=NSX[5].ReactivePowerL3_kVAr,lo:=6224,hi:=6225);
Read_Real(rVar:=NSX[5].ReactivePowerMaxDemand_kVAr,lo:=6226,hi:=6227);
Read_Real(rVar:=NSX[5].ReactivePowerTotal_kVAr,lo:=6228,hi:=6229);
Read_Real(rVar:=NSX[5].THDI1_P,lo:=6230,hi:=6231);
Read_Real(rVar:=NSX[5].THDI2_P,lo:=6232,hi:=6233);
Read_Real(rVar:=NSX[5].THDI3_P,lo:=6234,hi:=6235);
Read_Real(rVar:=NSX[5].THDV12_P,lo:=6236,hi:=6237);
Read_Real(rVar:=NSX[5].THDV1N_P,lo:=6238,hi:=6239);
Read_Real(rVar:=NSX[5].THDV23_P,lo:=6240,hi:=6241);
Read_Real(rVar:=NSX[5].THDV2N_P,lo:=6242,hi:=6243);
Read_Real(rVar:=NSX[5].THDV31_P,lo:=6244,hi:=6245);
Read_Real(rVar:=NSX[5].THDV3N_P,lo:=6246,hi:=6247);
Read_Real(rVar:=NSX[5].VoltageAvgPhToN_V,lo:=6248,hi:=6249);
Read_Real(rVar:=NSX[5].VoltageAvgPhToPh_V,lo:=6250,hi:=6251);
Read_Real(rVar:=NSX[5].VoltageUnbV12_P,lo:=6252,hi:=6253);
Read_Real(rVar:=NSX[5].VoltageUnbV1N_P,lo:=6254,hi:=6255);
Read_Real(rVar:=NSX[5].VoltageUnbV23_P,lo:=6256,hi:=6257);
Read_Real(rVar:=NSX[5].VoltageUnbV2N_P,lo:=6258,hi:=6259);
Read_Real(rVar:=NSX[5].VoltageUnbV31_P,lo:=6260,hi:=6261);
Read_Real(rVar:=NSX[5].VoltageUnbV3N_P,lo:=6262,hi:=6263);
Read_Real(rVar:=NSX[5].VoltageV12_V,lo:=6264,hi:=6265);
Read_Real(rVar:=NSX[5].VoltageV1N_V,lo:=6266,hi:=6267);
Read_Real(rVar:=NSX[5].VoltageV23_V,lo:=6268,hi:=6269);
Read_Real(rVar:=NSX[5].VoltageV2N_V,lo:=6270,hi:=6271);
Read_Real(rVar:=NSX[5].VoltageV31_V,lo:=6272,hi:=6273);
Read_Real(rVar:=NSX[5].VoltageV3N_V,lo:=6274,hi:=6275);
Read_Real(rVar:=NSX[6].ActiveEnergy_kWh,lo:=6276,hi:=6277);
Read_Real(rVar:=NSX[6].ActiveNegativeEnergy_kWh,lo:=6278,hi:=6279);
Read_Real(rVar:=NSX[6].ActivePositiveEnergy_kWh,lo:=6280,hi:=6281);
Read_Real(rVar:=NSX[6].ActivePowerDemand_kW,lo:=6282,hi:=6283);
Read_Real(rVar:=NSX[6].ActivePowerL1_kW,lo:=6284,hi:=6285);
Read_Real(rVar:=NSX[6].ActivePowerL2_kW,lo:=6286,hi:=6287);
Read_Real(rVar:=NSX[6].ActivePowerL3_kW,lo:=6288,hi:=6289);
Read_Real(rVar:=NSX[6].ActivePowerMaxDemand_kW,lo:=6290,hi:=6291);
Read_Real(rVar:=NSX[6].ActivePowerTotal_kW,lo:=6292,hi:=6293);
Read_Real(rVar:=NSX[6].ApparentEnergy_kVAh,lo:=6294,hi:=6295);
Read_Real(rVar:=NSX[6].ApparentPowerDemand_kVA,lo:=6296,hi:=6297);
Read_Real(rVar:=NSX[6].ApparentPowerMaxDemand_kVA,lo:=6298,hi:=6299);
Read_Real(rVar:=NSX[6].ApparetnPowerL1_kVA,lo:=6300,hi:=6301);
Read_Real(rVar:=NSX[6].ApparetnPowerL2_kVA,lo:=6302,hi:=6303);
Read_Real(rVar:=NSX[6].ApparetnPowerL3_kVA,lo:=6304,hi:=6305);
Read_Real(rVar:=NSX[6].ApparetnPowerTotal_kVA,lo:=6306,hi:=6307);
Read_Real(rVar:=NSX[6].CosFL1,lo:=6308,hi:=6309);
Read_Real(rVar:=NSX[6].CosFL2,lo:=6310,hi:=6311);
Read_Real(rVar:=NSX[6].CosFL3,lo:=6312,hi:=6313);
Read_Real(rVar:=NSX[6].CosFTotal,lo:=6314,hi:=6315);
Read_Real(rVar:=NSX[6].CumulNegativeActiveEnergy_kWh,lo:=6316,hi:=6317);
Read_Real(rVar:=NSX[6].CumulPositiveActiveEnergy_kWh,lo:=6318,hi:=6319);
Read_Real(rVar:=NSX[6].CurrentAvgI1I2I3_A,lo:=6320,hi:=6321);
Read_Real(rVar:=NSX[6].CurrentDemandL1_A,lo:=6322,hi:=6323);
Read_Real(rVar:=NSX[6].CurrentDemandL2_A,lo:=6324,hi:=6325);
Read_Real(rVar:=NSX[6].CurrentDemandL3_A,lo:=6326,hi:=6327);
Read_Real(rVar:=NSX[6].CurrentDemandMaxL1_A,lo:=6328,hi:=6329);
Read_Real(rVar:=NSX[6].CurrentDemandMaxL2_A,lo:=6330,hi:=6331);
Read_Real(rVar:=NSX[6].CurrentDemandMaxL3_A,lo:=6332,hi:=6333);
Read_Real(rVar:=NSX[6].CurrentDemandMaxN_A,lo:=6334,hi:=6335);
Read_Real(rVar:=NSX[6].CurrentDemandN_A,lo:=6336,hi:=6337);
Read_Real(rVar:=NSX[6].CurrentL1_A,lo:=6338,hi:=6339);
Read_Real(rVar:=NSX[6].CurrentL2_A,lo:=6340,hi:=6341);
Read_Real(rVar:=NSX[6].CurrentL3_A,lo:=6342,hi:=6343);
Read_Real(rVar:=NSX[6].CurrentN_A,lo:=6344,hi:=6345);
Read_Real(rVar:=NSX[6].CurrentUnbI1_P,lo:=6346,hi:=6347);
Read_Real(rVar:=NSX[6].CurrentUnbI2_P,lo:=6348,hi:=6349);
Read_Real(rVar:=NSX[6].CurrentUnbI3_P,lo:=6350,hi:=6351);
Read_Real(rVar:=NSX[6].CurrentUnbN_P,lo:=6352,hi:=6353);
Read_Real(rVar:=NSX[6].DelovnaEnergija_TEMP,lo:=6354,hi:=6355);
Read_Real(rVar:=NSX[6].DistortionPowerL1_kVAr,lo:=6356,hi:=6357);
Read_Real(rVar:=NSX[6].DistortionPowerL2_kVAr,lo:=6358,hi:=6359);
Read_Real(rVar:=NSX[6].DistortionPowerL3_kVAr,lo:=6360,hi:=6361);
Read_Real(rVar:=NSX[6].DistortionPowerTotal_kVAr,lo:=6362,hi:=6363);
Read_Real(rVar:=NSX[6].Frequency_Hz,lo:=6364,hi:=6365);
Read_Real(rVar:=NSX[6].FunReactivePowerL1_kVAr,lo:=6366,hi:=6367);
Read_Real(rVar:=NSX[6].FunReactivePowerL2_kVAr,lo:=6368,hi:=6369);
Read_Real(rVar:=NSX[6].FunReactivePowerL3_kVAr,lo:=6370,hi:=6371);
Read_Real(rVar:=NSX[6].FunReactivePowerTotal_kVAr,lo:=6372,hi:=6373);
Read_Real(rVar:=NSX[6].MAX_ActivePowerL1_kW,lo:=6374,hi:=6375);
Read_Real(rVar:=NSX[6].MAX_ActivePowerL2_kW,lo:=6376,hi:=6377);
Read_Real(rVar:=NSX[6].MAX_ActivePowerL3_kW,lo:=6378,hi:=6379);
Read_Real(rVar:=NSX[6].MAX_ActivePowerTotal_kW,lo:=6380,hi:=6381);
Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL1_kVA,lo:=6382,hi:=6383);
Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL2_kVA,lo:=6384,hi:=6385);
Read_Real(rVar:=NSX[6].MAX_ApparetnPowerL3_kVA,lo:=6386,hi:=6387);
Read_Real(rVar:=NSX[6].MAX_ApparetnPowerTotal_kVA,lo:=6388,hi:=6389);
Read_Real(rVar:=NSX[6].MAX_CosFL1,lo:=6390,hi:=6391);
Read_Real(rVar:=NSX[6].MAX_CosFL2,lo:=6392,hi:=6393);
Read_Real(rVar:=NSX[6].MAX_CosFL3,lo:=6394,hi:=6395);
Read_Real(rVar:=NSX[6].MAX_CosFTotal,lo:=6396,hi:=6397);
Read_Real(rVar:=NSX[6].MAX_CurrentAvgI1I2I3_A,lo:=6398,hi:=6399);
Read_Real(rVar:=NSX[6].MAX_CurrentL1_A,lo:=6400,hi:=6401);
Read_Real(rVar:=NSX[6].MAX_CurrentL2_A,lo:=6402,hi:=6403);
Read_Real(rVar:=NSX[6].MAX_CurrentL3_A,lo:=6404,hi:=6405);
Read_Real(rVar:=NSX[6].MAX_CurrentMaxL1L2L3N_A,lo:=6406,hi:=6407);
Read_Real(rVar:=NSX[6].MAX_CurrentN_A,lo:=6408,hi:=6409);
Read_Real(rVar:=NSX[6].MAX_DistortionPowerL1_kVAr,lo:=6410,hi:=6411);
Read_Real(rVar:=NSX[6].MAX_DistortionPowerL2_kVAr,lo:=6412,hi:=6413);
Read_Real(rVar:=NSX[6].MAX_DistortionPowerL3_kVAr,lo:=6414,hi:=6415);
Read_Real(rVar:=NSX[6].MAX_DistortionPowerTotal_kVAr,lo:=6416,hi:=6417);
Read_Real(rVar:=NSX[6].MAX_Frequency_Hz,lo:=6418,hi:=6419);
Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL1_kVAr,lo:=6420,hi:=6421);
Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL2_kVAr,lo:=6422,hi:=6423);
Read_Real(rVar:=NSX[6].MAX_FunReactivePowerL3_kVAr,lo:=6424,hi:=6425);
Read_Real(rVar:=NSX[6].MAX_FunReactivePowerTotal_kVAr,lo:=6426,hi:=6427);
Read_Real(rVar:=NSX[6].MAX_PowerFactorL1,lo:=6428,hi:=6429);
Read_Real(rVar:=NSX[6].MAX_PowerFactorL2,lo:=6430,hi:=6431);
Read_Real(rVar:=NSX[6].MAX_PowerFactorL3,lo:=6432,hi:=6433);
Read_Real(rVar:=NSX[6].MAX_PowerFactorTotal,lo:=6434,hi:=6435);
Read_Real(rVar:=NSX[6].MAX_ReactivePowerL1_kVAr,lo:=6436,hi:=6437);
Read_Real(rVar:=NSX[6].MAX_ReactivePowerL2_kVAr,lo:=6438,hi:=6439);
Read_Real(rVar:=NSX[6].MAX_ReactivePowerL3_kVAr,lo:=6440,hi:=6441);
Read_Real(rVar:=NSX[6].MAX_ReactivePowerTotal_kVAr,lo:=6442,hi:=6443);
Read_Real(rVar:=NSX[6].MAX_THDI1_P,lo:=6444,hi:=6445);
Read_Real(rVar:=NSX[6].MAX_THDI2_P,lo:=6446,hi:=6447);
Read_Real(rVar:=NSX[6].MAX_THDI3_P,lo:=6448,hi:=6449);
Read_Real(rVar:=NSX[6].MAX_THDV12_P,lo:=6450,hi:=6451);
Read_Real(rVar:=NSX[6].MAX_THDV1N_P,lo:=6452,hi:=6453);
Read_Real(rVar:=NSX[6].MAX_THDV23_P,lo:=6454,hi:=6455);
Read_Real(rVar:=NSX[6].MAX_THDV2N_P,lo:=6456,hi:=6457);
Read_Real(rVar:=NSX[6].MAX_THDV31_P,lo:=6458,hi:=6459);
Read_Real(rVar:=NSX[6].MAX_THDV3N_P,lo:=6460,hi:=6461);
Read_Real(rVar:=NSX[6].MAX_VoltageAvgPhToN_V,lo:=6462,hi:=6463);
Read_Real(rVar:=NSX[6].MAX_VoltageAvgPhToPh_V,lo:=6464,hi:=6465);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV12_P,lo:=6466,hi:=6467);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV1N_P,lo:=6468,hi:=6469);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV23_P,lo:=6470,hi:=6471);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV2N_P,lo:=6472,hi:=6473);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV31_P,lo:=6474,hi:=6475);
Read_Real(rVar:=NSX[6].MAX_VoltageUnbV3N_P,lo:=6476,hi:=6477);
Read_Real(rVar:=NSX[6].MAX_VoltageV12_V,lo:=6478,hi:=6479);
Read_Real(rVar:=NSX[6].MAX_VoltageV1N_V,lo:=6480,hi:=6481);
Read_Real(rVar:=NSX[6].MAX_VoltageV23_V,lo:=6482,hi:=6483);
Read_Real(rVar:=NSX[6].MAX_VoltageV2N_V,lo:=6484,hi:=6485);
Read_Real(rVar:=NSX[6].MAX_VoltageV31_V,lo:=6486,hi:=6487);
Read_Real(rVar:=NSX[6].MAX_VoltageV3N_V,lo:=6488,hi:=6489);
Read_Real(rVar:=NSX[6].MIN_ActivePowerL1_kW,lo:=6490,hi:=6491);
Read_Real(rVar:=NSX[6].MIN_ActivePowerL2_kW,lo:=6492,hi:=6493);
Read_Real(rVar:=NSX[6].MIN_ActivePowerL3_kW,lo:=6494,hi:=6495);
Read_Real(rVar:=NSX[6].MIN_ActivePowerTotal_kW,lo:=6496,hi:=6497);
Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL1_kVA,lo:=6498,hi:=6499);
Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL2_kVA,lo:=6500,hi:=6501);
Read_Real(rVar:=NSX[6].MIN_ApparetnPowerL3_kVA,lo:=6502,hi:=6503);
Read_Real(rVar:=NSX[6].MIN_ApparetnPowerTotal_kVA,lo:=6504,hi:=6505);
Read_Real(rVar:=NSX[6].MIN_CosFL1,lo:=6506,hi:=6507);
Read_Real(rVar:=NSX[6].MIN_CosFL2,lo:=6508,hi:=6509);
Read_Real(rVar:=NSX[6].MIN_CosFL3,lo:=6510,hi:=6511);
Read_Real(rVar:=NSX[6].MIN_CosFTotal,lo:=6512,hi:=6513);
Read_Real(rVar:=NSX[6].MIN_CurrentAvgI1I2I3_A,lo:=6514,hi:=6515);
Read_Real(rVar:=NSX[6].MIN_CurrentL1_A,lo:=6516,hi:=6517);
Read_Real(rVar:=NSX[6].MIN_CurrentL2_A,lo:=6518,hi:=6519);
Read_Real(rVar:=NSX[6].MIN_CurrentL3_A,lo:=6520,hi:=6521);
Read_Real(rVar:=NSX[6].MIN_CurrentMaxL1L2L3N_A,lo:=6522,hi:=6523);
Read_Real(rVar:=NSX[6].MIN_CurrentN_A,lo:=6524,hi:=6525);
Read_Real(rVar:=NSX[6].MIN_DistortionPowerL1_kVAr,lo:=6526,hi:=6527);
Read_Real(rVar:=NSX[6].MIN_DistortionPowerL2_kVAr,lo:=6528,hi:=6529);
Read_Real(rVar:=NSX[6].MIN_DistortionPowerL3_kVAr,lo:=6530,hi:=6531);
Read_Real(rVar:=NSX[6].MIN_DistortionPowerTotal_kVAr,lo:=6532,hi:=6533);
Read_Real(rVar:=NSX[6].MIN_Frequency_Hz,lo:=6534,hi:=6535);
Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL1_kVAr,lo:=6536,hi:=6537);
Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL2_kVAr,lo:=6538,hi:=6539);
Read_Real(rVar:=NSX[6].MIN_FunReactivePowerL3_kVAr,lo:=6540,hi:=6541);
Read_Real(rVar:=NSX[6].MIN_FunReactivePowerTotal_kVAr,lo:=6542,hi:=6543);
Read_Real(rVar:=NSX[6].MIN_PowerFactorL1,lo:=6544,hi:=6545);
Read_Real(rVar:=NSX[6].MIN_PowerFactorL2,lo:=6546,hi:=6547);
Read_Real(rVar:=NSX[6].MIN_PowerFactorL3,lo:=6548,hi:=6549);
Read_Real(rVar:=NSX[6].MIN_PowerFactorTotal,lo:=6550,hi:=6551);
Read_Real(rVar:=NSX[6].MIN_ReactivePowerL1_kVAr,lo:=6552,hi:=6553);
Read_Real(rVar:=NSX[6].MIN_ReactivePowerL2_kVAr,lo:=6554,hi:=6555);
Read_Real(rVar:=NSX[6].MIN_ReactivePowerL3_kVAr,lo:=6556,hi:=6557);
Read_Real(rVar:=NSX[6].MIN_ReactivePowerTotal_kVAr,lo:=6558,hi:=6559);
Read_Real(rVar:=NSX[6].MIN_THDI1_P,lo:=6560,hi:=6561);
Read_Real(rVar:=NSX[6].MIN_THDI2_P,lo:=6562,hi:=6563);
Read_Real(rVar:=NSX[6].MIN_THDI3_P,lo:=6564,hi:=6565);
Read_Real(rVar:=NSX[6].MIN_THDV12_P,lo:=6566,hi:=6567);
Read_Real(rVar:=NSX[6].MIN_THDV1N_P,lo:=6568,hi:=6569);
Read_Real(rVar:=NSX[6].MIN_THDV23_P,lo:=6570,hi:=6571);
Read_Real(rVar:=NSX[6].MIN_THDV2N_P,lo:=6572,hi:=6573);
Read_Real(rVar:=NSX[6].MIN_THDV31_P,lo:=6574,hi:=6575);
Read_Real(rVar:=NSX[6].MIN_THDV3N_P,lo:=6576,hi:=6577);
Read_Real(rVar:=NSX[6].MIN_VoltageAvgPhToN_V,lo:=6578,hi:=6579);
Read_Real(rVar:=NSX[6].MIN_VoltageAvgPhToPh_V,lo:=6580,hi:=6581);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV12_P,lo:=6582,hi:=6583);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV1N_P,lo:=6584,hi:=6585);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV23_P,lo:=6586,hi:=6587);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV2N_P,lo:=6588,hi:=6589);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV31_P,lo:=6590,hi:=6591);
Read_Real(rVar:=NSX[6].MIN_VoltageUnbV3N_P,lo:=6592,hi:=6593);
Read_Real(rVar:=NSX[6].MIN_VoltageV12_V,lo:=6594,hi:=6595);
Read_Real(rVar:=NSX[6].MIN_VoltageV1N_V,lo:=6596,hi:=6597);
Read_Real(rVar:=NSX[6].MIN_VoltageV23_V,lo:=6598,hi:=6599);
Read_Real(rVar:=NSX[6].MIN_VoltageV2N_V,lo:=6600,hi:=6601);
Read_Real(rVar:=NSX[6].MIN_VoltageV31_V,lo:=6602,hi:=6603);
Read_Real(rVar:=NSX[6].MIN_VoltageV3N_V,lo:=6604,hi:=6605);
Read_Real(rVar:=NSX[6].PowerFactorL1,lo:=6606,hi:=6607);
Read_Real(rVar:=NSX[6].PowerFactorL2,lo:=6608,hi:=6609);
Read_Real(rVar:=NSX[6].PowerFactorL3,lo:=6610,hi:=6611);
Read_Real(rVar:=NSX[6].PowerFactorTotal,lo:=6612,hi:=6613);
Read_Real(rVar:=NSX[6].RazEner_D,lo:=6614,hi:=6615);
Read_Real(rVar:=NSX[6].RazEner_D_SCADA,lo:=6616,hi:=6617);
Read_Real(rVar:=NSX[6].RazEner_D_TEMP,lo:=6618,hi:=6619);
Read_Real(rVar:=NSX[6].RazEner_M,lo:=6620,hi:=6621);
Read_Real(rVar:=NSX[6].RazEner_M_SCADA,lo:=6622,hi:=6623);
Read_Real(rVar:=NSX[6].RazEner_M_TEMP,lo:=6624,hi:=6625);
Read_Real(rVar:=NSX[6].RazEner_T,lo:=6626,hi:=6627);
Read_Real(rVar:=NSX[6].RazEner_T_SCADA,lo:=6628,hi:=6629);
Read_Real(rVar:=NSX[6].RazEner_T_TEMP,lo:=6630,hi:=6631);
Read_Real(rVar:=NSX[6].ReactiveEnergy_kVArh,lo:=6632,hi:=6633);
Read_Real(rVar:=NSX[6].ReactiveNegativeEnergy_kVArh,lo:=6634,hi:=6635);
Read_Real(rVar:=NSX[6].ReactivePositiveEnergy_kVArh,lo:=6636,hi:=6637);
Read_Real(rVar:=NSX[6].ReactivePowerDemand_kVAr,lo:=6638,hi:=6639);
Read_Real(rVar:=NSX[6].ReactivePowerL1_kVAr,lo:=6640,hi:=6641);
Read_Real(rVar:=NSX[6].ReactivePowerL2_kVAr,lo:=6642,hi:=6643);
Read_Real(rVar:=NSX[6].ReactivePowerL3_kVAr,lo:=6644,hi:=6645);
Read_Real(rVar:=NSX[6].ReactivePowerMaxDemand_kVAr,lo:=6646,hi:=6647);
Read_Real(rVar:=NSX[6].ReactivePowerTotal_kVAr,lo:=6648,hi:=6649);
Read_Real(rVar:=NSX[6].THDI1_P,lo:=6650,hi:=6651);
Read_Real(rVar:=NSX[6].THDI2_P,lo:=6652,hi:=6653);
Read_Real(rVar:=NSX[6].THDI3_P,lo:=6654,hi:=6655);
Read_Real(rVar:=NSX[6].THDV12_P,lo:=6656,hi:=6657);
Read_Real(rVar:=NSX[6].THDV1N_P,lo:=6658,hi:=6659);
Read_Real(rVar:=NSX[6].THDV23_P,lo:=6660,hi:=6661);
Read_Real(rVar:=NSX[6].THDV2N_P,lo:=6662,hi:=6663);
Read_Real(rVar:=NSX[6].THDV31_P,lo:=6664,hi:=6665);
Read_Real(rVar:=NSX[6].THDV3N_P,lo:=6666,hi:=6667);
Read_Real(rVar:=NSX[6].VoltageAvgPhToN_V,lo:=6668,hi:=6669);
Read_Real(rVar:=NSX[6].VoltageAvgPhToPh_V,lo:=6670,hi:=6671);
Read_Real(rVar:=NSX[6].VoltageUnbV12_P,lo:=6672,hi:=6673);
Read_Real(rVar:=NSX[6].VoltageUnbV1N_P,lo:=6674,hi:=6675);
Read_Real(rVar:=NSX[6].VoltageUnbV23_P,lo:=6676,hi:=6677);
Read_Real(rVar:=NSX[6].VoltageUnbV2N_P,lo:=6678,hi:=6679);
Read_Real(rVar:=NSX[6].VoltageUnbV31_P,lo:=6680,hi:=6681);
Read_Real(rVar:=NSX[6].VoltageUnbV3N_P,lo:=6682,hi:=6683);
Read_Real(rVar:=NSX[6].VoltageV12_V,lo:=6684,hi:=6685);
Read_Real(rVar:=NSX[6].VoltageV1N_V,lo:=6686,hi:=6687);
Read_Real(rVar:=NSX[6].VoltageV23_V,lo:=6688,hi:=6689);
Read_Real(rVar:=NSX[6].VoltageV2N_V,lo:=6690,hi:=6691);
Read_Real(rVar:=NSX[6].VoltageV31_V,lo:=6692,hi:=6693);
Read_Real(rVar:=NSX[6].VoltageV3N_V,lo:=6694,hi:=6695);
Read_Real(rVar:=PMM.VirA.Current[10],lo:=6696,hi:=6697);
Read_Real(rVar:=PMM.VirA.Current[11],lo:=6698,hi:=6699);
Read_Real(rVar:=PMM.VirA.Current[12],lo:=6700,hi:=6701);
Read_Real(rVar:=PMM.VirA.Current[13],lo:=6702,hi:=6703);
Read_Real(rVar:=PMM.VirA.Current[14],lo:=6704,hi:=6705);
Read_Real(rVar:=PMM.VirA.Current[15],lo:=6706,hi:=6707);
Read_Real(rVar:=PMM.VirA.Current[16],lo:=6708,hi:=6709);
Read_Real(rVar:=PMM.VirA.Current[17],lo:=6710,hi:=6711);
Read_Real(rVar:=PMM.VirA.Current[18],lo:=6712,hi:=6713);
Read_Real(rVar:=PMM.VirA.Current[19],lo:=6714,hi:=6715);
Read_Real(rVar:=PMM.VirA.Current[1],lo:=6716,hi:=6717);
Read_Real(rVar:=PMM.VirA.Current[20],lo:=6718,hi:=6719);
Read_Real(rVar:=PMM.VirA.Current[21],lo:=6720,hi:=6721);
Read_Real(rVar:=PMM.VirA.Current[22],lo:=6722,hi:=6723);
Read_Real(rVar:=PMM.VirA.Current[23],lo:=6724,hi:=6725);
Read_Real(rVar:=PMM.VirA.Current[24],lo:=6726,hi:=6727);
Read_Real(rVar:=PMM.VirA.Current[25],lo:=6728,hi:=6729);
Read_Real(rVar:=PMM.VirA.Current[26],lo:=6730,hi:=6731);
Read_Real(rVar:=PMM.VirA.Current[27],lo:=6732,hi:=6733);
Read_Real(rVar:=PMM.VirA.Current[28],lo:=6734,hi:=6735);
Read_Real(rVar:=PMM.VirA.Current[29],lo:=6736,hi:=6737);
Read_Real(rVar:=PMM.VirA.Current[2],lo:=6738,hi:=6739);
Read_Real(rVar:=PMM.VirA.Current[30],lo:=6740,hi:=6741);
Read_Real(rVar:=PMM.VirA.Current[31],lo:=6742,hi:=6743);
Read_Real(rVar:=PMM.VirA.Current[32],lo:=6744,hi:=6745);
Read_Real(rVar:=PMM.VirA.Current[33],lo:=6746,hi:=6747);
Read_Real(rVar:=PMM.VirA.Current[34],lo:=6748,hi:=6749);
Read_Real(rVar:=PMM.VirA.Current[35],lo:=6750,hi:=6751);
Read_Real(rVar:=PMM.VirA.Current[36],lo:=6752,hi:=6753);
Read_Real(rVar:=PMM.VirA.Current[37],lo:=6754,hi:=6755);
Read_Real(rVar:=PMM.VirA.Current[38],lo:=6756,hi:=6757);
Read_Real(rVar:=PMM.VirA.Current[39],lo:=6758,hi:=6759);
Read_Real(rVar:=PMM.VirA.Current[3],lo:=6760,hi:=6761);
Read_Real(rVar:=PMM.VirA.Current[40],lo:=6762,hi:=6763);
Read_Real(rVar:=PMM.VirA.Current[41],lo:=6764,hi:=6765);
Read_Real(rVar:=PMM.VirA.Current[42],lo:=6766,hi:=6767);
Read_Real(rVar:=PMM.VirA.Current[43],lo:=6768,hi:=6769);
Read_Real(rVar:=PMM.VirA.Current[44],lo:=6770,hi:=6771);
Read_Real(rVar:=PMM.VirA.Current[4],lo:=6772,hi:=6773);
Read_Real(rVar:=PMM.VirA.Current[5],lo:=6774,hi:=6775);
Read_Real(rVar:=PMM.VirA.Current[6],lo:=6776,hi:=6777);
Read_Real(rVar:=PMM.VirA.Current[7],lo:=6778,hi:=6779);
Read_Real(rVar:=PMM.VirA.Current[8],lo:=6780,hi:=6781);
Read_Real(rVar:=PMM.VirA.Current[9],lo:=6782,hi:=6783);
Read_Real(rVar:=PMM.VirA_fsys,lo:=6784,hi:=6785);
Read_Real(rVar:=PMM.VirA_Isys,lo:=6786,hi:=6787);
Read_Real(rVar:=PMM.VirA_PFsys,lo:=6788,hi:=6789);
Read_Real(rVar:=PMM.VirA_Psys,lo:=6790,hi:=6791);
Read_Real(rVar:=PMM.VirA_Qsys,lo:=6792,hi:=6793);
Read_Real(rVar:=PMM.VirA_Ssys,lo:=6794,hi:=6795);
Read_Real(rVar:=PMM.VirA_Usys,lo:=6796,hi:=6797);
Read_Real(rVar:=PMM.VirAActiveEnergyConsumed_kWh,lo:=6798,hi:=6799);
Read_Real(rVar:=PMM.VirAActivePowerPhaseA_kW,lo:=6800,hi:=6801);
Read_Real(rVar:=PMM.VirAActivePowerPhaseB_kW,lo:=6802,hi:=6803);
Read_Real(rVar:=PMM.VirAActivePowerPhaseC_kW,lo:=6804,hi:=6805);
Read_Real(rVar:=PMM.VirAAparentPowerPhaseA,lo:=6806,hi:=6807);
Read_Real(rVar:=PMM.VirAAparentPowerPhaseB,lo:=6808,hi:=6809);
Read_Real(rVar:=PMM.VirAAparentPowerPhaseC,lo:=6810,hi:=6811);
Read_Real(rVar:=PMM.VirACurrentInPhaseA_A,lo:=6812,hi:=6813);
Read_Real(rVar:=PMM.VirACurrentInPhaseB_A,lo:=6814,hi:=6815);
Read_Real(rVar:=PMM.VirACurrentInPhaseC_A,lo:=6816,hi:=6817);
Read_Real(rVar:=PMM.VirAReactiveEnergyConsumed_kVARh,lo:=6818,hi:=6819);
Read_Real(rVar:=PMM.VirAReactivePowerPhaseA,lo:=6820,hi:=6821);
Read_Real(rVar:=PMM.VirAReactivePowerPhaseB,lo:=6822,hi:=6823);
Read_Real(rVar:=PMM.VirAReactivePowerPhaseC,lo:=6824,hi:=6825);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseAB_V,lo:=6826,hi:=6827);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseAN_V,lo:=6828,hi:=6829);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseBC_V,lo:=6830,hi:=6831);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseBN_V,lo:=6832,hi:=6833);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseCA_V,lo:=6834,hi:=6835);
Read_Real(rVar:=PMM.VirAVoltageBetweenPhaseCN_V,lo:=6836,hi:=6837);
Read_Real(rVar:=PMM.VirB.Current[10],lo:=6838,hi:=6839);
Read_Real(rVar:=PMM.VirB.Current[11],lo:=6840,hi:=6841);
Read_Real(rVar:=PMM.VirB.Current[12],lo:=6842,hi:=6843);
Read_Real(rVar:=PMM.VirB.Current[13],lo:=6844,hi:=6845);
Read_Real(rVar:=PMM.VirB.Current[14],lo:=6846,hi:=6847);
Read_Real(rVar:=PMM.VirB.Current[15],lo:=6848,hi:=6849);
Read_Real(rVar:=PMM.VirB.Current[16],lo:=6850,hi:=6851);
Read_Real(rVar:=PMM.VirB.Current[17],lo:=6852,hi:=6853);
Read_Real(rVar:=PMM.VirB.Current[18],lo:=6854,hi:=6855);
Read_Real(rVar:=PMM.VirB.Current[19],lo:=6856,hi:=6857);
Read_Real(rVar:=PMM.VirB.Current[1],lo:=6858,hi:=6859);
Read_Real(rVar:=PMM.VirB.Current[20],lo:=6860,hi:=6861);
Read_Real(rVar:=PMM.VirB.Current[21],lo:=6862,hi:=6863);
Read_Real(rVar:=PMM.VirB.Current[22],lo:=6864,hi:=6865);
Read_Real(rVar:=PMM.VirB.Current[23],lo:=6866,hi:=6867);
Read_Real(rVar:=PMM.VirB.Current[24],lo:=6868,hi:=6869);
Read_Real(rVar:=PMM.VirB.Current[25],lo:=6870,hi:=6871);
Read_Real(rVar:=PMM.VirB.Current[26],lo:=6872,hi:=6873);
Read_Real(rVar:=PMM.VirB.Current[27],lo:=6874,hi:=6875);
Read_Real(rVar:=PMM.VirB.Current[28],lo:=6876,hi:=6877);
Read_Real(rVar:=PMM.VirB.Current[29],lo:=6878,hi:=6879);
Read_Real(rVar:=PMM.VirB.Current[2],lo:=6880,hi:=6881);
Read_Real(rVar:=PMM.VirB.Current[30],lo:=6882,hi:=6883);
Read_Real(rVar:=PMM.VirB.Current[31],lo:=6884,hi:=6885);
Read_Real(rVar:=PMM.VirB.Current[32],lo:=6886,hi:=6887);
Read_Real(rVar:=PMM.VirB.Current[33],lo:=6888,hi:=6889);
Read_Real(rVar:=PMM.VirB.Current[34],lo:=6890,hi:=6891);
Read_Real(rVar:=PMM.VirB.Current[35],lo:=6892,hi:=6893);
Read_Real(rVar:=PMM.VirB.Current[36],lo:=6894,hi:=6895);
Read_Real(rVar:=PMM.VirB.Current[37],lo:=6896,hi:=6897);
Read_Real(rVar:=PMM.VirB.Current[38],lo:=6898,hi:=6899);
Read_Real(rVar:=PMM.VirB.Current[39],lo:=6900,hi:=6901);
Read_Real(rVar:=PMM.VirB.Current[3],lo:=6902,hi:=6903);
Read_Real(rVar:=PMM.VirB.Current[40],lo:=6904,hi:=6905);
Read_Real(rVar:=PMM.VirB.Current[41],lo:=6906,hi:=6907);
Read_Real(rVar:=PMM.VirB.Current[42],lo:=6908,hi:=6909);
Read_Real(rVar:=PMM.VirB.Current[43],lo:=6910,hi:=6911);
Read_Real(rVar:=PMM.VirB.Current[44],lo:=6912,hi:=6913);
Read_Real(rVar:=PMM.VirB.Current[4],lo:=6914,hi:=6915);
Read_Real(rVar:=PMM.VirB.Current[5],lo:=6916,hi:=6917);
Read_Real(rVar:=PMM.VirB.Current[6],lo:=6918,hi:=6919);
Read_Real(rVar:=PMM.VirB.Current[7],lo:=6920,hi:=6921);
Read_Real(rVar:=PMM.VirB.Current[8],lo:=6922,hi:=6923);
Read_Real(rVar:=PMM.VirB.Current[9],lo:=6924,hi:=6925);
Read_Real(rVar:=PMM.VirB_fsys,lo:=6926,hi:=6927);
Read_Real(rVar:=PMM.VirB_Isys,lo:=6928,hi:=6929);
Read_Real(rVar:=PMM.VirB_PFsys,lo:=6930,hi:=6931);
Read_Real(rVar:=PMM.VirB_Psys,lo:=6932,hi:=6933);
Read_Real(rVar:=PMM.VirB_Qsys,lo:=6934,hi:=6935);
Read_Real(rVar:=PMM.VirB_Ssys,lo:=6936,hi:=6937);
Read_Real(rVar:=PMM.VirB_Usys,lo:=6938,hi:=6939);
Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=6940,hi:=6941);
Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=6942,hi:=6943);
Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=6944,hi:=6945);
Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=6946,hi:=6947);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=6948,hi:=6949);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=6950,hi:=6951);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=6952,hi:=6953);
Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=6954,hi:=6955);
Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=6956,hi:=6957);
Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=6958,hi:=6959);
Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kVARh,lo:=6960,hi:=6961);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=6962,hi:=6963);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=6964,hi:=6965);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=6966,hi:=6967);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=6968,hi:=6969);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=6970,hi:=6971);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=6972,hi:=6973);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=6974,hi:=6975);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=6976,hi:=6977);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=6978,hi:=6979);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=7000);
Read_String(sVar:=Date_Time[1],start:=7015);
Read_String(sVar:=Date_Time[2],start:=7030);
Read_String(sVar:=Date_Time[3],start:=7045);
Read_String(sVar:=kom_nast_cas_izpada,start:=7060);
Read_String(sVar:=UserCurrentName,start:=7075);
Read_String(sVar:=UserDisplay,start:=7090);
(*Branje ULONG*)
(**)
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
1:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
2:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
3:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
4:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
5:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
6:ComError:=Bit_0;
7:ComSCADA:=Bit_0;
8:ComSCADA1:=Bit_0;
9:ComSCADA2:=Bit_0;
10:ComSCADA3:=Bit_0;
11:DI2_I10_Rezerva3:=Bit_0;
12:DI2_I11_Rezerva4:=Bit_0;
13:DI2_I12_Rezerva5:=Bit_0;
14:DI2_I13_Rezerva6:=Bit_0;
15:DI2_I8_Rezerva1:=Bit_0;
16:DI2_I9_Rezerva2:=Bit_0;
17:DI_SB_IROGSM21_Q0_Izkljucen:=Bit_0;
18:DI_SB_IROGSM21_Q0_Vkljucen:=Bit_0;
19:DI_SB_IROGSM21_Q11_Izkljucen:=Bit_0;
20:DI_SB_IROGSM21_Q11_Vkljucen:=Bit_0;
21:DI_SB_IROGSM21_Q12_Izkljucen:=Bit_0;
22:DI_SB_IROGSM21_Q12_Vkljucen:=Bit_0;
23:DI_SB_IROGSM21_Q13_Izpad:=Bit_0;
24:DI_SB_IROGSM21_Q13_Vkljucen:=Bit_0;
25:DI_SB_IROGSM21_Q14_Izpad:=Bit_0;
26:DI_SB_IROGSM21_Q14_Vkljucen:=Bit_0;
27:DI_SB_IROGSM21_Q15_Izpad:=Bit_0;
28:DI_SB_IROGSM21_Q15_Vkljucen:=Bit_0;
29:DI_SB_IROGSM21_SkupnaNapaka:=Bit_0;
30:DI_SB_IROGSM22_Q0_Izkljucen:=Bit_0;
31:DI_SB_IROGSM22_Q0_Vkljucen:=Bit_0;
32:DI_SB_IROGSM22_Q11_Izkljucen:=Bit_0;
33:DI_SB_IROGSM22_Q11_Vkljucen:=Bit_0;
34:DI_SB_IROGSM22_Q12_Izkljucen:=Bit_0;
35:DI_SB_IROGSM22_Q12_Vkljucen:=Bit_0;
36:DI_SB_IROGSM22_Q13_Izpad:=Bit_0;
37:DI_SB_IROGSM22_Q13_Vkljucen:=Bit_0;
38:DI_SB_IROGSM22_Q14_Izpad:=Bit_0;
39:DI_SB_IROGSM22_Q14_Vkljucen:=Bit_0;
40:DI_SB_IROGSM22_Q15_Izpad:=Bit_0;
41:DI_SB_IROGSM22_Q15_Vkljucen:=Bit_0;
42:DI_SB_IROGSM22_SkupnaNapaka:=Bit_0;
43:DI_SBi_RAZS_AA_Izolacija_NOT_OK:=Bit_0;
44:DI_SBi_RAZS_AB_Izolacija_NOT_OK:=Bit_0;
45:ErrComNSX[1]:=Bit_0;
46:ErrComNSX[2]:=Bit_0;
47:ErrComNSX[3]:=Bit_0;
48:ErrComNSX[4]:=Bit_0;
49:ErrComNSX[5]:=Bit_0;
50:ErrComNSX[6]:=Bit_0;
51:ErrComPMM[1]:=Bit_0;
52:ErrComPort2:=Bit_0;
53:ErrorComPMM[1].Error:=Bit_0;
54:napaka_kom_panel:=Bit_0;
55:napaka_kom_scada:=Bit_0;
56:napaka_kom_scada2:=Bit_0;
57:NapakaSenzorSkupno:=Bit_0;
58:NapakaSenzorVlagaHIA1:=Bit_0;
59:NapakaSenzorVlagaHIA2:=Bit_0;
60:NapakaSenzorVlagaHIA3:=Bit_0;
61:NapakaSenzorVlagaHIA4:=Bit_0;
62:NapakaSenzorVlagaHIA5:=Bit_0;
63:NapakaSenzorVlagaHIA6:=Bit_0;
64:NapakaSenzorVlagaHIA7:=Bit_0;
65:NapakaSenzorVlagaHIA8:=Bit_0;
66:NapakaTSTempTIA1:=Bit_0;
67:NapakaTSTempTIA2:=Bit_0;
68:NapakaTSTempTIA3:=Bit_0;
69:NapakaTSTempTIA4:=Bit_0;
70:NapakaTSTempTIA5:=Bit_0;
71:NapakaTSTempTIA6:=Bit_0;
72:NapakaTSTempTIA7:=Bit_0;
73:NapakaTSTempTIA8:=Bit_0;
74:NSX[1].ResetMAX:=Bit_0;
75:NSX[1].ResetMIN:=Bit_0;
76:NSX[2].ResetMAX:=Bit_0;
77:NSX[2].ResetMIN:=Bit_0;
78:NSX[3].ResetMAX:=Bit_0;
79:NSX[3].ResetMIN:=Bit_0;
80:NSX[4].ResetMAX:=Bit_0;
81:NSX[4].ResetMIN:=Bit_0;
82:NSX[5].ResetMAX:=Bit_0;
83:NSX[5].ResetMIN:=Bit_0;
84:NSX[6].ResetMAX:=Bit_0;
85:NSX[6].ResetMIN:=Bit_0;
86:PLC_SB_IROGSM21_F2_2_NOT_OK:=Bit_0;
87:PLC_SB_IROGSM22_F2_2_NOT_OK:=Bit_0;
88:PMM.QA1_GlStik_IZKLOP_IZPAD:=Bit_0;
89:PMM.QB1_GlStik_IZKLOP_IZPAD:=Bit_0;
90:PMM.SkNapaka_med60in80:=Bit_0;
91:PMM.SkNapaka_nad80:=Bit_0;
92:PMM.SkNapakaVirA_med60in80:=Bit_0;
93:PMM.SkNapakaVirA_nad80:=Bit_0;
94:PMM.SkNapakaVirB_med60in80:=Bit_0;
95:PMM.SkNapakaVirB_nad80:=Bit_0;
96:PMM.VirA_NapakaOzemljitve:=Bit_0;
97:PMM.VirB_NapakaOzemljitve:=Bit_0;
98:PrevisokaTemp:=Bit_0;
99:razlitjeLAH1:=Bit_0;
100:SetDateTime:=Bit_0;
101:SetDateTimeDemand:=Bit_0;
102:SetDateTimeError:=Bit_0;
103:SetDateTimeFinished:=Bit_0;
104:SlabaBaterijaPLC:=Bit_0;
105:TIA1_previs_temp:=Bit_0;
106:TIA2_previs_temp:=Bit_0;
107:TIA3_previs_temp:=Bit_0;
108:TIA4_previs_temp:=Bit_0;
109:TIA5_previs_temp:=Bit_0;
110:TIA6_previs_temp:=Bit_0;
111:TIA7_previs_temp:=Bit_0;
112:TIA8_previs_temp:=Bit_0;
113:ups_alarm:=Bit_0;
114:ups_baterijski_nac:=Bit_0;
115:ups_polnjenje:=Bit_0;
116:UserLoggedIn:=Bit_0;
117:XVH_AlarmOn:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:iPMM_VirA_Tok1:=Real_0;
4003:iPMM_VirA_Tok10:=Real_0;
4005:iPMM_VirA_Tok11:=Real_0;
4007:iPMM_VirA_Tok12:=Real_0;
4009:iPMM_VirA_Tok13:=Real_0;
4011:iPMM_VirA_Tok14:=Real_0;
4013:iPMM_VirA_Tok15:=Real_0;
4015:iPMM_VirA_Tok16:=Real_0;
4017:iPMM_VirA_Tok17:=Real_0;
4019:iPMM_VirA_Tok18:=Real_0;
4021:iPMM_VirA_Tok19:=Real_0;
4023:iPMM_VirA_Tok2:=Real_0;
4025:iPMM_VirA_Tok20:=Real_0;
4027:iPMM_VirA_Tok21:=Real_0;
4029:iPMM_VirA_Tok22:=Real_0;
4031:iPMM_VirA_Tok23:=Real_0;
4033:iPMM_VirA_Tok24:=Real_0;
4035:iPMM_VirA_Tok25:=Real_0;
4037:iPMM_VirA_Tok26:=Real_0;
4039:iPMM_VirA_Tok27:=Real_0;
4041:iPMM_VirA_Tok28:=Real_0;
4043:iPMM_VirA_Tok29:=Real_0;
4045:iPMM_VirA_Tok3:=Real_0;
4047:iPMM_VirA_Tok30:=Real_0;
4049:iPMM_VirA_Tok31:=Real_0;
4051:iPMM_VirA_Tok32:=Real_0;
4053:iPMM_VirA_Tok33:=Real_0;
4055:iPMM_VirA_Tok34:=Real_0;
4057:iPMM_VirA_Tok35:=Real_0;
4059:iPMM_VirA_Tok36:=Real_0;
4061:iPMM_VirA_Tok37:=Real_0;
4063:iPMM_VirA_Tok38:=Real_0;
4065:iPMM_VirA_Tok39:=Real_0;
4067:iPMM_VirA_Tok4:=Real_0;
4069:iPMM_VirA_Tok40:=Real_0;
4071:iPMM_VirA_Tok41:=Real_0;
4073:iPMM_VirA_Tok42:=Real_0;
4075:iPMM_VirA_Tok43:=Real_0;
4077:iPMM_VirA_Tok44:=Real_0;
4079:iPMM_VirA_Tok5:=Real_0;
4081:iPMM_VirA_Tok6:=Real_0;
4083:iPMM_VirA_Tok7:=Real_0;
4085:iPMM_VirA_Tok8:=Real_0;
4087:iPMM_VirA_Tok9:=Real_0;
4089:iPMM_VirB_Tok1:=Real_0;
4091:iPMM_VirB_Tok10:=Real_0;
4093:iPMM_VirB_Tok11:=Real_0;
4095:iPMM_VirB_Tok12:=Real_0;
4097:iPMM_VirB_Tok13:=Real_0;
4099:iPMM_VirB_Tok14:=Real_0;
4101:iPMM_VirB_Tok15:=Real_0;
4103:iPMM_VirB_Tok16:=Real_0;
4105:iPMM_VirB_Tok17:=Real_0;
4107:iPMM_VirB_Tok18:=Real_0;
4109:iPMM_VirB_Tok19:=Real_0;
4111:iPMM_VirB_Tok2:=Real_0;
4113:iPMM_VirB_Tok20:=Real_0;
4115:iPMM_VirB_Tok21:=Real_0;
4117:iPMM_VirB_Tok22:=Real_0;
4119:iPMM_VirB_Tok23:=Real_0;
4121:iPMM_VirB_Tok24:=Real_0;
4123:iPMM_VirB_Tok25:=Real_0;
4125:iPMM_VirB_Tok26:=Real_0;
4127:iPMM_VirB_Tok27:=Real_0;
4129:iPMM_VirB_Tok28:=Real_0;
4131:iPMM_VirB_Tok29:=Real_0;
4133:iPMM_VirB_Tok3:=Real_0;
4135:iPMM_VirB_Tok30:=Real_0;
4137:iPMM_VirB_Tok31:=Real_0;
4139:iPMM_VirB_Tok32:=Real_0;
4141:iPMM_VirB_Tok33:=Real_0;
4143:iPMM_VirB_Tok34:=Real_0;
4145:iPMM_VirB_Tok35:=Real_0;
4147:iPMM_VirB_Tok36:=Real_0;
4149:iPMM_VirB_Tok37:=Real_0;
4151:iPMM_VirB_Tok38:=Real_0;
4153:iPMM_VirB_Tok39:=Real_0;
4155:iPMM_VirB_Tok4:=Real_0;
4157:iPMM_VirB_Tok40:=Real_0;
4159:iPMM_VirB_Tok41:=Real_0;
4161:iPMM_VirB_Tok42:=Real_0;
4163:iPMM_VirB_Tok43:=Real_0;
4165:iPMM_VirB_Tok44:=Real_0;
4167:iPMM_VirB_Tok5:=Real_0;
4169:iPMM_VirB_Tok6:=Real_0;
4171:iPMM_VirB_Tok7:=Real_0;
4173:iPMM_VirB_Tok8:=Real_0;
4175:iPMM_VirB_Tok9:=Real_0;
4177:NSX[1].ActiveEnergy_kWh:=Real_0;
4179:NSX[1].ActiveNegativeEnergy_kWh:=Real_0;
4181:NSX[1].ActivePositiveEnergy_kWh:=Real_0;
4183:NSX[1].ActivePowerDemand_kW:=Real_0;
4185:NSX[1].ActivePowerL1_kW:=Real_0;
4187:NSX[1].ActivePowerL2_kW:=Real_0;
4189:NSX[1].ActivePowerL3_kW:=Real_0;
4191:NSX[1].ActivePowerMaxDemand_kW:=Real_0;
4193:NSX[1].ActivePowerTotal_kW:=Real_0;
4195:NSX[1].ApparentEnergy_kVAh:=Real_0;
4197:NSX[1].ApparentPowerDemand_kVA:=Real_0;
4199:NSX[1].ApparentPowerMaxDemand_kVA:=Real_0;
4201:NSX[1].ApparetnPowerL1_kVA:=Real_0;
4203:NSX[1].ApparetnPowerL2_kVA:=Real_0;
4205:NSX[1].ApparetnPowerL3_kVA:=Real_0;
4207:NSX[1].ApparetnPowerTotal_kVA:=Real_0;
4209:NSX[1].CosFL1:=Real_0;
4211:NSX[1].CosFL2:=Real_0;
4213:NSX[1].CosFL3:=Real_0;
4215:NSX[1].CosFTotal:=Real_0;
4217:NSX[1].CumulNegativeActiveEnergy_kWh:=Real_0;
4219:NSX[1].CumulPositiveActiveEnergy_kWh:=Real_0;
4221:NSX[1].CurrentAvgI1I2I3_A:=Real_0;
4223:NSX[1].CurrentDemandL1_A:=Real_0;
4225:NSX[1].CurrentDemandL2_A:=Real_0;
4227:NSX[1].CurrentDemandL3_A:=Real_0;
4229:NSX[1].CurrentDemandMaxL1_A:=Real_0;
4231:NSX[1].CurrentDemandMaxL2_A:=Real_0;
4233:NSX[1].CurrentDemandMaxL3_A:=Real_0;
4235:NSX[1].CurrentDemandMaxN_A:=Real_0;
4237:NSX[1].CurrentDemandN_A:=Real_0;
4239:NSX[1].CurrentL1_A:=Real_0;
4241:NSX[1].CurrentL2_A:=Real_0;
4243:NSX[1].CurrentL3_A:=Real_0;
4245:NSX[1].CurrentN_A:=Real_0;
4247:NSX[1].CurrentUnbI1_P:=Real_0;
4249:NSX[1].CurrentUnbI2_P:=Real_0;
4251:NSX[1].CurrentUnbI3_P:=Real_0;
4253:NSX[1].CurrentUnbN_P:=Real_0;
4255:NSX[1].DelovnaEnergija_TEMP:=Real_0;
4257:NSX[1].DistortionPowerL1_kVAr:=Real_0;
4259:NSX[1].DistortionPowerL2_kVAr:=Real_0;
4261:NSX[1].DistortionPowerL3_kVAr:=Real_0;
4263:NSX[1].DistortionPowerTotal_kVAr:=Real_0;
4265:NSX[1].Frequency_Hz:=Real_0;
4267:NSX[1].FunReactivePowerL1_kVAr:=Real_0;
4269:NSX[1].FunReactivePowerL2_kVAr:=Real_0;
4271:NSX[1].FunReactivePowerL3_kVAr:=Real_0;
4273:NSX[1].FunReactivePowerTotal_kVAr:=Real_0;
4275:NSX[1].MAX_ActivePowerL1_kW:=Real_0;
4277:NSX[1].MAX_ActivePowerL2_kW:=Real_0;
4279:NSX[1].MAX_ActivePowerL3_kW:=Real_0;
4281:NSX[1].MAX_ActivePowerTotal_kW:=Real_0;
4283:NSX[1].MAX_ApparetnPowerL1_kVA:=Real_0;
4285:NSX[1].MAX_ApparetnPowerL2_kVA:=Real_0;
4287:NSX[1].MAX_ApparetnPowerL3_kVA:=Real_0;
4289:NSX[1].MAX_ApparetnPowerTotal_kVA:=Real_0;
4291:NSX[1].MAX_CosFL1:=Real_0;
4293:NSX[1].MAX_CosFL2:=Real_0;
4295:NSX[1].MAX_CosFL3:=Real_0;
4297:NSX[1].MAX_CosFTotal:=Real_0;
4299:NSX[1].MAX_CurrentAvgI1I2I3_A:=Real_0;
4301:NSX[1].MAX_CurrentL1_A:=Real_0;
4303:NSX[1].MAX_CurrentL2_A:=Real_0;
4305:NSX[1].MAX_CurrentL3_A:=Real_0;
4307:NSX[1].MAX_CurrentMaxL1L2L3N_A:=Real_0;
4309:NSX[1].MAX_CurrentN_A:=Real_0;
4311:NSX[1].MAX_DistortionPowerL1_kVAr:=Real_0;
4313:NSX[1].MAX_DistortionPowerL2_kVAr:=Real_0;
4315:NSX[1].MAX_DistortionPowerL3_kVAr:=Real_0;
4317:NSX[1].MAX_DistortionPowerTotal_kVAr:=Real_0;
4319:NSX[1].MAX_Frequency_Hz:=Real_0;
4321:NSX[1].MAX_FunReactivePowerL1_kVAr:=Real_0;
4323:NSX[1].MAX_FunReactivePowerL2_kVAr:=Real_0;
4325:NSX[1].MAX_FunReactivePowerL3_kVAr:=Real_0;
4327:NSX[1].MAX_FunReactivePowerTotal_kVAr:=Real_0;
4329:NSX[1].MAX_PowerFactorL1:=Real_0;
4331:NSX[1].MAX_PowerFactorL2:=Real_0;
4333:NSX[1].MAX_PowerFactorL3:=Real_0;
4335:NSX[1].MAX_PowerFactorTotal:=Real_0;
4337:NSX[1].MAX_ReactivePowerL1_kVAr:=Real_0;
4339:NSX[1].MAX_ReactivePowerL2_kVAr:=Real_0;
4341:NSX[1].MAX_ReactivePowerL3_kVAr:=Real_0;
4343:NSX[1].MAX_ReactivePowerTotal_kVAr:=Real_0;
4345:NSX[1].MAX_THDI1_P:=Real_0;
4347:NSX[1].MAX_THDI2_P:=Real_0;
4349:NSX[1].MAX_THDI3_P:=Real_0;
4351:NSX[1].MAX_THDV12_P:=Real_0;
4353:NSX[1].MAX_THDV1N_P:=Real_0;
4355:NSX[1].MAX_THDV23_P:=Real_0;
4357:NSX[1].MAX_THDV2N_P:=Real_0;
4359:NSX[1].MAX_THDV31_P:=Real_0;
4361:NSX[1].MAX_THDV3N_P:=Real_0;
4363:NSX[1].MAX_VoltageAvgPhToN_V:=Real_0;
4365:NSX[1].MAX_VoltageAvgPhToPh_V:=Real_0;
4367:NSX[1].MAX_VoltageUnbV12_P:=Real_0;
4369:NSX[1].MAX_VoltageUnbV1N_P:=Real_0;
4371:NSX[1].MAX_VoltageUnbV23_P:=Real_0;
4373:NSX[1].MAX_VoltageUnbV2N_P:=Real_0;
4375:NSX[1].MAX_VoltageUnbV31_P:=Real_0;
4377:NSX[1].MAX_VoltageUnbV3N_P:=Real_0;
4379:NSX[1].MAX_VoltageV12_V:=Real_0;
4381:NSX[1].MAX_VoltageV1N_V:=Real_0;
4383:NSX[1].MAX_VoltageV23_V:=Real_0;
4385:NSX[1].MAX_VoltageV2N_V:=Real_0;
4387:NSX[1].MAX_VoltageV31_V:=Real_0;
4389:NSX[1].MAX_VoltageV3N_V:=Real_0;
4391:NSX[1].MIN_ActivePowerL1_kW:=Real_0;
4393:NSX[1].MIN_ActivePowerL2_kW:=Real_0;
4395:NSX[1].MIN_ActivePowerL3_kW:=Real_0;
4397:NSX[1].MIN_ActivePowerTotal_kW:=Real_0;
4399:NSX[1].MIN_ApparetnPowerL1_kVA:=Real_0;
4401:NSX[1].MIN_ApparetnPowerL2_kVA:=Real_0;
4403:NSX[1].MIN_ApparetnPowerL3_kVA:=Real_0;
4405:NSX[1].MIN_ApparetnPowerTotal_kVA:=Real_0;
4407:NSX[1].MIN_CosFL1:=Real_0;
4409:NSX[1].MIN_CosFL2:=Real_0;
4411:NSX[1].MIN_CosFL3:=Real_0;
4413:NSX[1].MIN_CosFTotal:=Real_0;
4415:NSX[1].MIN_CurrentAvgI1I2I3_A:=Real_0;
4417:NSX[1].MIN_CurrentL1_A:=Real_0;
4419:NSX[1].MIN_CurrentL2_A:=Real_0;
4421:NSX[1].MIN_CurrentL3_A:=Real_0;
4423:NSX[1].MIN_CurrentMaxL1L2L3N_A:=Real_0;
4425:NSX[1].MIN_CurrentN_A:=Real_0;
4427:NSX[1].MIN_DistortionPowerL1_kVAr:=Real_0;
4429:NSX[1].MIN_DistortionPowerL2_kVAr:=Real_0;
4431:NSX[1].MIN_DistortionPowerL3_kVAr:=Real_0;
4433:NSX[1].MIN_DistortionPowerTotal_kVAr:=Real_0;
4435:NSX[1].MIN_Frequency_Hz:=Real_0;
4437:NSX[1].MIN_FunReactivePowerL1_kVAr:=Real_0;
4439:NSX[1].MIN_FunReactivePowerL2_kVAr:=Real_0;
4441:NSX[1].MIN_FunReactivePowerL3_kVAr:=Real_0;
4443:NSX[1].MIN_FunReactivePowerTotal_kVAr:=Real_0;
4445:NSX[1].MIN_PowerFactorL1:=Real_0;
4447:NSX[1].MIN_PowerFactorL2:=Real_0;
4449:NSX[1].MIN_PowerFactorL3:=Real_0;
4451:NSX[1].MIN_PowerFactorTotal:=Real_0;
4453:NSX[1].MIN_ReactivePowerL1_kVAr:=Real_0;
4455:NSX[1].MIN_ReactivePowerL2_kVAr:=Real_0;
4457:NSX[1].MIN_ReactivePowerL3_kVAr:=Real_0;
4459:NSX[1].MIN_ReactivePowerTotal_kVAr:=Real_0;
4461:NSX[1].MIN_THDI1_P:=Real_0;
4463:NSX[1].MIN_THDI2_P:=Real_0;
4465:NSX[1].MIN_THDI3_P:=Real_0;
4467:NSX[1].MIN_THDV12_P:=Real_0;
4469:NSX[1].MIN_THDV1N_P:=Real_0;
4471:NSX[1].MIN_THDV23_P:=Real_0;
4473:NSX[1].MIN_THDV2N_P:=Real_0;
4475:NSX[1].MIN_THDV31_P:=Real_0;
4477:NSX[1].MIN_THDV3N_P:=Real_0;
4479:NSX[1].MIN_VoltageAvgPhToN_V:=Real_0;
4481:NSX[1].MIN_VoltageAvgPhToPh_V:=Real_0;
4483:NSX[1].MIN_VoltageUnbV12_P:=Real_0;
4485:NSX[1].MIN_VoltageUnbV1N_P:=Real_0;
4487:NSX[1].MIN_VoltageUnbV23_P:=Real_0;
4489:NSX[1].MIN_VoltageUnbV2N_P:=Real_0;
4491:NSX[1].MIN_VoltageUnbV31_P:=Real_0;
4493:NSX[1].MIN_VoltageUnbV3N_P:=Real_0;
4495:NSX[1].MIN_VoltageV12_V:=Real_0;
4497:NSX[1].MIN_VoltageV1N_V:=Real_0;
4499:NSX[1].MIN_VoltageV23_V:=Real_0;
4501:NSX[1].MIN_VoltageV2N_V:=Real_0;
4503:NSX[1].MIN_VoltageV31_V:=Real_0;
4505:NSX[1].MIN_VoltageV3N_V:=Real_0;
4507:NSX[1].PowerFactorL1:=Real_0;
4509:NSX[1].PowerFactorL2:=Real_0;
4511:NSX[1].PowerFactorL3:=Real_0;
4513:NSX[1].PowerFactorTotal:=Real_0;
4515:NSX[1].RazEner_D:=Real_0;
4517:NSX[1].RazEner_D_SCADA:=Real_0;
4519:NSX[1].RazEner_D_TEMP:=Real_0;
4521:NSX[1].RazEner_M:=Real_0;
4523:NSX[1].RazEner_M_SCADA:=Real_0;
4525:NSX[1].RazEner_M_TEMP:=Real_0;
4527:NSX[1].RazEner_T:=Real_0;
4529:NSX[1].RazEner_T_SCADA:=Real_0;
4531:NSX[1].RazEner_T_TEMP:=Real_0;
4533:NSX[1].ReactiveEnergy_kVArh:=Real_0;
4535:NSX[1].ReactiveNegativeEnergy_kVArh:=Real_0;
4537:NSX[1].ReactivePositiveEnergy_kVArh:=Real_0;
4539:NSX[1].ReactivePowerDemand_kVAr:=Real_0;
4541:NSX[1].ReactivePowerL1_kVAr:=Real_0;
4543:NSX[1].ReactivePowerL2_kVAr:=Real_0;
4545:NSX[1].ReactivePowerL3_kVAr:=Real_0;
4547:NSX[1].ReactivePowerMaxDemand_kVAr:=Real_0;
4549:NSX[1].ReactivePowerTotal_kVAr:=Real_0;
4551:NSX[1].THDI1_P:=Real_0;
4553:NSX[1].THDI2_P:=Real_0;
4555:NSX[1].THDI3_P:=Real_0;
4557:NSX[1].THDV12_P:=Real_0;
4559:NSX[1].THDV1N_P:=Real_0;
4561:NSX[1].THDV23_P:=Real_0;
4563:NSX[1].THDV2N_P:=Real_0;
4565:NSX[1].THDV31_P:=Real_0;
4567:NSX[1].THDV3N_P:=Real_0;
4569:NSX[1].VoltageAvgPhToN_V:=Real_0;
4571:NSX[1].VoltageAvgPhToPh_V:=Real_0;
4573:NSX[1].VoltageUnbV12_P:=Real_0;
4575:NSX[1].VoltageUnbV1N_P:=Real_0;
4577:NSX[1].VoltageUnbV23_P:=Real_0;
4579:NSX[1].VoltageUnbV2N_P:=Real_0;
4581:NSX[1].VoltageUnbV31_P:=Real_0;
4583:NSX[1].VoltageUnbV3N_P:=Real_0;
4585:NSX[1].VoltageV12_V:=Real_0;
4587:NSX[1].VoltageV1N_V:=Real_0;
4589:NSX[1].VoltageV23_V:=Real_0;
4591:NSX[1].VoltageV2N_V:=Real_0;
4593:NSX[1].VoltageV31_V:=Real_0;
4595:NSX[1].VoltageV3N_V:=Real_0;
4597:NSX[2].ActiveEnergy_kWh:=Real_0;
4599:NSX[2].ActiveNegativeEnergy_kWh:=Real_0;
4601:NSX[2].ActivePositiveEnergy_kWh:=Real_0;
4603:NSX[2].ActivePowerDemand_kW:=Real_0;
4605:NSX[2].ActivePowerL1_kW:=Real_0;
4607:NSX[2].ActivePowerL2_kW:=Real_0;
4609:NSX[2].ActivePowerL3_kW:=Real_0;
4611:NSX[2].ActivePowerMaxDemand_kW:=Real_0;
4613:NSX[2].ActivePowerTotal_kW:=Real_0;
4615:NSX[2].ApparentEnergy_kVAh:=Real_0;
4617:NSX[2].ApparentPowerDemand_kVA:=Real_0;
4619:NSX[2].ApparentPowerMaxDemand_kVA:=Real_0;
4621:NSX[2].ApparetnPowerL1_kVA:=Real_0;
4623:NSX[2].ApparetnPowerL2_kVA:=Real_0;
4625:NSX[2].ApparetnPowerL3_kVA:=Real_0;
4627:NSX[2].ApparetnPowerTotal_kVA:=Real_0;
4629:NSX[2].CosFL1:=Real_0;
4631:NSX[2].CosFL2:=Real_0;
4633:NSX[2].CosFL3:=Real_0;
4635:NSX[2].CosFTotal:=Real_0;
4637:NSX[2].CumulNegativeActiveEnergy_kWh:=Real_0;
4639:NSX[2].CumulPositiveActiveEnergy_kWh:=Real_0;
4641:NSX[2].CurrentAvgI1I2I3_A:=Real_0;
4643:NSX[2].CurrentDemandL1_A:=Real_0;
4645:NSX[2].CurrentDemandL2_A:=Real_0;
4647:NSX[2].CurrentDemandL3_A:=Real_0;
4649:NSX[2].CurrentDemandMaxL1_A:=Real_0;
4651:NSX[2].CurrentDemandMaxL2_A:=Real_0;
4653:NSX[2].CurrentDemandMaxL3_A:=Real_0;
4655:NSX[2].CurrentDemandMaxN_A:=Real_0;
4657:NSX[2].CurrentDemandN_A:=Real_0;
4659:NSX[2].CurrentL1_A:=Real_0;
4661:NSX[2].CurrentL2_A:=Real_0;
4663:NSX[2].CurrentL3_A:=Real_0;
4665:NSX[2].CurrentN_A:=Real_0;
4667:NSX[2].CurrentUnbI1_P:=Real_0;
4669:NSX[2].CurrentUnbI2_P:=Real_0;
4671:NSX[2].CurrentUnbI3_P:=Real_0;
4673:NSX[2].CurrentUnbN_P:=Real_0;
4675:NSX[2].DelovnaEnergija_TEMP:=Real_0;
4677:NSX[2].DistortionPowerL1_kVAr:=Real_0;
4679:NSX[2].DistortionPowerL2_kVAr:=Real_0;
4681:NSX[2].DistortionPowerL3_kVAr:=Real_0;
4683:NSX[2].DistortionPowerTotal_kVAr:=Real_0;
4685:NSX[2].Frequency_Hz:=Real_0;
4687:NSX[2].FunReactivePowerL1_kVAr:=Real_0;
4689:NSX[2].FunReactivePowerL2_kVAr:=Real_0;
4691:NSX[2].FunReactivePowerL3_kVAr:=Real_0;
4693:NSX[2].FunReactivePowerTotal_kVAr:=Real_0;
4695:NSX[2].MAX_ActivePowerL1_kW:=Real_0;
4697:NSX[2].MAX_ActivePowerL2_kW:=Real_0;
4699:NSX[2].MAX_ActivePowerL3_kW:=Real_0;
4701:NSX[2].MAX_ActivePowerTotal_kW:=Real_0;
4703:NSX[2].MAX_ApparetnPowerL1_kVA:=Real_0;
4705:NSX[2].MAX_ApparetnPowerL2_kVA:=Real_0;
4707:NSX[2].MAX_ApparetnPowerL3_kVA:=Real_0;
4709:NSX[2].MAX_ApparetnPowerTotal_kVA:=Real_0;
4711:NSX[2].MAX_CosFL1:=Real_0;
4713:NSX[2].MAX_CosFL2:=Real_0;
4715:NSX[2].MAX_CosFL3:=Real_0;
4717:NSX[2].MAX_CosFTotal:=Real_0;
4719:NSX[2].MAX_CurrentAvgI1I2I3_A:=Real_0;
4721:NSX[2].MAX_CurrentL1_A:=Real_0;
4723:NSX[2].MAX_CurrentL2_A:=Real_0;
4725:NSX[2].MAX_CurrentL3_A:=Real_0;
4727:NSX[2].MAX_CurrentMaxL1L2L3N_A:=Real_0;
4729:NSX[2].MAX_CurrentN_A:=Real_0;
4731:NSX[2].MAX_DistortionPowerL1_kVAr:=Real_0;
4733:NSX[2].MAX_DistortionPowerL2_kVAr:=Real_0;
4735:NSX[2].MAX_DistortionPowerL3_kVAr:=Real_0;
4737:NSX[2].MAX_DistortionPowerTotal_kVAr:=Real_0;
4739:NSX[2].MAX_Frequency_Hz:=Real_0;
4741:NSX[2].MAX_FunReactivePowerL1_kVAr:=Real_0;
4743:NSX[2].MAX_FunReactivePowerL2_kVAr:=Real_0;
4745:NSX[2].MAX_FunReactivePowerL3_kVAr:=Real_0;
4747:NSX[2].MAX_FunReactivePowerTotal_kVAr:=Real_0;
4749:NSX[2].MAX_PowerFactorL1:=Real_0;
4751:NSX[2].MAX_PowerFactorL2:=Real_0;
4753:NSX[2].MAX_PowerFactorL3:=Real_0;
4755:NSX[2].MAX_PowerFactorTotal:=Real_0;
4757:NSX[2].MAX_ReactivePowerL1_kVAr:=Real_0;
4759:NSX[2].MAX_ReactivePowerL2_kVAr:=Real_0;
4761:NSX[2].MAX_ReactivePowerL3_kVAr:=Real_0;
4763:NSX[2].MAX_ReactivePowerTotal_kVAr:=Real_0;
4765:NSX[2].MAX_THDI1_P:=Real_0;
4767:NSX[2].MAX_THDI2_P:=Real_0;
4769:NSX[2].MAX_THDI3_P:=Real_0;
4771:NSX[2].MAX_THDV12_P:=Real_0;
4773:NSX[2].MAX_THDV1N_P:=Real_0;
4775:NSX[2].MAX_THDV23_P:=Real_0;
4777:NSX[2].MAX_THDV2N_P:=Real_0;
4779:NSX[2].MAX_THDV31_P:=Real_0;
4781:NSX[2].MAX_THDV3N_P:=Real_0;
4783:NSX[2].MAX_VoltageAvgPhToN_V:=Real_0;
4785:NSX[2].MAX_VoltageAvgPhToPh_V:=Real_0;
4787:NSX[2].MAX_VoltageUnbV12_P:=Real_0;
4789:NSX[2].MAX_VoltageUnbV1N_P:=Real_0;
4791:NSX[2].MAX_VoltageUnbV23_P:=Real_0;
4793:NSX[2].MAX_VoltageUnbV2N_P:=Real_0;
4795:NSX[2].MAX_VoltageUnbV31_P:=Real_0;
4797:NSX[2].MAX_VoltageUnbV3N_P:=Real_0;
4799:NSX[2].MAX_VoltageV12_V:=Real_0;
4801:NSX[2].MAX_VoltageV1N_V:=Real_0;
4803:NSX[2].MAX_VoltageV23_V:=Real_0;
4805:NSX[2].MAX_VoltageV2N_V:=Real_0;
4807:NSX[2].MAX_VoltageV31_V:=Real_0;
4809:NSX[2].MAX_VoltageV3N_V:=Real_0;
4811:NSX[2].MIN_ActivePowerL1_kW:=Real_0;
4813:NSX[2].MIN_ActivePowerL2_kW:=Real_0;
4815:NSX[2].MIN_ActivePowerL3_kW:=Real_0;
4817:NSX[2].MIN_ActivePowerTotal_kW:=Real_0;
4819:NSX[2].MIN_ApparetnPowerL1_kVA:=Real_0;
4821:NSX[2].MIN_ApparetnPowerL2_kVA:=Real_0;
4823:NSX[2].MIN_ApparetnPowerL3_kVA:=Real_0;
4825:NSX[2].MIN_ApparetnPowerTotal_kVA:=Real_0;
4827:NSX[2].MIN_CosFL1:=Real_0;
4829:NSX[2].MIN_CosFL2:=Real_0;
4831:NSX[2].MIN_CosFL3:=Real_0;
4833:NSX[2].MIN_CosFTotal:=Real_0;
4835:NSX[2].MIN_CurrentAvgI1I2I3_A:=Real_0;
4837:NSX[2].MIN_CurrentL1_A:=Real_0;
4839:NSX[2].MIN_CurrentL2_A:=Real_0;
4841:NSX[2].MIN_CurrentL3_A:=Real_0;
4843:NSX[2].MIN_CurrentMaxL1L2L3N_A:=Real_0;
4845:NSX[2].MIN_CurrentN_A:=Real_0;
4847:NSX[2].MIN_DistortionPowerL1_kVAr:=Real_0;
4849:NSX[2].MIN_DistortionPowerL2_kVAr:=Real_0;
4851:NSX[2].MIN_DistortionPowerL3_kVAr:=Real_0;
4853:NSX[2].MIN_DistortionPowerTotal_kVAr:=Real_0;
4855:NSX[2].MIN_Frequency_Hz:=Real_0;
4857:NSX[2].MIN_FunReactivePowerL1_kVAr:=Real_0;
4859:NSX[2].MIN_FunReactivePowerL2_kVAr:=Real_0;
4861:NSX[2].MIN_FunReactivePowerL3_kVAr:=Real_0;
4863:NSX[2].MIN_FunReactivePowerTotal_kVAr:=Real_0;
4865:NSX[2].MIN_PowerFactorL1:=Real_0;
4867:NSX[2].MIN_PowerFactorL2:=Real_0;
4869:NSX[2].MIN_PowerFactorL3:=Real_0;
4871:NSX[2].MIN_PowerFactorTotal:=Real_0;
4873:NSX[2].MIN_ReactivePowerL1_kVAr:=Real_0;
4875:NSX[2].MIN_ReactivePowerL2_kVAr:=Real_0;
4877:NSX[2].MIN_ReactivePowerL3_kVAr:=Real_0;
4879:NSX[2].MIN_ReactivePowerTotal_kVAr:=Real_0;
4881:NSX[2].MIN_THDI1_P:=Real_0;
4883:NSX[2].MIN_THDI2_P:=Real_0;
4885:NSX[2].MIN_THDI3_P:=Real_0;
4887:NSX[2].MIN_THDV12_P:=Real_0;
4889:NSX[2].MIN_THDV1N_P:=Real_0;
4891:NSX[2].MIN_THDV23_P:=Real_0;
4893:NSX[2].MIN_THDV2N_P:=Real_0;
4895:NSX[2].MIN_THDV31_P:=Real_0;
4897:NSX[2].MIN_THDV3N_P:=Real_0;
4899:NSX[2].MIN_VoltageAvgPhToN_V:=Real_0;
4901:NSX[2].MIN_VoltageAvgPhToPh_V:=Real_0;
4903:NSX[2].MIN_VoltageUnbV12_P:=Real_0;
4905:NSX[2].MIN_VoltageUnbV1N_P:=Real_0;
4907:NSX[2].MIN_VoltageUnbV23_P:=Real_0;
4909:NSX[2].MIN_VoltageUnbV2N_P:=Real_0;
4911:NSX[2].MIN_VoltageUnbV31_P:=Real_0;
4913:NSX[2].MIN_VoltageUnbV3N_P:=Real_0;
4915:NSX[2].MIN_VoltageV12_V:=Real_0;
4917:NSX[2].MIN_VoltageV1N_V:=Real_0;
4919:NSX[2].MIN_VoltageV23_V:=Real_0;
4921:NSX[2].MIN_VoltageV2N_V:=Real_0;
4923:NSX[2].MIN_VoltageV31_V:=Real_0;
4925:NSX[2].MIN_VoltageV3N_V:=Real_0;
4927:NSX[2].PowerFactorL1:=Real_0;
4929:NSX[2].PowerFactorL2:=Real_0;
4931:NSX[2].PowerFactorL3:=Real_0;
4933:NSX[2].PowerFactorTotal:=Real_0;
4935:NSX[2].RazEner_D:=Real_0;
4937:NSX[2].RazEner_D_SCADA:=Real_0;
4939:NSX[2].RazEner_D_TEMP:=Real_0;
4941:NSX[2].RazEner_M:=Real_0;
4943:NSX[2].RazEner_M_SCADA:=Real_0;
4945:NSX[2].RazEner_M_TEMP:=Real_0;
4947:NSX[2].RazEner_T:=Real_0;
4949:NSX[2].RazEner_T_SCADA:=Real_0;
4951:NSX[2].RazEner_T_TEMP:=Real_0;
4953:NSX[2].ReactiveEnergy_kVArh:=Real_0;
4955:NSX[2].ReactiveNegativeEnergy_kVArh:=Real_0;
4957:NSX[2].ReactivePositiveEnergy_kVArh:=Real_0;
4959:NSX[2].ReactivePowerDemand_kVAr:=Real_0;
4961:NSX[2].ReactivePowerL1_kVAr:=Real_0;
4963:NSX[2].ReactivePowerL2_kVAr:=Real_0;
4965:NSX[2].ReactivePowerL3_kVAr:=Real_0;
4967:NSX[2].ReactivePowerMaxDemand_kVAr:=Real_0;
4969:NSX[2].ReactivePowerTotal_kVAr:=Real_0;
4971:NSX[2].THDI1_P:=Real_0;
4973:NSX[2].THDI2_P:=Real_0;
4975:NSX[2].THDI3_P:=Real_0;
4977:NSX[2].THDV12_P:=Real_0;
4979:NSX[2].THDV1N_P:=Real_0;
4981:NSX[2].THDV23_P:=Real_0;
4983:NSX[2].THDV2N_P:=Real_0;
4985:NSX[2].THDV31_P:=Real_0;
4987:NSX[2].THDV3N_P:=Real_0;
4989:NSX[2].VoltageAvgPhToN_V:=Real_0;
4991:NSX[2].VoltageAvgPhToPh_V:=Real_0;
4993:NSX[2].VoltageUnbV12_P:=Real_0;
4995:NSX[2].VoltageUnbV1N_P:=Real_0;
4997:NSX[2].VoltageUnbV23_P:=Real_0;
4999:NSX[2].VoltageUnbV2N_P:=Real_0;
5001:NSX[2].VoltageUnbV31_P:=Real_0;
5003:NSX[2].VoltageUnbV3N_P:=Real_0;
5005:NSX[2].VoltageV12_V:=Real_0;
5007:NSX[2].VoltageV1N_V:=Real_0;
5009:NSX[2].VoltageV23_V:=Real_0;
5011:NSX[2].VoltageV2N_V:=Real_0;
5013:NSX[2].VoltageV31_V:=Real_0;
5015:NSX[2].VoltageV3N_V:=Real_0;
5017:NSX[3].ActiveEnergy_kWh:=Real_0;
5019:NSX[3].ActiveNegativeEnergy_kWh:=Real_0;
5021:NSX[3].ActivePositiveEnergy_kWh:=Real_0;
5023:NSX[3].ActivePowerDemand_kW:=Real_0;
5025:NSX[3].ActivePowerL1_kW:=Real_0;
5027:NSX[3].ActivePowerL2_kW:=Real_0;
5029:NSX[3].ActivePowerL3_kW:=Real_0;
5031:NSX[3].ActivePowerMaxDemand_kW:=Real_0;
5033:NSX[3].ActivePowerTotal_kW:=Real_0;
5035:NSX[3].ApparentEnergy_kVAh:=Real_0;
5037:NSX[3].ApparentPowerDemand_kVA:=Real_0;
5039:NSX[3].ApparentPowerMaxDemand_kVA:=Real_0;
5041:NSX[3].ApparetnPowerL1_kVA:=Real_0;
5043:NSX[3].ApparetnPowerL2_kVA:=Real_0;
5045:NSX[3].ApparetnPowerL3_kVA:=Real_0;
5047:NSX[3].ApparetnPowerTotal_kVA:=Real_0;
5049:NSX[3].CosFL1:=Real_0;
5051:NSX[3].CosFL2:=Real_0;
5053:NSX[3].CosFL3:=Real_0;
5055:NSX[3].CosFTotal:=Real_0;
5057:NSX[3].CumulNegativeActiveEnergy_kWh:=Real_0;
5059:NSX[3].CumulPositiveActiveEnergy_kWh:=Real_0;
5061:NSX[3].CurrentAvgI1I2I3_A:=Real_0;
5063:NSX[3].CurrentDemandL1_A:=Real_0;
5065:NSX[3].CurrentDemandL2_A:=Real_0;
5067:NSX[3].CurrentDemandL3_A:=Real_0;
5069:NSX[3].CurrentDemandMaxL1_A:=Real_0;
5071:NSX[3].CurrentDemandMaxL2_A:=Real_0;
5073:NSX[3].CurrentDemandMaxL3_A:=Real_0;
5075:NSX[3].CurrentDemandMaxN_A:=Real_0;
5077:NSX[3].CurrentDemandN_A:=Real_0;
5079:NSX[3].CurrentL1_A:=Real_0;
5081:NSX[3].CurrentL2_A:=Real_0;
5083:NSX[3].CurrentL3_A:=Real_0;
5085:NSX[3].CurrentN_A:=Real_0;
5087:NSX[3].CurrentUnbI1_P:=Real_0;
5089:NSX[3].CurrentUnbI2_P:=Real_0;
5091:NSX[3].CurrentUnbI3_P:=Real_0;
5093:NSX[3].CurrentUnbN_P:=Real_0;
5095:NSX[3].DelovnaEnergija_TEMP:=Real_0;
5097:NSX[3].DistortionPowerL1_kVAr:=Real_0;
5099:NSX[3].DistortionPowerL2_kVAr:=Real_0;
5101:NSX[3].DistortionPowerL3_kVAr:=Real_0;
5103:NSX[3].DistortionPowerTotal_kVAr:=Real_0;
5105:NSX[3].Frequency_Hz:=Real_0;
5107:NSX[3].FunReactivePowerL1_kVAr:=Real_0;
5109:NSX[3].FunReactivePowerL2_kVAr:=Real_0;
5111:NSX[3].FunReactivePowerL3_kVAr:=Real_0;
5113:NSX[3].FunReactivePowerTotal_kVAr:=Real_0;
5115:NSX[3].MAX_ActivePowerL1_kW:=Real_0;
5117:NSX[3].MAX_ActivePowerL2_kW:=Real_0;
5119:NSX[3].MAX_ActivePowerL3_kW:=Real_0;
5121:NSX[3].MAX_ActivePowerTotal_kW:=Real_0;
5123:NSX[3].MAX_ApparetnPowerL1_kVA:=Real_0;
5125:NSX[3].MAX_ApparetnPowerL2_kVA:=Real_0;
5127:NSX[3].MAX_ApparetnPowerL3_kVA:=Real_0;
5129:NSX[3].MAX_ApparetnPowerTotal_kVA:=Real_0;
5131:NSX[3].MAX_CosFL1:=Real_0;
5133:NSX[3].MAX_CosFL2:=Real_0;
5135:NSX[3].MAX_CosFL3:=Real_0;
5137:NSX[3].MAX_CosFTotal:=Real_0;
5139:NSX[3].MAX_CurrentAvgI1I2I3_A:=Real_0;
5141:NSX[3].MAX_CurrentL1_A:=Real_0;
5143:NSX[3].MAX_CurrentL2_A:=Real_0;
5145:NSX[3].MAX_CurrentL3_A:=Real_0;
5147:NSX[3].MAX_CurrentMaxL1L2L3N_A:=Real_0;
5149:NSX[3].MAX_CurrentN_A:=Real_0;
5151:NSX[3].MAX_DistortionPowerL1_kVAr:=Real_0;
5153:NSX[3].MAX_DistortionPowerL2_kVAr:=Real_0;
5155:NSX[3].MAX_DistortionPowerL3_kVAr:=Real_0;
5157:NSX[3].MAX_DistortionPowerTotal_kVAr:=Real_0;
5159:NSX[3].MAX_Frequency_Hz:=Real_0;
5161:NSX[3].MAX_FunReactivePowerL1_kVAr:=Real_0;
5163:NSX[3].MAX_FunReactivePowerL2_kVAr:=Real_0;
5165:NSX[3].MAX_FunReactivePowerL3_kVAr:=Real_0;
5167:NSX[3].MAX_FunReactivePowerTotal_kVAr:=Real_0;
5169:NSX[3].MAX_PowerFactorL1:=Real_0;
5171:NSX[3].MAX_PowerFactorL2:=Real_0;
5173:NSX[3].MAX_PowerFactorL3:=Real_0;
5175:NSX[3].MAX_PowerFactorTotal:=Real_0;
5177:NSX[3].MAX_ReactivePowerL1_kVAr:=Real_0;
5179:NSX[3].MAX_ReactivePowerL2_kVAr:=Real_0;
5181:NSX[3].MAX_ReactivePowerL3_kVAr:=Real_0;
5183:NSX[3].MAX_ReactivePowerTotal_kVAr:=Real_0;
5185:NSX[3].MAX_THDI1_P:=Real_0;
5187:NSX[3].MAX_THDI2_P:=Real_0;
5189:NSX[3].MAX_THDI3_P:=Real_0;
5191:NSX[3].MAX_THDV12_P:=Real_0;
5193:NSX[3].MAX_THDV1N_P:=Real_0;
5195:NSX[3].MAX_THDV23_P:=Real_0;
5197:NSX[3].MAX_THDV2N_P:=Real_0;
5199:NSX[3].MAX_THDV31_P:=Real_0;
5201:NSX[3].MAX_THDV3N_P:=Real_0;
5203:NSX[3].MAX_VoltageAvgPhToN_V:=Real_0;
5205:NSX[3].MAX_VoltageAvgPhToPh_V:=Real_0;
5207:NSX[3].MAX_VoltageUnbV12_P:=Real_0;
5209:NSX[3].MAX_VoltageUnbV1N_P:=Real_0;
5211:NSX[3].MAX_VoltageUnbV23_P:=Real_0;
5213:NSX[3].MAX_VoltageUnbV2N_P:=Real_0;
5215:NSX[3].MAX_VoltageUnbV31_P:=Real_0;
5217:NSX[3].MAX_VoltageUnbV3N_P:=Real_0;
5219:NSX[3].MAX_VoltageV12_V:=Real_0;
5221:NSX[3].MAX_VoltageV1N_V:=Real_0;
5223:NSX[3].MAX_VoltageV23_V:=Real_0;
5225:NSX[3].MAX_VoltageV2N_V:=Real_0;
5227:NSX[3].MAX_VoltageV31_V:=Real_0;
5229:NSX[3].MAX_VoltageV3N_V:=Real_0;
5231:NSX[3].MIN_ActivePowerL1_kW:=Real_0;
5233:NSX[3].MIN_ActivePowerL2_kW:=Real_0;
5235:NSX[3].MIN_ActivePowerL3_kW:=Real_0;
5237:NSX[3].MIN_ActivePowerTotal_kW:=Real_0;
5239:NSX[3].MIN_ApparetnPowerL1_kVA:=Real_0;
5241:NSX[3].MIN_ApparetnPowerL2_kVA:=Real_0;
5243:NSX[3].MIN_ApparetnPowerL3_kVA:=Real_0;
5245:NSX[3].MIN_ApparetnPowerTotal_kVA:=Real_0;
5247:NSX[3].MIN_CosFL1:=Real_0;
5249:NSX[3].MIN_CosFL2:=Real_0;
5251:NSX[3].MIN_CosFL3:=Real_0;
5253:NSX[3].MIN_CosFTotal:=Real_0;
5255:NSX[3].MIN_CurrentAvgI1I2I3_A:=Real_0;
5257:NSX[3].MIN_CurrentL1_A:=Real_0;
5259:NSX[3].MIN_CurrentL2_A:=Real_0;
5261:NSX[3].MIN_CurrentL3_A:=Real_0;
5263:NSX[3].MIN_CurrentMaxL1L2L3N_A:=Real_0;
5265:NSX[3].MIN_CurrentN_A:=Real_0;
5267:NSX[3].MIN_DistortionPowerL1_kVAr:=Real_0;
5269:NSX[3].MIN_DistortionPowerL2_kVAr:=Real_0;
5271:NSX[3].MIN_DistortionPowerL3_kVAr:=Real_0;
5273:NSX[3].MIN_DistortionPowerTotal_kVAr:=Real_0;
5275:NSX[3].MIN_Frequency_Hz:=Real_0;
5277:NSX[3].MIN_FunReactivePowerL1_kVAr:=Real_0;
5279:NSX[3].MIN_FunReactivePowerL2_kVAr:=Real_0;
5281:NSX[3].MIN_FunReactivePowerL3_kVAr:=Real_0;
5283:NSX[3].MIN_FunReactivePowerTotal_kVAr:=Real_0;
5285:NSX[3].MIN_PowerFactorL1:=Real_0;
5287:NSX[3].MIN_PowerFactorL2:=Real_0;
5289:NSX[3].MIN_PowerFactorL3:=Real_0;
5291:NSX[3].MIN_PowerFactorTotal:=Real_0;
5293:NSX[3].MIN_ReactivePowerL1_kVAr:=Real_0;
5295:NSX[3].MIN_ReactivePowerL2_kVAr:=Real_0;
5297:NSX[3].MIN_ReactivePowerL3_kVAr:=Real_0;
5299:NSX[3].MIN_ReactivePowerTotal_kVAr:=Real_0;
5301:NSX[3].MIN_THDI1_P:=Real_0;
5303:NSX[3].MIN_THDI2_P:=Real_0;
5305:NSX[3].MIN_THDI3_P:=Real_0;
5307:NSX[3].MIN_THDV12_P:=Real_0;
5309:NSX[3].MIN_THDV1N_P:=Real_0;
5311:NSX[3].MIN_THDV23_P:=Real_0;
5313:NSX[3].MIN_THDV2N_P:=Real_0;
5315:NSX[3].MIN_THDV31_P:=Real_0;
5317:NSX[3].MIN_THDV3N_P:=Real_0;
5319:NSX[3].MIN_VoltageAvgPhToN_V:=Real_0;
5321:NSX[3].MIN_VoltageAvgPhToPh_V:=Real_0;
5323:NSX[3].MIN_VoltageUnbV12_P:=Real_0;
5325:NSX[3].MIN_VoltageUnbV1N_P:=Real_0;
5327:NSX[3].MIN_VoltageUnbV23_P:=Real_0;
5329:NSX[3].MIN_VoltageUnbV2N_P:=Real_0;
5331:NSX[3].MIN_VoltageUnbV31_P:=Real_0;
5333:NSX[3].MIN_VoltageUnbV3N_P:=Real_0;
5335:NSX[3].MIN_VoltageV12_V:=Real_0;
5337:NSX[3].MIN_VoltageV1N_V:=Real_0;
5339:NSX[3].MIN_VoltageV23_V:=Real_0;
5341:NSX[3].MIN_VoltageV2N_V:=Real_0;
5343:NSX[3].MIN_VoltageV31_V:=Real_0;
5345:NSX[3].MIN_VoltageV3N_V:=Real_0;
5347:NSX[3].PowerFactorL1:=Real_0;
5349:NSX[3].PowerFactorL2:=Real_0;
5351:NSX[3].PowerFactorL3:=Real_0;
5353:NSX[3].PowerFactorTotal:=Real_0;
5355:NSX[3].RazEner_D:=Real_0;
5357:NSX[3].RazEner_D_SCADA:=Real_0;
5359:NSX[3].RazEner_D_TEMP:=Real_0;
5361:NSX[3].RazEner_M:=Real_0;
5363:NSX[3].RazEner_M_SCADA:=Real_0;
5365:NSX[3].RazEner_M_TEMP:=Real_0;
5367:NSX[3].RazEner_T:=Real_0;
5369:NSX[3].RazEner_T_SCADA:=Real_0;
5371:NSX[3].RazEner_T_TEMP:=Real_0;
5373:NSX[3].ReactiveEnergy_kVArh:=Real_0;
5375:NSX[3].ReactiveNegativeEnergy_kVArh:=Real_0;
5377:NSX[3].ReactivePositiveEnergy_kVArh:=Real_0;
5379:NSX[3].ReactivePowerDemand_kVAr:=Real_0;
5381:NSX[3].ReactivePowerL1_kVAr:=Real_0;
5383:NSX[3].ReactivePowerL2_kVAr:=Real_0;
5385:NSX[3].ReactivePowerL3_kVAr:=Real_0;
5387:NSX[3].ReactivePowerMaxDemand_kVAr:=Real_0;
5389:NSX[3].ReactivePowerTotal_kVAr:=Real_0;
5391:NSX[3].THDI1_P:=Real_0;
5393:NSX[3].THDI2_P:=Real_0;
5395:NSX[3].THDI3_P:=Real_0;
5397:NSX[3].THDV12_P:=Real_0;
5399:NSX[3].THDV1N_P:=Real_0;
5401:NSX[3].THDV23_P:=Real_0;
5403:NSX[3].THDV2N_P:=Real_0;
5405:NSX[3].THDV31_P:=Real_0;
5407:NSX[3].THDV3N_P:=Real_0;
5409:NSX[3].VoltageAvgPhToN_V:=Real_0;
5411:NSX[3].VoltageAvgPhToPh_V:=Real_0;
5413:NSX[3].VoltageUnbV12_P:=Real_0;
5415:NSX[3].VoltageUnbV1N_P:=Real_0;
5417:NSX[3].VoltageUnbV23_P:=Real_0;
5419:NSX[3].VoltageUnbV2N_P:=Real_0;
5421:NSX[3].VoltageUnbV31_P:=Real_0;
5423:NSX[3].VoltageUnbV3N_P:=Real_0;
5425:NSX[3].VoltageV12_V:=Real_0;
5427:NSX[3].VoltageV1N_V:=Real_0;
5429:NSX[3].VoltageV23_V:=Real_0;
5431:NSX[3].VoltageV2N_V:=Real_0;
5433:NSX[3].VoltageV31_V:=Real_0;
5435:NSX[3].VoltageV3N_V:=Real_0;
5437:NSX[4].ActiveEnergy_kWh:=Real_0;
5439:NSX[4].ActiveNegativeEnergy_kWh:=Real_0;
5441:NSX[4].ActivePositiveEnergy_kWh:=Real_0;
5443:NSX[4].ActivePowerDemand_kW:=Real_0;
5445:NSX[4].ActivePowerL1_kW:=Real_0;
5447:NSX[4].ActivePowerL2_kW:=Real_0;
5449:NSX[4].ActivePowerL3_kW:=Real_0;
5451:NSX[4].ActivePowerMaxDemand_kW:=Real_0;
5453:NSX[4].ActivePowerTotal_kW:=Real_0;
5455:NSX[4].ApparentEnergy_kVAh:=Real_0;
5457:NSX[4].ApparentPowerDemand_kVA:=Real_0;
5459:NSX[4].ApparentPowerMaxDemand_kVA:=Real_0;
5461:NSX[4].ApparetnPowerL1_kVA:=Real_0;
5463:NSX[4].ApparetnPowerL2_kVA:=Real_0;
5465:NSX[4].ApparetnPowerL3_kVA:=Real_0;
5467:NSX[4].ApparetnPowerTotal_kVA:=Real_0;
5469:NSX[4].CosFL1:=Real_0;
5471:NSX[4].CosFL2:=Real_0;
5473:NSX[4].CosFL3:=Real_0;
5475:NSX[4].CosFTotal:=Real_0;
5477:NSX[4].CumulNegativeActiveEnergy_kWh:=Real_0;
5479:NSX[4].CumulPositiveActiveEnergy_kWh:=Real_0;
5481:NSX[4].CurrentAvgI1I2I3_A:=Real_0;
5483:NSX[4].CurrentDemandL1_A:=Real_0;
5485:NSX[4].CurrentDemandL2_A:=Real_0;
5487:NSX[4].CurrentDemandL3_A:=Real_0;
5489:NSX[4].CurrentDemandMaxL1_A:=Real_0;
5491:NSX[4].CurrentDemandMaxL2_A:=Real_0;
5493:NSX[4].CurrentDemandMaxL3_A:=Real_0;
5495:NSX[4].CurrentDemandMaxN_A:=Real_0;
5497:NSX[4].CurrentDemandN_A:=Real_0;
5499:NSX[4].CurrentL1_A:=Real_0;
5501:NSX[4].CurrentL2_A:=Real_0;
5503:NSX[4].CurrentL3_A:=Real_0;
5505:NSX[4].CurrentN_A:=Real_0;
5507:NSX[4].CurrentUnbI1_P:=Real_0;
5509:NSX[4].CurrentUnbI2_P:=Real_0;
5511:NSX[4].CurrentUnbI3_P:=Real_0;
5513:NSX[4].CurrentUnbN_P:=Real_0;
5515:NSX[4].DelovnaEnergija_TEMP:=Real_0;
5517:NSX[4].DistortionPowerL1_kVAr:=Real_0;
5519:NSX[4].DistortionPowerL2_kVAr:=Real_0;
5521:NSX[4].DistortionPowerL3_kVAr:=Real_0;
5523:NSX[4].DistortionPowerTotal_kVAr:=Real_0;
5525:NSX[4].Frequency_Hz:=Real_0;
5527:NSX[4].FunReactivePowerL1_kVAr:=Real_0;
5529:NSX[4].FunReactivePowerL2_kVAr:=Real_0;
5531:NSX[4].FunReactivePowerL3_kVAr:=Real_0;
5533:NSX[4].FunReactivePowerTotal_kVAr:=Real_0;
5535:NSX[4].MAX_ActivePowerL1_kW:=Real_0;
5537:NSX[4].MAX_ActivePowerL2_kW:=Real_0;
5539:NSX[4].MAX_ActivePowerL3_kW:=Real_0;
5541:NSX[4].MAX_ActivePowerTotal_kW:=Real_0;
5543:NSX[4].MAX_ApparetnPowerL1_kVA:=Real_0;
5545:NSX[4].MAX_ApparetnPowerL2_kVA:=Real_0;
5547:NSX[4].MAX_ApparetnPowerL3_kVA:=Real_0;
5549:NSX[4].MAX_ApparetnPowerTotal_kVA:=Real_0;
5551:NSX[4].MAX_CosFL1:=Real_0;
5553:NSX[4].MAX_CosFL2:=Real_0;
5555:NSX[4].MAX_CosFL3:=Real_0;
5557:NSX[4].MAX_CosFTotal:=Real_0;
5559:NSX[4].MAX_CurrentAvgI1I2I3_A:=Real_0;
5561:NSX[4].MAX_CurrentL1_A:=Real_0;
5563:NSX[4].MAX_CurrentL2_A:=Real_0;
5565:NSX[4].MAX_CurrentL3_A:=Real_0;
5567:NSX[4].MAX_CurrentMaxL1L2L3N_A:=Real_0;
5569:NSX[4].MAX_CurrentN_A:=Real_0;
5571:NSX[4].MAX_DistortionPowerL1_kVAr:=Real_0;
5573:NSX[4].MAX_DistortionPowerL2_kVAr:=Real_0;
5575:NSX[4].MAX_DistortionPowerL3_kVAr:=Real_0;
5577:NSX[4].MAX_DistortionPowerTotal_kVAr:=Real_0;
5579:NSX[4].MAX_Frequency_Hz:=Real_0;
5581:NSX[4].MAX_FunReactivePowerL1_kVAr:=Real_0;
5583:NSX[4].MAX_FunReactivePowerL2_kVAr:=Real_0;
5585:NSX[4].MAX_FunReactivePowerL3_kVAr:=Real_0;
5587:NSX[4].MAX_FunReactivePowerTotal_kVAr:=Real_0;
5589:NSX[4].MAX_PowerFactorL1:=Real_0;
5591:NSX[4].MAX_PowerFactorL2:=Real_0;
5593:NSX[4].MAX_PowerFactorL3:=Real_0;
5595:NSX[4].MAX_PowerFactorTotal:=Real_0;
5597:NSX[4].MAX_ReactivePowerL1_kVAr:=Real_0;
5599:NSX[4].MAX_ReactivePowerL2_kVAr:=Real_0;
5601:NSX[4].MAX_ReactivePowerL3_kVAr:=Real_0;
5603:NSX[4].MAX_ReactivePowerTotal_kVAr:=Real_0;
5605:NSX[4].MAX_THDI1_P:=Real_0;
5607:NSX[4].MAX_THDI2_P:=Real_0;
5609:NSX[4].MAX_THDI3_P:=Real_0;
5611:NSX[4].MAX_THDV12_P:=Real_0;
5613:NSX[4].MAX_THDV1N_P:=Real_0;
5615:NSX[4].MAX_THDV23_P:=Real_0;
5617:NSX[4].MAX_THDV2N_P:=Real_0;
5619:NSX[4].MAX_THDV31_P:=Real_0;
5621:NSX[4].MAX_THDV3N_P:=Real_0;
5623:NSX[4].MAX_VoltageAvgPhToN_V:=Real_0;
5625:NSX[4].MAX_VoltageAvgPhToPh_V:=Real_0;
5627:NSX[4].MAX_VoltageUnbV12_P:=Real_0;
5629:NSX[4].MAX_VoltageUnbV1N_P:=Real_0;
5631:NSX[4].MAX_VoltageUnbV23_P:=Real_0;
5633:NSX[4].MAX_VoltageUnbV2N_P:=Real_0;
5635:NSX[4].MAX_VoltageUnbV31_P:=Real_0;
5637:NSX[4].MAX_VoltageUnbV3N_P:=Real_0;
5639:NSX[4].MAX_VoltageV12_V:=Real_0;
5641:NSX[4].MAX_VoltageV1N_V:=Real_0;
5643:NSX[4].MAX_VoltageV23_V:=Real_0;
5645:NSX[4].MAX_VoltageV2N_V:=Real_0;
5647:NSX[4].MAX_VoltageV31_V:=Real_0;
5649:NSX[4].MAX_VoltageV3N_V:=Real_0;
5651:NSX[4].MIN_ActivePowerL1_kW:=Real_0;
5653:NSX[4].MIN_ActivePowerL2_kW:=Real_0;
5655:NSX[4].MIN_ActivePowerL3_kW:=Real_0;
5657:NSX[4].MIN_ActivePowerTotal_kW:=Real_0;
5659:NSX[4].MIN_ApparetnPowerL1_kVA:=Real_0;
5661:NSX[4].MIN_ApparetnPowerL2_kVA:=Real_0;
5663:NSX[4].MIN_ApparetnPowerL3_kVA:=Real_0;
5665:NSX[4].MIN_ApparetnPowerTotal_kVA:=Real_0;
5667:NSX[4].MIN_CosFL1:=Real_0;
5669:NSX[4].MIN_CosFL2:=Real_0;
5671:NSX[4].MIN_CosFL3:=Real_0;
5673:NSX[4].MIN_CosFTotal:=Real_0;
5675:NSX[4].MIN_CurrentAvgI1I2I3_A:=Real_0;
5677:NSX[4].MIN_CurrentL1_A:=Real_0;
5679:NSX[4].MIN_CurrentL2_A:=Real_0;
5681:NSX[4].MIN_CurrentL3_A:=Real_0;
5683:NSX[4].MIN_CurrentMaxL1L2L3N_A:=Real_0;
5685:NSX[4].MIN_CurrentN_A:=Real_0;
5687:NSX[4].MIN_DistortionPowerL1_kVAr:=Real_0;
5689:NSX[4].MIN_DistortionPowerL2_kVAr:=Real_0;
5691:NSX[4].MIN_DistortionPowerL3_kVAr:=Real_0;
5693:NSX[4].MIN_DistortionPowerTotal_kVAr:=Real_0;
5695:NSX[4].MIN_Frequency_Hz:=Real_0;
5697:NSX[4].MIN_FunReactivePowerL1_kVAr:=Real_0;
5699:NSX[4].MIN_FunReactivePowerL2_kVAr:=Real_0;
5701:NSX[4].MIN_FunReactivePowerL3_kVAr:=Real_0;
5703:NSX[4].MIN_FunReactivePowerTotal_kVAr:=Real_0;
5705:NSX[4].MIN_PowerFactorL1:=Real_0;
5707:NSX[4].MIN_PowerFactorL2:=Real_0;
5709:NSX[4].MIN_PowerFactorL3:=Real_0;
5711:NSX[4].MIN_PowerFactorTotal:=Real_0;
5713:NSX[4].MIN_ReactivePowerL1_kVAr:=Real_0;
5715:NSX[4].MIN_ReactivePowerL2_kVAr:=Real_0;
5717:NSX[4].MIN_ReactivePowerL3_kVAr:=Real_0;
5719:NSX[4].MIN_ReactivePowerTotal_kVAr:=Real_0;
5721:NSX[4].MIN_THDI1_P:=Real_0;
5723:NSX[4].MIN_THDI2_P:=Real_0;
5725:NSX[4].MIN_THDI3_P:=Real_0;
5727:NSX[4].MIN_THDV12_P:=Real_0;
5729:NSX[4].MIN_THDV1N_P:=Real_0;
5731:NSX[4].MIN_THDV23_P:=Real_0;
5733:NSX[4].MIN_THDV2N_P:=Real_0;
5735:NSX[4].MIN_THDV31_P:=Real_0;
5737:NSX[4].MIN_THDV3N_P:=Real_0;
5739:NSX[4].MIN_VoltageAvgPhToN_V:=Real_0;
5741:NSX[4].MIN_VoltageAvgPhToPh_V:=Real_0;
5743:NSX[4].MIN_VoltageUnbV12_P:=Real_0;
5745:NSX[4].MIN_VoltageUnbV1N_P:=Real_0;
5747:NSX[4].MIN_VoltageUnbV23_P:=Real_0;
5749:NSX[4].MIN_VoltageUnbV2N_P:=Real_0;
5751:NSX[4].MIN_VoltageUnbV31_P:=Real_0;
5753:NSX[4].MIN_VoltageUnbV3N_P:=Real_0;
5755:NSX[4].MIN_VoltageV12_V:=Real_0;
5757:NSX[4].MIN_VoltageV1N_V:=Real_0;
5759:NSX[4].MIN_VoltageV23_V:=Real_0;
5761:NSX[4].MIN_VoltageV2N_V:=Real_0;
5763:NSX[4].MIN_VoltageV31_V:=Real_0;
5765:NSX[4].MIN_VoltageV3N_V:=Real_0;
5767:NSX[4].PowerFactorL1:=Real_0;
5769:NSX[4].PowerFactorL2:=Real_0;
5771:NSX[4].PowerFactorL3:=Real_0;
5773:NSX[4].PowerFactorTotal:=Real_0;
5775:NSX[4].RazEner_D:=Real_0;
5777:NSX[4].RazEner_D_SCADA:=Real_0;
5779:NSX[4].RazEner_D_TEMP:=Real_0;
5781:NSX[4].RazEner_M:=Real_0;
5783:NSX[4].RazEner_M_SCADA:=Real_0;
5785:NSX[4].RazEner_M_TEMP:=Real_0;
5787:NSX[4].RazEner_T:=Real_0;
5789:NSX[4].RazEner_T_SCADA:=Real_0;
5791:NSX[4].RazEner_T_TEMP:=Real_0;
5793:NSX[4].ReactiveEnergy_kVArh:=Real_0;
5795:NSX[4].ReactiveNegativeEnergy_kVArh:=Real_0;
5797:NSX[4].ReactivePositiveEnergy_kVArh:=Real_0;
5799:NSX[4].ReactivePowerDemand_kVAr:=Real_0;
5801:NSX[4].ReactivePowerL1_kVAr:=Real_0;
5803:NSX[4].ReactivePowerL2_kVAr:=Real_0;
5805:NSX[4].ReactivePowerL3_kVAr:=Real_0;
5807:NSX[4].ReactivePowerMaxDemand_kVAr:=Real_0;
5809:NSX[4].ReactivePowerTotal_kVAr:=Real_0;
5811:NSX[4].THDI1_P:=Real_0;
5813:NSX[4].THDI2_P:=Real_0;
5815:NSX[4].THDI3_P:=Real_0;
5817:NSX[4].THDV12_P:=Real_0;
5819:NSX[4].THDV1N_P:=Real_0;
5821:NSX[4].THDV23_P:=Real_0;
5823:NSX[4].THDV2N_P:=Real_0;
5825:NSX[4].THDV31_P:=Real_0;
5827:NSX[4].THDV3N_P:=Real_0;
5829:NSX[4].VoltageAvgPhToN_V:=Real_0;
5831:NSX[4].VoltageAvgPhToPh_V:=Real_0;
5833:NSX[4].VoltageUnbV12_P:=Real_0;
5835:NSX[4].VoltageUnbV1N_P:=Real_0;
5837:NSX[4].VoltageUnbV23_P:=Real_0;
5839:NSX[4].VoltageUnbV2N_P:=Real_0;
5841:NSX[4].VoltageUnbV31_P:=Real_0;
5843:NSX[4].VoltageUnbV3N_P:=Real_0;
5845:NSX[4].VoltageV12_V:=Real_0;
5847:NSX[4].VoltageV1N_V:=Real_0;
5849:NSX[4].VoltageV23_V:=Real_0;
5851:NSX[4].VoltageV2N_V:=Real_0;
5853:NSX[4].VoltageV31_V:=Real_0;
5855:NSX[4].VoltageV3N_V:=Real_0;
5857:NSX[5].ActiveEnergy_kWh:=Real_0;
5859:NSX[5].ActiveNegativeEnergy_kWh:=Real_0;
5861:NSX[5].ActivePositiveEnergy_kWh:=Real_0;
5863:NSX[5].ActivePowerDemand_kW:=Real_0;
5865:NSX[5].ActivePowerL1_kW:=Real_0;
5867:NSX[5].ActivePowerL2_kW:=Real_0;
5869:NSX[5].ActivePowerL3_kW:=Real_0;
5871:NSX[5].ActivePowerMaxDemand_kW:=Real_0;
5873:NSX[5].ActivePowerTotal_kW:=Real_0;
5875:NSX[5].ApparentEnergy_kVAh:=Real_0;
5877:NSX[5].ApparentPowerDemand_kVA:=Real_0;
5879:NSX[5].ApparentPowerMaxDemand_kVA:=Real_0;
5881:NSX[5].ApparetnPowerL1_kVA:=Real_0;
5883:NSX[5].ApparetnPowerL2_kVA:=Real_0;
5885:NSX[5].ApparetnPowerL3_kVA:=Real_0;
5887:NSX[5].ApparetnPowerTotal_kVA:=Real_0;
5889:NSX[5].CosFL1:=Real_0;
5891:NSX[5].CosFL2:=Real_0;
5893:NSX[5].CosFL3:=Real_0;
5895:NSX[5].CosFTotal:=Real_0;
5897:NSX[5].CumulNegativeActiveEnergy_kWh:=Real_0;
5899:NSX[5].CumulPositiveActiveEnergy_kWh:=Real_0;
5901:NSX[5].CurrentAvgI1I2I3_A:=Real_0;
5903:NSX[5].CurrentDemandL1_A:=Real_0;
5905:NSX[5].CurrentDemandL2_A:=Real_0;
5907:NSX[5].CurrentDemandL3_A:=Real_0;
5909:NSX[5].CurrentDemandMaxL1_A:=Real_0;
5911:NSX[5].CurrentDemandMaxL2_A:=Real_0;
5913:NSX[5].CurrentDemandMaxL3_A:=Real_0;
5915:NSX[5].CurrentDemandMaxN_A:=Real_0;
5917:NSX[5].CurrentDemandN_A:=Real_0;
5919:NSX[5].CurrentL1_A:=Real_0;
5921:NSX[5].CurrentL2_A:=Real_0;
5923:NSX[5].CurrentL3_A:=Real_0;
5925:NSX[5].CurrentN_A:=Real_0;
5927:NSX[5].CurrentUnbI1_P:=Real_0;
5929:NSX[5].CurrentUnbI2_P:=Real_0;
5931:NSX[5].CurrentUnbI3_P:=Real_0;
5933:NSX[5].CurrentUnbN_P:=Real_0;
5935:NSX[5].DelovnaEnergija_TEMP:=Real_0;
5937:NSX[5].DistortionPowerL1_kVAr:=Real_0;
5939:NSX[5].DistortionPowerL2_kVAr:=Real_0;
5941:NSX[5].DistortionPowerL3_kVAr:=Real_0;
5943:NSX[5].DistortionPowerTotal_kVAr:=Real_0;
5945:NSX[5].Frequency_Hz:=Real_0;
5947:NSX[5].FunReactivePowerL1_kVAr:=Real_0;
5949:NSX[5].FunReactivePowerL2_kVAr:=Real_0;
5951:NSX[5].FunReactivePowerL3_kVAr:=Real_0;
5953:NSX[5].FunReactivePowerTotal_kVAr:=Real_0;
5955:NSX[5].MAX_ActivePowerL1_kW:=Real_0;
5957:NSX[5].MAX_ActivePowerL2_kW:=Real_0;
5959:NSX[5].MAX_ActivePowerL3_kW:=Real_0;
5961:NSX[5].MAX_ActivePowerTotal_kW:=Real_0;
5963:NSX[5].MAX_ApparetnPowerL1_kVA:=Real_0;
5965:NSX[5].MAX_ApparetnPowerL2_kVA:=Real_0;
5967:NSX[5].MAX_ApparetnPowerL3_kVA:=Real_0;
5969:NSX[5].MAX_ApparetnPowerTotal_kVA:=Real_0;
5971:NSX[5].MAX_CosFL1:=Real_0;
5973:NSX[5].MAX_CosFL2:=Real_0;
5975:NSX[5].MAX_CosFL3:=Real_0;
5977:NSX[5].MAX_CosFTotal:=Real_0;
5979:NSX[5].MAX_CurrentAvgI1I2I3_A:=Real_0;
5981:NSX[5].MAX_CurrentL1_A:=Real_0;
5983:NSX[5].MAX_CurrentL2_A:=Real_0;
5985:NSX[5].MAX_CurrentL3_A:=Real_0;
5987:NSX[5].MAX_CurrentMaxL1L2L3N_A:=Real_0;
5989:NSX[5].MAX_CurrentN_A:=Real_0;
5991:NSX[5].MAX_DistortionPowerL1_kVAr:=Real_0;
5993:NSX[5].MAX_DistortionPowerL2_kVAr:=Real_0;
5995:NSX[5].MAX_DistortionPowerL3_kVAr:=Real_0;
5997:NSX[5].MAX_DistortionPowerTotal_kVAr:=Real_0;
5999:NSX[5].MAX_Frequency_Hz:=Real_0;
6001:NSX[5].MAX_FunReactivePowerL1_kVAr:=Real_0;
6003:NSX[5].MAX_FunReactivePowerL2_kVAr:=Real_0;
6005:NSX[5].MAX_FunReactivePowerL3_kVAr:=Real_0;
6007:NSX[5].MAX_FunReactivePowerTotal_kVAr:=Real_0;
6009:NSX[5].MAX_PowerFactorL1:=Real_0;
6011:NSX[5].MAX_PowerFactorL2:=Real_0;
6013:NSX[5].MAX_PowerFactorL3:=Real_0;
6015:NSX[5].MAX_PowerFactorTotal:=Real_0;
6017:NSX[5].MAX_ReactivePowerL1_kVAr:=Real_0;
6019:NSX[5].MAX_ReactivePowerL2_kVAr:=Real_0;
6021:NSX[5].MAX_ReactivePowerL3_kVAr:=Real_0;
6023:NSX[5].MAX_ReactivePowerTotal_kVAr:=Real_0;
6025:NSX[5].MAX_THDI1_P:=Real_0;
6027:NSX[5].MAX_THDI2_P:=Real_0;
6029:NSX[5].MAX_THDI3_P:=Real_0;
6031:NSX[5].MAX_THDV12_P:=Real_0;
6033:NSX[5].MAX_THDV1N_P:=Real_0;
6035:NSX[5].MAX_THDV23_P:=Real_0;
6037:NSX[5].MAX_THDV2N_P:=Real_0;
6039:NSX[5].MAX_THDV31_P:=Real_0;
6041:NSX[5].MAX_THDV3N_P:=Real_0;
6043:NSX[5].MAX_VoltageAvgPhToN_V:=Real_0;
6045:NSX[5].MAX_VoltageAvgPhToPh_V:=Real_0;
6047:NSX[5].MAX_VoltageUnbV12_P:=Real_0;
6049:NSX[5].MAX_VoltageUnbV1N_P:=Real_0;
6051:NSX[5].MAX_VoltageUnbV23_P:=Real_0;
6053:NSX[5].MAX_VoltageUnbV2N_P:=Real_0;
6055:NSX[5].MAX_VoltageUnbV31_P:=Real_0;
6057:NSX[5].MAX_VoltageUnbV3N_P:=Real_0;
6059:NSX[5].MAX_VoltageV12_V:=Real_0;
6061:NSX[5].MAX_VoltageV1N_V:=Real_0;
6063:NSX[5].MAX_VoltageV23_V:=Real_0;
6065:NSX[5].MAX_VoltageV2N_V:=Real_0;
6067:NSX[5].MAX_VoltageV31_V:=Real_0;
6069:NSX[5].MAX_VoltageV3N_V:=Real_0;
6071:NSX[5].MIN_ActivePowerL1_kW:=Real_0;
6073:NSX[5].MIN_ActivePowerL2_kW:=Real_0;
6075:NSX[5].MIN_ActivePowerL3_kW:=Real_0;
6077:NSX[5].MIN_ActivePowerTotal_kW:=Real_0;
6079:NSX[5].MIN_ApparetnPowerL1_kVA:=Real_0;
6081:NSX[5].MIN_ApparetnPowerL2_kVA:=Real_0;
6083:NSX[5].MIN_ApparetnPowerL3_kVA:=Real_0;
6085:NSX[5].MIN_ApparetnPowerTotal_kVA:=Real_0;
6087:NSX[5].MIN_CosFL1:=Real_0;
6089:NSX[5].MIN_CosFL2:=Real_0;
6091:NSX[5].MIN_CosFL3:=Real_0;
6093:NSX[5].MIN_CosFTotal:=Real_0;
6095:NSX[5].MIN_CurrentAvgI1I2I3_A:=Real_0;
6097:NSX[5].MIN_CurrentL1_A:=Real_0;
6099:NSX[5].MIN_CurrentL2_A:=Real_0;
6101:NSX[5].MIN_CurrentL3_A:=Real_0;
6103:NSX[5].MIN_CurrentMaxL1L2L3N_A:=Real_0;
6105:NSX[5].MIN_CurrentN_A:=Real_0;
6107:NSX[5].MIN_DistortionPowerL1_kVAr:=Real_0;
6109:NSX[5].MIN_DistortionPowerL2_kVAr:=Real_0;
6111:NSX[5].MIN_DistortionPowerL3_kVAr:=Real_0;
6113:NSX[5].MIN_DistortionPowerTotal_kVAr:=Real_0;
6115:NSX[5].MIN_Frequency_Hz:=Real_0;
6117:NSX[5].MIN_FunReactivePowerL1_kVAr:=Real_0;
6119:NSX[5].MIN_FunReactivePowerL2_kVAr:=Real_0;
6121:NSX[5].MIN_FunReactivePowerL3_kVAr:=Real_0;
6123:NSX[5].MIN_FunReactivePowerTotal_kVAr:=Real_0;
6125:NSX[5].MIN_PowerFactorL1:=Real_0;
6127:NSX[5].MIN_PowerFactorL2:=Real_0;
6129:NSX[5].MIN_PowerFactorL3:=Real_0;
6131:NSX[5].MIN_PowerFactorTotal:=Real_0;
6133:NSX[5].MIN_ReactivePowerL1_kVAr:=Real_0;
6135:NSX[5].MIN_ReactivePowerL2_kVAr:=Real_0;
6137:NSX[5].MIN_ReactivePowerL3_kVAr:=Real_0;
6139:NSX[5].MIN_ReactivePowerTotal_kVAr:=Real_0;
6141:NSX[5].MIN_THDI1_P:=Real_0;
6143:NSX[5].MIN_THDI2_P:=Real_0;
6145:NSX[5].MIN_THDI3_P:=Real_0;
6147:NSX[5].MIN_THDV12_P:=Real_0;
6149:NSX[5].MIN_THDV1N_P:=Real_0;
6151:NSX[5].MIN_THDV23_P:=Real_0;
6153:NSX[5].MIN_THDV2N_P:=Real_0;
6155:NSX[5].MIN_THDV31_P:=Real_0;
6157:NSX[5].MIN_THDV3N_P:=Real_0;
6159:NSX[5].MIN_VoltageAvgPhToN_V:=Real_0;
6161:NSX[5].MIN_VoltageAvgPhToPh_V:=Real_0;
6163:NSX[5].MIN_VoltageUnbV12_P:=Real_0;
6165:NSX[5].MIN_VoltageUnbV1N_P:=Real_0;
6167:NSX[5].MIN_VoltageUnbV23_P:=Real_0;
6169:NSX[5].MIN_VoltageUnbV2N_P:=Real_0;
6171:NSX[5].MIN_VoltageUnbV31_P:=Real_0;
6173:NSX[5].MIN_VoltageUnbV3N_P:=Real_0;
6175:NSX[5].MIN_VoltageV12_V:=Real_0;
6177:NSX[5].MIN_VoltageV1N_V:=Real_0;
6179:NSX[5].MIN_VoltageV23_V:=Real_0;
6181:NSX[5].MIN_VoltageV2N_V:=Real_0;
6183:NSX[5].MIN_VoltageV31_V:=Real_0;
6185:NSX[5].MIN_VoltageV3N_V:=Real_0;
6187:NSX[5].PowerFactorL1:=Real_0;
6189:NSX[5].PowerFactorL2:=Real_0;
6191:NSX[5].PowerFactorL3:=Real_0;
6193:NSX[5].PowerFactorTotal:=Real_0;
6195:NSX[5].RazEner_D:=Real_0;
6197:NSX[5].RazEner_D_SCADA:=Real_0;
6199:NSX[5].RazEner_D_TEMP:=Real_0;
6201:NSX[5].RazEner_M:=Real_0;
6203:NSX[5].RazEner_M_SCADA:=Real_0;
6205:NSX[5].RazEner_M_TEMP:=Real_0;
6207:NSX[5].RazEner_T:=Real_0;
6209:NSX[5].RazEner_T_SCADA:=Real_0;
6211:NSX[5].RazEner_T_TEMP:=Real_0;
6213:NSX[5].ReactiveEnergy_kVArh:=Real_0;
6215:NSX[5].ReactiveNegativeEnergy_kVArh:=Real_0;
6217:NSX[5].ReactivePositiveEnergy_kVArh:=Real_0;
6219:NSX[5].ReactivePowerDemand_kVAr:=Real_0;
6221:NSX[5].ReactivePowerL1_kVAr:=Real_0;
6223:NSX[5].ReactivePowerL2_kVAr:=Real_0;
6225:NSX[5].ReactivePowerL3_kVAr:=Real_0;
6227:NSX[5].ReactivePowerMaxDemand_kVAr:=Real_0;
6229:NSX[5].ReactivePowerTotal_kVAr:=Real_0;
6231:NSX[5].THDI1_P:=Real_0;
6233:NSX[5].THDI2_P:=Real_0;
6235:NSX[5].THDI3_P:=Real_0;
6237:NSX[5].THDV12_P:=Real_0;
6239:NSX[5].THDV1N_P:=Real_0;
6241:NSX[5].THDV23_P:=Real_0;
6243:NSX[5].THDV2N_P:=Real_0;
6245:NSX[5].THDV31_P:=Real_0;
6247:NSX[5].THDV3N_P:=Real_0;
6249:NSX[5].VoltageAvgPhToN_V:=Real_0;
6251:NSX[5].VoltageAvgPhToPh_V:=Real_0;
6253:NSX[5].VoltageUnbV12_P:=Real_0;
6255:NSX[5].VoltageUnbV1N_P:=Real_0;
6257:NSX[5].VoltageUnbV23_P:=Real_0;
6259:NSX[5].VoltageUnbV2N_P:=Real_0;
6261:NSX[5].VoltageUnbV31_P:=Real_0;
6263:NSX[5].VoltageUnbV3N_P:=Real_0;
6265:NSX[5].VoltageV12_V:=Real_0;
6267:NSX[5].VoltageV1N_V:=Real_0;
6269:NSX[5].VoltageV23_V:=Real_0;
6271:NSX[5].VoltageV2N_V:=Real_0;
6273:NSX[5].VoltageV31_V:=Real_0;
6275:NSX[5].VoltageV3N_V:=Real_0;
6277:NSX[6].ActiveEnergy_kWh:=Real_0;
6279:NSX[6].ActiveNegativeEnergy_kWh:=Real_0;
6281:NSX[6].ActivePositiveEnergy_kWh:=Real_0;
6283:NSX[6].ActivePowerDemand_kW:=Real_0;
6285:NSX[6].ActivePowerL1_kW:=Real_0;
6287:NSX[6].ActivePowerL2_kW:=Real_0;
6289:NSX[6].ActivePowerL3_kW:=Real_0;
6291:NSX[6].ActivePowerMaxDemand_kW:=Real_0;
6293:NSX[6].ActivePowerTotal_kW:=Real_0;
6295:NSX[6].ApparentEnergy_kVAh:=Real_0;
6297:NSX[6].ApparentPowerDemand_kVA:=Real_0;
6299:NSX[6].ApparentPowerMaxDemand_kVA:=Real_0;
6301:NSX[6].ApparetnPowerL1_kVA:=Real_0;
6303:NSX[6].ApparetnPowerL2_kVA:=Real_0;
6305:NSX[6].ApparetnPowerL3_kVA:=Real_0;
6307:NSX[6].ApparetnPowerTotal_kVA:=Real_0;
6309:NSX[6].CosFL1:=Real_0;
6311:NSX[6].CosFL2:=Real_0;
6313:NSX[6].CosFL3:=Real_0;
6315:NSX[6].CosFTotal:=Real_0;
6317:NSX[6].CumulNegativeActiveEnergy_kWh:=Real_0;
6319:NSX[6].CumulPositiveActiveEnergy_kWh:=Real_0;
6321:NSX[6].CurrentAvgI1I2I3_A:=Real_0;
6323:NSX[6].CurrentDemandL1_A:=Real_0;
6325:NSX[6].CurrentDemandL2_A:=Real_0;
6327:NSX[6].CurrentDemandL3_A:=Real_0;
6329:NSX[6].CurrentDemandMaxL1_A:=Real_0;
6331:NSX[6].CurrentDemandMaxL2_A:=Real_0;
6333:NSX[6].CurrentDemandMaxL3_A:=Real_0;
6335:NSX[6].CurrentDemandMaxN_A:=Real_0;
6337:NSX[6].CurrentDemandN_A:=Real_0;
6339:NSX[6].CurrentL1_A:=Real_0;
6341:NSX[6].CurrentL2_A:=Real_0;
6343:NSX[6].CurrentL3_A:=Real_0;
6345:NSX[6].CurrentN_A:=Real_0;
6347:NSX[6].CurrentUnbI1_P:=Real_0;
6349:NSX[6].CurrentUnbI2_P:=Real_0;
6351:NSX[6].CurrentUnbI3_P:=Real_0;
6353:NSX[6].CurrentUnbN_P:=Real_0;
6355:NSX[6].DelovnaEnergija_TEMP:=Real_0;
6357:NSX[6].DistortionPowerL1_kVAr:=Real_0;
6359:NSX[6].DistortionPowerL2_kVAr:=Real_0;
6361:NSX[6].DistortionPowerL3_kVAr:=Real_0;
6363:NSX[6].DistortionPowerTotal_kVAr:=Real_0;
6365:NSX[6].Frequency_Hz:=Real_0;
6367:NSX[6].FunReactivePowerL1_kVAr:=Real_0;
6369:NSX[6].FunReactivePowerL2_kVAr:=Real_0;
6371:NSX[6].FunReactivePowerL3_kVAr:=Real_0;
6373:NSX[6].FunReactivePowerTotal_kVAr:=Real_0;
6375:NSX[6].MAX_ActivePowerL1_kW:=Real_0;
6377:NSX[6].MAX_ActivePowerL2_kW:=Real_0;
6379:NSX[6].MAX_ActivePowerL3_kW:=Real_0;
6381:NSX[6].MAX_ActivePowerTotal_kW:=Real_0;
6383:NSX[6].MAX_ApparetnPowerL1_kVA:=Real_0;
6385:NSX[6].MAX_ApparetnPowerL2_kVA:=Real_0;
6387:NSX[6].MAX_ApparetnPowerL3_kVA:=Real_0;
6389:NSX[6].MAX_ApparetnPowerTotal_kVA:=Real_0;
6391:NSX[6].MAX_CosFL1:=Real_0;
6393:NSX[6].MAX_CosFL2:=Real_0;
6395:NSX[6].MAX_CosFL3:=Real_0;
6397:NSX[6].MAX_CosFTotal:=Real_0;
6399:NSX[6].MAX_CurrentAvgI1I2I3_A:=Real_0;
6401:NSX[6].MAX_CurrentL1_A:=Real_0;
6403:NSX[6].MAX_CurrentL2_A:=Real_0;
6405:NSX[6].MAX_CurrentL3_A:=Real_0;
6407:NSX[6].MAX_CurrentMaxL1L2L3N_A:=Real_0;
6409:NSX[6].MAX_CurrentN_A:=Real_0;
6411:NSX[6].MAX_DistortionPowerL1_kVAr:=Real_0;
6413:NSX[6].MAX_DistortionPowerL2_kVAr:=Real_0;
6415:NSX[6].MAX_DistortionPowerL3_kVAr:=Real_0;
6417:NSX[6].MAX_DistortionPowerTotal_kVAr:=Real_0;
6419:NSX[6].MAX_Frequency_Hz:=Real_0;
6421:NSX[6].MAX_FunReactivePowerL1_kVAr:=Real_0;
6423:NSX[6].MAX_FunReactivePowerL2_kVAr:=Real_0;
6425:NSX[6].MAX_FunReactivePowerL3_kVAr:=Real_0;
6427:NSX[6].MAX_FunReactivePowerTotal_kVAr:=Real_0;
6429:NSX[6].MAX_PowerFactorL1:=Real_0;
6431:NSX[6].MAX_PowerFactorL2:=Real_0;
6433:NSX[6].MAX_PowerFactorL3:=Real_0;
6435:NSX[6].MAX_PowerFactorTotal:=Real_0;
6437:NSX[6].MAX_ReactivePowerL1_kVAr:=Real_0;
6439:NSX[6].MAX_ReactivePowerL2_kVAr:=Real_0;
6441:NSX[6].MAX_ReactivePowerL3_kVAr:=Real_0;
6443:NSX[6].MAX_ReactivePowerTotal_kVAr:=Real_0;
6445:NSX[6].MAX_THDI1_P:=Real_0;
6447:NSX[6].MAX_THDI2_P:=Real_0;
6449:NSX[6].MAX_THDI3_P:=Real_0;
6451:NSX[6].MAX_THDV12_P:=Real_0;
6453:NSX[6].MAX_THDV1N_P:=Real_0;
6455:NSX[6].MAX_THDV23_P:=Real_0;
6457:NSX[6].MAX_THDV2N_P:=Real_0;
6459:NSX[6].MAX_THDV31_P:=Real_0;
6461:NSX[6].MAX_THDV3N_P:=Real_0;
6463:NSX[6].MAX_VoltageAvgPhToN_V:=Real_0;
6465:NSX[6].MAX_VoltageAvgPhToPh_V:=Real_0;
6467:NSX[6].MAX_VoltageUnbV12_P:=Real_0;
6469:NSX[6].MAX_VoltageUnbV1N_P:=Real_0;
6471:NSX[6].MAX_VoltageUnbV23_P:=Real_0;
6473:NSX[6].MAX_VoltageUnbV2N_P:=Real_0;
6475:NSX[6].MAX_VoltageUnbV31_P:=Real_0;
6477:NSX[6].MAX_VoltageUnbV3N_P:=Real_0;
6479:NSX[6].MAX_VoltageV12_V:=Real_0;
6481:NSX[6].MAX_VoltageV1N_V:=Real_0;
6483:NSX[6].MAX_VoltageV23_V:=Real_0;
6485:NSX[6].MAX_VoltageV2N_V:=Real_0;
6487:NSX[6].MAX_VoltageV31_V:=Real_0;
6489:NSX[6].MAX_VoltageV3N_V:=Real_0;
6491:NSX[6].MIN_ActivePowerL1_kW:=Real_0;
6493:NSX[6].MIN_ActivePowerL2_kW:=Real_0;
6495:NSX[6].MIN_ActivePowerL3_kW:=Real_0;
6497:NSX[6].MIN_ActivePowerTotal_kW:=Real_0;
6499:NSX[6].MIN_ApparetnPowerL1_kVA:=Real_0;
6501:NSX[6].MIN_ApparetnPowerL2_kVA:=Real_0;
6503:NSX[6].MIN_ApparetnPowerL3_kVA:=Real_0;
6505:NSX[6].MIN_ApparetnPowerTotal_kVA:=Real_0;
6507:NSX[6].MIN_CosFL1:=Real_0;
6509:NSX[6].MIN_CosFL2:=Real_0;
6511:NSX[6].MIN_CosFL3:=Real_0;
6513:NSX[6].MIN_CosFTotal:=Real_0;
6515:NSX[6].MIN_CurrentAvgI1I2I3_A:=Real_0;
6517:NSX[6].MIN_CurrentL1_A:=Real_0;
6519:NSX[6].MIN_CurrentL2_A:=Real_0;
6521:NSX[6].MIN_CurrentL3_A:=Real_0;
6523:NSX[6].MIN_CurrentMaxL1L2L3N_A:=Real_0;
6525:NSX[6].MIN_CurrentN_A:=Real_0;
6527:NSX[6].MIN_DistortionPowerL1_kVAr:=Real_0;
6529:NSX[6].MIN_DistortionPowerL2_kVAr:=Real_0;
6531:NSX[6].MIN_DistortionPowerL3_kVAr:=Real_0;
6533:NSX[6].MIN_DistortionPowerTotal_kVAr:=Real_0;
6535:NSX[6].MIN_Frequency_Hz:=Real_0;
6537:NSX[6].MIN_FunReactivePowerL1_kVAr:=Real_0;
6539:NSX[6].MIN_FunReactivePowerL2_kVAr:=Real_0;
6541:NSX[6].MIN_FunReactivePowerL3_kVAr:=Real_0;
6543:NSX[6].MIN_FunReactivePowerTotal_kVAr:=Real_0;
6545:NSX[6].MIN_PowerFactorL1:=Real_0;
6547:NSX[6].MIN_PowerFactorL2:=Real_0;
6549:NSX[6].MIN_PowerFactorL3:=Real_0;
6551:NSX[6].MIN_PowerFactorTotal:=Real_0;
6553:NSX[6].MIN_ReactivePowerL1_kVAr:=Real_0;
6555:NSX[6].MIN_ReactivePowerL2_kVAr:=Real_0;
6557:NSX[6].MIN_ReactivePowerL3_kVAr:=Real_0;
6559:NSX[6].MIN_ReactivePowerTotal_kVAr:=Real_0;
6561:NSX[6].MIN_THDI1_P:=Real_0;
6563:NSX[6].MIN_THDI2_P:=Real_0;
6565:NSX[6].MIN_THDI3_P:=Real_0;
6567:NSX[6].MIN_THDV12_P:=Real_0;
6569:NSX[6].MIN_THDV1N_P:=Real_0;
6571:NSX[6].MIN_THDV23_P:=Real_0;
6573:NSX[6].MIN_THDV2N_P:=Real_0;
6575:NSX[6].MIN_THDV31_P:=Real_0;
6577:NSX[6].MIN_THDV3N_P:=Real_0;
6579:NSX[6].MIN_VoltageAvgPhToN_V:=Real_0;
6581:NSX[6].MIN_VoltageAvgPhToPh_V:=Real_0;
6583:NSX[6].MIN_VoltageUnbV12_P:=Real_0;
6585:NSX[6].MIN_VoltageUnbV1N_P:=Real_0;
6587:NSX[6].MIN_VoltageUnbV23_P:=Real_0;
6589:NSX[6].MIN_VoltageUnbV2N_P:=Real_0;
6591:NSX[6].MIN_VoltageUnbV31_P:=Real_0;
6593:NSX[6].MIN_VoltageUnbV3N_P:=Real_0;
6595:NSX[6].MIN_VoltageV12_V:=Real_0;
6597:NSX[6].MIN_VoltageV1N_V:=Real_0;
6599:NSX[6].MIN_VoltageV23_V:=Real_0;
6601:NSX[6].MIN_VoltageV2N_V:=Real_0;
6603:NSX[6].MIN_VoltageV31_V:=Real_0;
6605:NSX[6].MIN_VoltageV3N_V:=Real_0;
6607:NSX[6].PowerFactorL1:=Real_0;
6609:NSX[6].PowerFactorL2:=Real_0;
6611:NSX[6].PowerFactorL3:=Real_0;
6613:NSX[6].PowerFactorTotal:=Real_0;
6615:NSX[6].RazEner_D:=Real_0;
6617:NSX[6].RazEner_D_SCADA:=Real_0;
6619:NSX[6].RazEner_D_TEMP:=Real_0;
6621:NSX[6].RazEner_M:=Real_0;
6623:NSX[6].RazEner_M_SCADA:=Real_0;
6625:NSX[6].RazEner_M_TEMP:=Real_0;
6627:NSX[6].RazEner_T:=Real_0;
6629:NSX[6].RazEner_T_SCADA:=Real_0;
6631:NSX[6].RazEner_T_TEMP:=Real_0;
6633:NSX[6].ReactiveEnergy_kVArh:=Real_0;
6635:NSX[6].ReactiveNegativeEnergy_kVArh:=Real_0;
6637:NSX[6].ReactivePositiveEnergy_kVArh:=Real_0;
6639:NSX[6].ReactivePowerDemand_kVAr:=Real_0;
6641:NSX[6].ReactivePowerL1_kVAr:=Real_0;
6643:NSX[6].ReactivePowerL2_kVAr:=Real_0;
6645:NSX[6].ReactivePowerL3_kVAr:=Real_0;
6647:NSX[6].ReactivePowerMaxDemand_kVAr:=Real_0;
6649:NSX[6].ReactivePowerTotal_kVAr:=Real_0;
6651:NSX[6].THDI1_P:=Real_0;
6653:NSX[6].THDI2_P:=Real_0;
6655:NSX[6].THDI3_P:=Real_0;
6657:NSX[6].THDV12_P:=Real_0;
6659:NSX[6].THDV1N_P:=Real_0;
6661:NSX[6].THDV23_P:=Real_0;
6663:NSX[6].THDV2N_P:=Real_0;
6665:NSX[6].THDV31_P:=Real_0;
6667:NSX[6].THDV3N_P:=Real_0;
6669:NSX[6].VoltageAvgPhToN_V:=Real_0;
6671:NSX[6].VoltageAvgPhToPh_V:=Real_0;
6673:NSX[6].VoltageUnbV12_P:=Real_0;
6675:NSX[6].VoltageUnbV1N_P:=Real_0;
6677:NSX[6].VoltageUnbV23_P:=Real_0;
6679:NSX[6].VoltageUnbV2N_P:=Real_0;
6681:NSX[6].VoltageUnbV31_P:=Real_0;
6683:NSX[6].VoltageUnbV3N_P:=Real_0;
6685:NSX[6].VoltageV12_V:=Real_0;
6687:NSX[6].VoltageV1N_V:=Real_0;
6689:NSX[6].VoltageV23_V:=Real_0;
6691:NSX[6].VoltageV2N_V:=Real_0;
6693:NSX[6].VoltageV31_V:=Real_0;
6695:NSX[6].VoltageV3N_V:=Real_0;
6697:PMM.VirA.Current[10]:=Real_0;
6699:PMM.VirA.Current[11]:=Real_0;
6701:PMM.VirA.Current[12]:=Real_0;
6703:PMM.VirA.Current[13]:=Real_0;
6705:PMM.VirA.Current[14]:=Real_0;
6707:PMM.VirA.Current[15]:=Real_0;
6709:PMM.VirA.Current[16]:=Real_0;
6711:PMM.VirA.Current[17]:=Real_0;
6713:PMM.VirA.Current[18]:=Real_0;
6715:PMM.VirA.Current[19]:=Real_0;
6717:PMM.VirA.Current[1]:=Real_0;
6719:PMM.VirA.Current[20]:=Real_0;
6721:PMM.VirA.Current[21]:=Real_0;
6723:PMM.VirA.Current[22]:=Real_0;
6725:PMM.VirA.Current[23]:=Real_0;
6727:PMM.VirA.Current[24]:=Real_0;
6729:PMM.VirA.Current[25]:=Real_0;
6731:PMM.VirA.Current[26]:=Real_0;
6733:PMM.VirA.Current[27]:=Real_0;
6735:PMM.VirA.Current[28]:=Real_0;
6737:PMM.VirA.Current[29]:=Real_0;
6739:PMM.VirA.Current[2]:=Real_0;
6741:PMM.VirA.Current[30]:=Real_0;
6743:PMM.VirA.Current[31]:=Real_0;
6745:PMM.VirA.Current[32]:=Real_0;
6747:PMM.VirA.Current[33]:=Real_0;
6749:PMM.VirA.Current[34]:=Real_0;
6751:PMM.VirA.Current[35]:=Real_0;
6753:PMM.VirA.Current[36]:=Real_0;
6755:PMM.VirA.Current[37]:=Real_0;
6757:PMM.VirA.Current[38]:=Real_0;
6759:PMM.VirA.Current[39]:=Real_0;
6761:PMM.VirA.Current[3]:=Real_0;
6763:PMM.VirA.Current[40]:=Real_0;
6765:PMM.VirA.Current[41]:=Real_0;
6767:PMM.VirA.Current[42]:=Real_0;
6769:PMM.VirA.Current[43]:=Real_0;
6771:PMM.VirA.Current[44]:=Real_0;
6773:PMM.VirA.Current[4]:=Real_0;
6775:PMM.VirA.Current[5]:=Real_0;
6777:PMM.VirA.Current[6]:=Real_0;
6779:PMM.VirA.Current[7]:=Real_0;
6781:PMM.VirA.Current[8]:=Real_0;
6783:PMM.VirA.Current[9]:=Real_0;
6785:PMM.VirA_fsys:=Real_0;
6787:PMM.VirA_Isys:=Real_0;
6789:PMM.VirA_PFsys:=Real_0;
6791:PMM.VirA_Psys:=Real_0;
6793:PMM.VirA_Qsys:=Real_0;
6795:PMM.VirA_Ssys:=Real_0;
6797:PMM.VirA_Usys:=Real_0;
6799:PMM.VirAActiveEnergyConsumed_kWh:=Real_0;
6801:PMM.VirAActivePowerPhaseA_kW:=Real_0;
6803:PMM.VirAActivePowerPhaseB_kW:=Real_0;
6805:PMM.VirAActivePowerPhaseC_kW:=Real_0;
6807:PMM.VirAAparentPowerPhaseA:=Real_0;
6809:PMM.VirAAparentPowerPhaseB:=Real_0;
6811:PMM.VirAAparentPowerPhaseC:=Real_0;
6813:PMM.VirACurrentInPhaseA_A:=Real_0;
6815:PMM.VirACurrentInPhaseB_A:=Real_0;
6817:PMM.VirACurrentInPhaseC_A:=Real_0;
6819:PMM.VirAReactiveEnergyConsumed_kVARh:=Real_0;
6821:PMM.VirAReactivePowerPhaseA:=Real_0;
6823:PMM.VirAReactivePowerPhaseB:=Real_0;
6825:PMM.VirAReactivePowerPhaseC:=Real_0;
6827:PMM.VirAVoltageBetweenPhaseAB_V:=Real_0;
6829:PMM.VirAVoltageBetweenPhaseAN_V:=Real_0;
6831:PMM.VirAVoltageBetweenPhaseBC_V:=Real_0;
6833:PMM.VirAVoltageBetweenPhaseBN_V:=Real_0;
6835:PMM.VirAVoltageBetweenPhaseCA_V:=Real_0;
6837:PMM.VirAVoltageBetweenPhaseCN_V:=Real_0;
6839:PMM.VirB.Current[10]:=Real_0;
6841:PMM.VirB.Current[11]:=Real_0;
6843:PMM.VirB.Current[12]:=Real_0;
6845:PMM.VirB.Current[13]:=Real_0;
6847:PMM.VirB.Current[14]:=Real_0;
6849:PMM.VirB.Current[15]:=Real_0;
6851:PMM.VirB.Current[16]:=Real_0;
6853:PMM.VirB.Current[17]:=Real_0;
6855:PMM.VirB.Current[18]:=Real_0;
6857:PMM.VirB.Current[19]:=Real_0;
6859:PMM.VirB.Current[1]:=Real_0;
6861:PMM.VirB.Current[20]:=Real_0;
6863:PMM.VirB.Current[21]:=Real_0;
6865:PMM.VirB.Current[22]:=Real_0;
6867:PMM.VirB.Current[23]:=Real_0;
6869:PMM.VirB.Current[24]:=Real_0;
6871:PMM.VirB.Current[25]:=Real_0;
6873:PMM.VirB.Current[26]:=Real_0;
6875:PMM.VirB.Current[27]:=Real_0;
6877:PMM.VirB.Current[28]:=Real_0;
6879:PMM.VirB.Current[29]:=Real_0;
6881:PMM.VirB.Current[2]:=Real_0;
6883:PMM.VirB.Current[30]:=Real_0;
6885:PMM.VirB.Current[31]:=Real_0;
6887:PMM.VirB.Current[32]:=Real_0;
6889:PMM.VirB.Current[33]:=Real_0;
6891:PMM.VirB.Current[34]:=Real_0;
6893:PMM.VirB.Current[35]:=Real_0;
6895:PMM.VirB.Current[36]:=Real_0;
6897:PMM.VirB.Current[37]:=Real_0;
6899:PMM.VirB.Current[38]:=Real_0;
6901:PMM.VirB.Current[39]:=Real_0;
6903:PMM.VirB.Current[3]:=Real_0;
6905:PMM.VirB.Current[40]:=Real_0;
6907:PMM.VirB.Current[41]:=Real_0;
6909:PMM.VirB.Current[42]:=Real_0;
6911:PMM.VirB.Current[43]:=Real_0;
6913:PMM.VirB.Current[44]:=Real_0;
6915:PMM.VirB.Current[4]:=Real_0;
6917:PMM.VirB.Current[5]:=Real_0;
6919:PMM.VirB.Current[6]:=Real_0;
6921:PMM.VirB.Current[7]:=Real_0;
6923:PMM.VirB.Current[8]:=Real_0;
6925:PMM.VirB.Current[9]:=Real_0;
6927:PMM.VirB_fsys:=Real_0;
6929:PMM.VirB_Isys:=Real_0;
6931:PMM.VirB_PFsys:=Real_0;
6933:PMM.VirB_Psys:=Real_0;
6935:PMM.VirB_Qsys:=Real_0;
6937:PMM.VirB_Ssys:=Real_0;
6939:PMM.VirB_Usys:=Real_0;
6941:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
6943:PMM.VirBActivePowerPhaseA_kW:=Real_0;
6945:PMM.VirBActivePowerPhaseB_kW:=Real_0;
6947:PMM.VirBActivePowerPhaseC_kW:=Real_0;
6949:PMM.VirBAparentPowerPhaseA:=Real_0;
6951:PMM.VirBAparentPowerPhaseB:=Real_0;
6953:PMM.VirBAparentPowerPhaseC:=Real_0;
6955:PMM.VirBCurrentInPhaseA_A:=Real_0;
6957:PMM.VirBCurrentInPhaseB_A:=Real_0;
6959:PMM.VirBCurrentInPhaseC_A:=Real_0;
6961:PMM.VirBReactiveEnergyConsumed_kVARh:=Real_0;
6963:PMM.VirBReactivePowerPhaseA:=Real_0;
6965:PMM.VirBReactivePowerPhaseB:=Real_0;
6967:PMM.VirBReactivePowerPhaseC:=Real_0;
6969:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
6971:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
6973:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
6975:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
6977:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
6979:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;
(*Pisanje ULONG*)
(**)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
7000:Date_Time[0]:=String_0;
7015:Date_Time[1]:=String_0;
7030:Date_Time[2]:=String_0;
7045:Date_Time[3]:=String_0;
7060:kom_nast_cas_izpada:=String_0;
7075:UserCurrentName:=String_0;
7090:UserDisplay:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.PLC_Dan:=Byte_0;
6:DateTime.PLC_DanVTednu:=Byte_0;
7:DateTime.PLC_Leto:=Byte_0;
8:DateTime.PLC_Mesec:=Byte_0;
9:DateTime.PLC_Minuta:=Byte_0;
10:DateTime.PLC_Sekunda:=Byte_0;
11:DateTime.PLC_Ura:=Byte_0;
12:DateTime.Sekunda:=Byte_0;
13:DateTime.Ura:=Byte_0;
14:ErrorComPMM[1].Status:=Word_01;
15:HIA1_vlaga_s:=Word_01;
16:HIA2_vlaga_s:=Word_01;
17:HIA3_vlaga_s:=Word_01;
18:HIA4_vlaga_s:=Word_01;
19:HIA5_vlaga_s:=Word_01;
20:HIA6_vlaga_s:=Word_01;
21:HIA7_vlaga_s:=Word_01;
22:HIA8_vlaga_s:=Word_01;
23:TIA1_alarm:=Word_01;
24:TIA1_temp_s:=Word_01;
25:TIA2_alarm:=Word_01;
26:TIA2_temp_s:=Word_01;
27:TIA3_alarm:=Word_01;
28:TIA3_temp_s:=Word_01;
29:TIA4_alarm:=Word_01;
30:TIA4_temp_s:=Word_01;
31:TIA5_alarm:=Word_01;
32:TIA5_temp_s:=Word_01;
33:TIA6_alarm:=Word_01;
34:TIA6_temp_s:=Word_01;
35:TIA7_alarm:=Word_01;
36:TIA7_temp_s:=Word_01;
37:TIA8_alarm:=Word_01;
38:TIA8_temp_s:=Word_01;
39:UserCurrentLevel:=Byte_0;
(*Pisanje UINT*)
(**)
8000:NSX[1].StatusSwitch:=Word_01;
8001:NSX[2].StatusSwitch:=Word_01;
8002:NSX[3].StatusSwitch:=Word_01;
8003:NSX[4].StatusSwitch:=Word_01;
8004:NSX[5].StatusSwitch:=Word_01;
8005:NSX[6].StatusSwitch:=Word_01;
8006:PMM.VirAAlarmPhase.C01_16_60to80:=Word_01;
8007:PMM.VirAAlarmPhase.C01_16_over80:=Word_01;
8008:PMM.VirAAlarmPhase.C17_32_60to80:=Word_01;
8009:PMM.VirAAlarmPhase.C17_32_over80:=Word_01;
8010:PMM.VirAAlarmPhase.C33_44_60to80:=Word_01;
8011:PMM.VirAAlarmPhase.C33_44_over80:=Word_01;
8012:PMM.VirBAlarmPhase.C01_16_60to80:=Word_01;
8013:PMM.VirBAlarmPhase.C01_16_over80:=Word_01;
8014:PMM.VirBAlarmPhase.C17_32_60to80:=Word_01;
8015:PMM.VirBAlarmPhase.C17_32_over80:=Word_01;
8016:PMM.VirBAlarmPhase.C33_44_60to80:=Word_01;
8017:PMM.VirBAlarmPhase.C33_44_over80:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord2 : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
ULong_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
Long_0 AT %MD0:DINT;
ULong_0 AT %MD0:UDINT;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)